## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| schema_version | 2.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 3.1
description
description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Outdoor unit manufacturer name
Note on B16: Outdoor unit model number
Note on B17: Indoor unit manufacturer name
Note on B18: Indoor unit model number
Note on B19: Refrigerant used
Note on B20: Type of compressor
Note on A21: Data group containing performance information
Note on B22: Method used to control different speeds of the compressor
Note on B23: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A24: Data group describing cooling performance over a range of conditions
Note on A25: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
283.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 112668.5632 | 111410.4872 | 13138.2571 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 122910.7799 | 121903.4308 | 13782.6812 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 56334.2816 | 55066.4267 | 6569.1286 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 61455.3899 | 60439.4865 | 6891.3406 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 119984.0891 | 113664.0672 | 13384.919 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 130891.329 | 125825.2029 | 14041.4418 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 59992.0446 | 53661.6088 | 6692.4595 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 65445.6645 | 60370.4287 | 7020.7209 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 192140.6546 | 184469.6944 | 16681.5997 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 204483.7293 | 198343.8651 | 16993.3054 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 96070.3273 | 88298.9315 | 8340.7999 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 102241.8647 | 96016.2849 | 8496.6527 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 204616.2726 | 165762.5785 | 16994.7855 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 217760.7783 | 186620.6154 | 17312.3432 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 102308.1363 | 71674.5632 | 8497.3927 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 108880.3891 | 77648.9452 | 8656.1716 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 175365.7755 | 123624.6885 | 16174.1968 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 175365.7755 | 123627.7062 | 16174.1968 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 87682.8877 | 61594.4172 | 8087.0984 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 87682.8877 | 61595.1663 | 8087.0984 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 186752.207 | 130923.94 | 16477.8564 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 186752.207 | 130924.622 | 16477.8564 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 93376.1035 | 65412.584 | 8238.9282 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 93376.1035 | 65412.7542 | 8238.9282 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 365191.4304 | 259021.7273 | 18796.6747 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 365191.4304 | 259098.1229 | 18796.6747 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 182595.7152 | 128658.3572 | 9398.3374 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 182595.7152 | 128677.2027 | 9398.3374 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 388903.1679 | 272998.3643 | 19149.5696 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 388903.1679 | 273015.4595 | 19149.5696 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 194451.5839 | 136307.3763 | 9574.7848 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 194451.5839 | 136311.638 | 9574.7848 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 78817.456 | 77553.5038 | 22111.3674 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 87829.6897 | 86817.4574 | 23856.148 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 39408.728 | 38137.935 | 11055.6837 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 43914.8448 | 42896.4999 | 11928.074 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 83935.0427 | 77608.7631 | 22526.4934 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 93532.4372 | 88461.1109 | 24304.0311 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 41967.5214 | 35633.9567 | 11263.2467 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 46766.2186 | 41688.3827 | 12152.0155 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 149190.6404 | 141474.7786 | 32501.9297 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 160202.7632 | 154025.7756 | 33534.7897 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 74595.3202 | 66801.4736 | 16250.9649 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 80101.3816 | 73857.2401 | 16767.3949 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 158877.5306 | 119976.0195 | 33112.1315 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 170604.6662 | 139424.9695 | 34164.3827 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 79438.7653 | 55642.6206 | 16556.0657 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 85302.3331 | 59752.5602 | 17082.1914 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 134257.1843 | 94488.3151 | 30868.8829 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 134257.1843 | 94490.078 | 30868.8829 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 67128.5922 | 47116.7433 | 15434.4415 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 67128.5922 | 47117.1817 | 15434.4415 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 142974.451 | 100197.7717 | 31448.4254 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 142974.451 | 100198.1711 | 31448.4254 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 71487.2255 | 50069.9552 | 15724.2127 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 71487.2255 | 50070.0549 | 15724.2127 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 305094.3808 | 215925.4007 | 36769.0524 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 305094.3808 | 215978.487 | 36769.0524 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 152547.1904 | 107369.6267 | 18384.5262 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 152547.1904 | 107382.7512 | 18384.5262 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 324904.0403 | 227967.3164 | 37459.3666 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 324904.0403 | 227979.237 | 37459.3666 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 162452.0201 | 113849.8793 | 18729.6833 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 162452.0201 | 113852.8524 | 18729.6833 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 40
323.15 | 40
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)