## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| schema_version | 2.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 3.1
description
description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Outdoor unit manufacturer name
Note on B16: Outdoor unit model number
Note on B17: Indoor unit manufacturer name
Note on B18: Indoor unit model number
Note on B19: Refrigerant used
Note on B20: Type of compressor
Note on A21: Data group containing performance information
Note on B22: Method used to control different speeds of the compressor
Note on B23: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A24: Data group describing cooling performance over a range of conditions
Note on A25: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
283.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 116203.4768 | 114946.0144 | 14164.1899 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 125592.3068 | 124585.3309 | 14717.7995 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 58101.7384 | 56834.1903 | 7082.0949 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 62796.1534 | 61780.4366 | 7358.8997 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 124818.4658 | 118499.2831 | 14426.5551 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 134903.3564 | 129837.7888 | 14990.4193 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 62409.2329 | 56079.2167 | 7213.2775 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 67451.6782 | 62376.7216 | 7495.2096 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 190892.5952 | 183220.3302 | 16900.2694 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 202832.68 | 196691.4316 | 17024.3009 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 95446.2976 | 87674.2494 | 8450.1347 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 101416.34 | 95190.0681 | 8512.1504 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 205044.819 | 166191.573 | 17213.3154 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 217870.107 | 186730.0358 | 17339.6443 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 102522.4095 | 71824.8014 | 8606.6577 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 108935.0535 | 77703.6554 | 8669.8222 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 174800.1022 | 123223.1026 | 16608.6169 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 174800.1022 | 123226.1007 | 16608.6169 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 87400.0511 | 61395.0353 | 8304.3084 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 87400.0511 | 61395.7796 | 8304.3084 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 187759.2752 | 131631.024 | 16916.2605 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 187759.2752 | 131631.7134 | 16916.2605 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 93879.6376 | 65765.5913 | 8458.1303 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 93879.6376 | 65765.7634 | 8458.1303 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 364546.9341 | 258558.5541 | 12659.3931 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 364546.9341 | 258634.6767 | 12659.3931 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 182273.4671 | 128429.8067 | 6329.6965 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 182273.4671 | 128448.5853 | 6329.6965 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 391573.3873 | 274878.0898 | 12893.8847 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 391573.3873 | 274895.4213 | 12893.8847 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 195786.6937 | 137244.5905 | 6446.9424 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 195786.6937 | 137248.911 | 6446.9424 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 87882.8273 | 86620.4488 | 23621.8791 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 95717.7037 | 94706.5695 | 25050.8518 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 43941.4136 | 42671.4074 | 11810.9395 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 47858.8519 | 46841.0559 | 12525.4259 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 94398.2054 | 88073.7421 | 24059.4303 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 102813.9369 | 97743.9025 | 25514.8721 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 47199.1027 | 40866.4462 | 12029.7151 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 51406.9684 | 46329.7785 | 12757.436 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 151076.4384 | 143362.5481 | 32921.2103 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 161335.0061 | 155158.9678 | 34001.0629 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 75538.2192 | 67745.3583 | 16460.6051 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 80667.5031 | 74423.8362 | 17000.5314 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 162276.8077 | 123378.8503 | 33531.0143 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 173295.9159 | 142118.4754 | 34630.8691 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 81138.4038 | 56833.9027 | 16765.5071 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 86647.958 | 60695.7995 | 17315.4346 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 137310.3888 | 96649.0049 | 31298.3187 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 137310.3888 | 96650.8493 | 31298.3187 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 68655.1944 | 48191.2026 | 15649.1593 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 68655.1944 | 48191.6611 | 15649.1593 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 147490.1831 | 103366.2098 | 31878.0616 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 147490.1831 | 103366.6349 | 31878.0616 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 73745.0916 | 51652.3162 | 15939.0308 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 73745.0916 | 51652.4223 | 15939.0308 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 303067.3106 | 214475.0337 | 39728.9878 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 303067.3106 | 214527.4091 | 39728.9878 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 151533.6553 | 106652.3621 | 19864.4939 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 151533.6553 | 106665.3119 | 19864.4939 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 325535.8427 | 228411.6614 | 40464.8932 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 325535.8427 | 228423.6284 | 40464.8932 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 162767.9214 | 114071.5301 | 20232.4466 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 162767.9214 | 114074.5147 | 20232.4466 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 40
323.15 | 40
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)