## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| schema_version | 2.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation that applies a constant COP of 3.1
description
description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Outdoor unit manufacturer name
Note on B16: Outdoor unit model number
Note on B17: Indoor unit manufacturer name
Note on B18: Indoor unit model number
Note on B19: Refrigerant used
Note on B20: Type of compressor
Note on A21: Data group containing performance information
Note on B22: Method used to control different speeds of the compressor
Note on B23: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A24: Data group describing cooling performance over a range of conditions
Note on A25: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
283.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 17526.3909 | 12268.4736 | 5615.4543 | COMP_STAGE_1
283.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 18942.4613 | 13259.7229 | 5834.9352 | COMP_STAGE_1
283.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 8763.1954 | 6134.2368 | 2807.7271 | COMP_STAGE_2
283.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 9471.2306 | 6629.8614 | 2917.4676 | COMP_STAGE_2
283.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 18825.7467 | 13178.0227 | 5719.4701 | COMP_STAGE_1
283.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 20346.8005 | 14242.7603 | 5943.0165 | COMP_STAGE_1
283.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 9412.8733 | 6589.0113 | 2859.735 | COMP_STAGE_2
283.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 10173.4002 | 7121.3802 | 2971.5082 | COMP_STAGE_2
283.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 28791.3781 | 20153.9647 | 6700.1848 | COMP_STAGE_1
283.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 30592.2416 | 21414.5691 | 6749.3576 | COMP_STAGE_1
283.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 14395.6891 | 10076.9823 | 3350.0924 | COMP_STAGE_2
283.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 15296.1208 | 10707.2845 | 3374.6788 | COMP_STAGE_2
283.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 30925.8875 | 21648.1212 | 6824.2932 | COMP_STAGE_1
283.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 32860.2617 | 23002.1832 | 6874.3769 | COMP_STAGE_1
283.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 15462.9437 | 10824.0606 | 3412.1466 | COMP_STAGE_2
283.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 16430.1308 | 11501.0916 | 3437.1884 | COMP_STAGE_2
283.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 26364.2277 | 18454.9594 | 6584.5579 | COMP_STAGE_1
283.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 26364.2277 | 18454.9594 | 6584.5579 | COMP_STAGE_1
283.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 13182.1138 | 9227.4797 | 3292.279 | COMP_STAGE_2
283.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 13182.1138 | 9227.4797 | 3292.279 | COMP_STAGE_2
283.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 28318.7951 | 19823.1566 | 6706.5246 | COMP_STAGE_1
283.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 28318.7951 | 19823.1566 | 6706.5246 | COMP_STAGE_1
283.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 14159.3975 | 9911.5783 | 3353.2623 | COMP_STAGE_2
283.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 14159.3975 | 9911.5783 | 3353.2623 | COMP_STAGE_2
283.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 54982.796 | 38487.9572 | 5018.8711 | COMP_STAGE_1
283.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 54982.796 | 38487.9572 | 5018.8711 | COMP_STAGE_1
283.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 27491.398 | 19243.9786 | 2509.4355 | COMP_STAGE_2
283.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 27491.398 | 19243.9786 | 2509.4355 | COMP_STAGE_2
283.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 59059.0612 | 41341.3428 | 5111.8363 | COMP_STAGE_1
283.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 59059.0612 | 41341.3428 | 5111.8363 | COMP_STAGE_1
283.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 29529.5306 | 20670.6714 | 2555.9181 | COMP_STAGE_2
283.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 29529.5306 | 20670.6714 | 2555.9181 | COMP_STAGE_2
323.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 13254.9285 | 9278.45 | 9364.996 | COMP_STAGE_1
323.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 14436.6239 | 10105.6367 | 9931.5184 | COMP_STAGE_1
323.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 6627.4643 | 4639.225 | 4682.498 | COMP_STAGE_2
323.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 7218.3119 | 5052.8184 | 4965.7592 | COMP_STAGE_2
323.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 14237.6105 | 9966.3274 | 9538.4651 | COMP_STAGE_1
323.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 15506.9134 | 10854.8393 | 10115.4812 | COMP_STAGE_1
323.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 7118.8053 | 4983.1637 | 4769.2325 | COMP_STAGE_2
323.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 7753.4567 | 5427.4197 | 5057.7406 | COMP_STAGE_2
323.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 22786.1058 | 15950.274 | 13051.756 | COMP_STAGE_1
323.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 24333.3544 | 17033.3481 | 13479.8682 | COMP_STAGE_1
323.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 11393.0529 | 7975.137 | 6525.878 | COMP_STAGE_2
323.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 12166.6772 | 8516.674 | 6739.9341 | COMP_STAGE_2
323.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 24475.4016 | 17132.7811 | 13293.5154 | COMP_STAGE_1
323.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 26137.3587 | 18296.1511 | 13729.5576 | COMP_STAGE_1
323.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 12237.7008 | 8566.3906 | 6646.7577 | COMP_STAGE_2
323.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 13068.6794 | 9148.0756 | 6864.7788 | COMP_STAGE_2
323.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 20709.8412 | 14496.8888 | 12408.3536 | COMP_STAGE_1
323.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 20709.8412 | 14496.8888 | 12408.3536 | COMP_STAGE_1
323.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 10354.9206 | 7248.4444 | 6204.1768 | COMP_STAGE_2
323.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 10354.9206 | 7248.4444 | 6204.1768 | COMP_STAGE_2
323.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 22245.2088 | 15571.6461 | 12638.1952 | COMP_STAGE_1
323.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 22245.2088 | 15571.6461 | 12638.1952 | COMP_STAGE_1
323.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 11122.6044 | 7785.8231 | 6319.0976 | COMP_STAGE_2
323.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 11122.6044 | 7785.8231 | 6319.0976 | COMP_STAGE_2
323.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 45710.131 | 31997.0917 | 15750.7288 | COMP_STAGE_1
323.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 45710.131 | 31997.0917 | 15750.7288 | COMP_STAGE_1
323.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 22855.0655 | 15998.5459 | 7875.3644 | COMP_STAGE_2
323.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 22855.0655 | 15998.5459 | 7875.3644 | COMP_STAGE_2
323.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 49098.9477 | 34369.2634 | 16042.4817 | COMP_STAGE_1
323.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 49098.9477 | 34369.2634 | 16042.4817 | COMP_STAGE_1
323.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 24549.4738 | 17184.6317 | 8021.2408 | COMP_STAGE_2
323.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 24549.4738 | 17184.6317 | 8021.2408 | COMP_STAGE_2
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 40
323.15 | 40
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)