## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| schema_version | 2.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation of the ASHRAE 90.1 Appendix G minimum requirements for unitary air-conditioners
description
description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Outdoor unit manufacturer name
Note on B16: Outdoor unit model number
Note on B17: Indoor unit manufacturer name
Note on B18: Indoor unit model number
Note on B19: Refrigerant used
Note on B20: Type of compressor
Note on A21: Data group containing performance information
Note on B22: Method used to control different speeds of the compressor
Note on B23: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A24: Data group describing cooling performance over a range of conditions
Note on A25: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
283.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 116203.4768 | 114946.0144 | 15008.2427 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 125592.3068 | 124585.3309 | 15386.2575 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 58101.7384 | 56834.1903 | 7504.1213 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 62796.1534 | 61780.4366 | 7693.1288 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 124818.4658 | 118499.2831 | 15286.2424 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 134903.3564 | 129837.7888 | 15671.2592 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 62409.2329 | 56079.2167 | 7643.1212 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 67451.6782 | 62376.7216 | 7835.6296 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 145294.6113 | 142889.4098 | 15946.6391 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 153572.5123 | 151645.996 | 16099.7378 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 72647.3056 | 70218.0707 | 7973.3195 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 76786.2561 | 74839.3683 | 8049.8689 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 156066.3327 | 143942.4831 | 16242.0208 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 164957.9332 | 155238.2611 | 16397.9555 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 78033.1663 | 65883.5015 | 8121.0104 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 82478.9666 | 72737.4126 | 8198.9777 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 169046.8574 | 164658.569 | 16274.7849 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 179244.349 | 175730.4672 | 16320.7882 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 84523.4287 | 80084.3508 | 8137.3925 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 89622.1745 | 86065.1046 | 8160.3941 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 181579.5015 | 159405.5655 | 16576.2449 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 192533.0056 | 174757.838 | 16623.1003 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 90789.7508 | 68561.2598 | 8288.1225 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 96266.5028 | 78444.9453 | 8311.5502 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 190892.5952 | 183220.3302 | 16315.5977 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 202832.68 | 196691.4316 | 16255.2897 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 95446.2976 | 87674.2494 | 8157.7988 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 101416.34 | 95190.0681 | 8127.6449 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 205044.819 | 166191.573 | 16617.8137 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 217870.107 | 186730.0358 | 16556.3886 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 102522.4095 | 71824.8014 | 8308.9068 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 108935.0535 | 77703.6554 | 8278.1943 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 124942.6735 | 112334.0029 | 15362.5751 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 130440.1977 | 120341.2587 | 15551.9413 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 62471.3368 | 49753.9714 | 7681.2876 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 65220.0989 | 55030.169 | 7775.9707 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 134205.5612 | 94047.3909 | 15647.1382 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 140110.6559 | 98190.3098 | 15840.012 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 67102.7806 | 46997.8067 | 7823.5691 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 70055.328 | 49066.926 | 7920.006 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 154835.4641 | 130667.0062 | 16119.2545 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 161901.8833 | 142559.4239 | 16210.8316 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 77417.732 | 54362.1644 | 8059.6272 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 80950.9417 | 61393.135 | 8105.4158 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 166314.5166 | 116577.7349 | 16417.8336 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 173904.8197 | 121905.7819 | 16511.107 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 83157.2583 | 58249.4475 | 8208.9168 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 86952.4099 | 60909.7584 | 8255.5535 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 184385.4792 | 140130.3511 | 16325.5925 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 192721.6352 | 157345.3302 | 16309.7453 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 92192.7396 | 64773.3824 | 8162.7963 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 96360.8176 | 67713.4426 | 8154.8727 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 198055.2843 | 138859.9847 | 16627.9936 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 207009.4587 | 145148.6746 | 16611.8529 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 99027.6421 | 69374.6268 | 8313.9968 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 103504.7293 | 72513.7734 | 8305.9265 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 214395.7847 | 151357.7989 | 16152.1535 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 223600.932 | 161463.0895 | 16043.6739 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 107197.8924 | 75357.3516 | 8076.0768 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 111800.466 | 78607.9081 | 8021.8369 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 230290.4669 | 161499.0928 | 16451.342 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 240178.0571 | 168447.0459 | 16340.853 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 115145.2334 | 80675.5371 | 8225.671 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 120089.0285 | 84142.8443 | 8170.4265 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 148439.0244 | 104534.4119 | 16010.0646 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 151072.9828 | 106401.8358 | 16058.1788 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 74219.5122 | 52109.9606 | 8005.0323 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 75536.4914 | 53037.7319 | 8029.0894 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 159443.8635 | 111755.8029 | 16306.6212 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 162273.0959 | 113741.7245 | 16355.6266 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 79721.9318 | 55841.6033 | 8153.3106 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 81136.548 | 56833.198 | 8177.8133 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 192815.6263 | 136014.7322 | 16309.4099 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 195824.4424 | 138157.4627 | 16296.9215 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 96407.8132 | 67745.4125 | 8154.7049 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 97912.2212 | 68807.5829 | 8148.4607 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 207110.418 | 145218.4882 | 16611.5113 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 210342.299 | 147489.2241 | 16598.7916 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 103555.209 | 72548.8951 | 8305.7556 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 105171.1495 | 73682.1555 | 8299.3958 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 241337.4883 | 170540.2422 | 15782.6473 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 244404.6509 | 172738.5919 | 15731.9298 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 120668.7442 | 84867.2263 | 7891.3236 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 122202.3255 | 85953.4695 | 7865.9649 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 259229.5503 | 181830.8233 | 16074.9914 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 262524.1034 | 184148.803 | 16023.3345 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 129614.7752 | 90822.7828 | 8037.4957 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 131262.0517 | 91978.8197 | 8011.6672 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 294581.2839 | 208529.8186 | 14790.5461 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 297461.8785 | 210617.9533 | 14735.1403 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 147290.642 | 103680.9267 | 7395.273 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 148730.9392 | 104706.8944 | 7367.5701 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 316420.6866 | 222029.779 | 15064.5134 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 319514.8401 | 224212.1126 | 15008.0813 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 158210.3433 | 110880.9034 | 7532.2567 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 159757.42 | 111967.9552 | 7504.0406 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 169773.7964 | 119656.9032 | 16279.7703 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 170230.71 | 119983.7368 | 16282.7648 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 84886.8982 | 59623.9435 | 8139.8852 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 85115.355 | 59785.6017 | 8141.3824 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 182360.3337 | 127840.7455 | 16581.3227 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 182851.1215 | 128185.9083 | 16584.3727 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 91180.1668 | 63873.21 | 8290.6613 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 91425.5608 | 64045.3881 | 8292.1863 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 224905.9111 | 158836.9183 | 16026.6373 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 225378.2482 | 159182.0522 | 16020.3763 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 112452.9556 | 79066.2086 | 8013.3186 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 112689.1241 | 79235.1221 | 8010.1881 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 241579.7836 | 169429.7005 | 16323.5008 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 242087.1383 | 169788.1772 | 16317.1239 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 120789.8918 | 84633.8098 | 8161.7504 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 121043.5692 | 84812.2146 | 8158.5619 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 285700.1819 | 202186.171 | 14962.8314 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 286142.1051 | 202527.2221 | 14954.2285 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 142850.091 | 100541.0768 | 7481.4157 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 143071.0526 | 100703.5939 | 7477.1143 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 306881.1654 | 215322.9884 | 15239.99 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 307355.8515 | 215662.52 | 15231.2277 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 153440.5827 | 107534.8021 | 7619.995 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 153677.9258 | 107702.751 | 7615.6139 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 352235.8593 | 249747.8093 | 13829.2989 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 352616.9967 | 250086.3886 | 13824.5383 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 176117.9296 | 124073.1252 | 6914.6494 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 176308.4983 | 124224.2429 | 6912.2692 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 378349.6051 | 265577.2184 | 14085.4608 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 378758.9989 | 265880.154 | 14080.6121 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 189174.8025 | 132605.2326 | 7042.7304 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 189379.4994 | 132752.5993 | 7040.3061 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 174800.1022 | 123223.1026 | 16306.9445 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 174800.1022 | 123226.1007 | 16306.9445 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 87400.0511 | 61395.0353 | 8153.4723 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 87400.0511 | 61395.7796 | 8153.4723 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 187759.2752 | 131631.024 | 16609.0003 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 187759.2752 | 131631.7134 | 16609.0003 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 93879.6376 | 65765.5913 | 8304.5001 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 93879.6376 | 65765.7634 | 8304.5001 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 232191.2877 | 164024.8712 | 15924.7875 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 232191.2877 | 164034.8786 | 15924.7875 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 116095.6439 | 81637.9913 | 7962.3938 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 116095.6439 | 81640.4703 | 7962.3938 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 249405.2769 | 174927.8351 | 16219.7645 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 249405.2769 | 174930.1283 | 16219.7645 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 124702.6384 | 87377.7975 | 8109.8822 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 124702.6384 | 87378.3697 | 8109.8822 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 295440.2317 | 209143.9966 | 14773.9918 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 295440.2317 | 209173.1395 | 14773.9918 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 147720.1158 | 103984.7604 | 7386.9959 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 147720.1158 | 103991.964 | 7386.9959 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 317343.3142 | 222678.582 | 15047.6524 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 317343.3142 | 222685.238 | 15047.6524 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 158671.6571 | 111204.5627 | 7523.8262 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 158671.6571 | 111206.2226 | 7523.8262 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 364546.9341 | 258558.5541 | 13690.5165 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 364546.9341 | 258634.6767 | 13690.5165 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 182273.4671 | 128429.8067 | 6845.2583 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 182273.4671 | 128448.5853 | 6845.2583 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 391573.3873 | 274878.0898 | 13944.1078 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 391573.3873 | 274895.4213 | 13944.1078 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 195786.6937 | 137244.5905 | 6972.0539 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 195786.6937 | 137248.911 | 6972.0539 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 121397.3036 | 120140.7429 | 17589.868 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 130397.6453 | 129391.3383 | 17868.1141 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 60698.6518 | 59431.5545 | 8794.934 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 65198.8226 | 64183.4403 | 8934.0571 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 130397.3479 | 124079.1336 | 17915.6874 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 140064.9488 | 135000.0996 | 18199.0876 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 65198.6739 | 58869.1419 | 8957.8437 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 70032.4744 | 64957.877 | 9099.5438 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 149312.7758 | 146908.9036 | 18185.7533 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 157270.3344 | 155344.7992 | 18222.878 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 74656.3879 | 72227.8176 | 9092.8766 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 78635.1672 | 76688.7698 | 9111.439 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 160382.3923 | 148259.9706 | 18522.6104 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 168929.9012 | 159211.2829 | 18560.4228 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 80191.1961 | 68042.2453 | 9261.3052 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 84464.9506 | 74723.9235 | 9280.2114 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 172160.8174 | 167774.4002 | 18158.2277 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 181983.4837 | 178470.9218 | 18029.6626 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 86080.4087 | 81642.2664 | 9079.1138 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 90991.7419 | 87435.3319 | 9014.8313 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 184924.3215 | 162752.3953 | 18494.575 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 195475.2118 | 177701.462 | 18363.6285 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 92462.1607 | 70234.6747 | 9247.2875 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 97737.6059 | 79916.7573 | 9181.8142 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 193212.5452 | 185542.7056 | 17808.6731 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 204732.2507 | 198592.5949 | 17508.8216 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 96606.2726 | 88835.4371 | 8904.3366 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 102366.1254 | 96140.6498 | 8754.4108 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 207536.7634 | 168686.1225 | 18138.5456 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 219910.5065 | 188772.1458 | 17833.1398 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 103768.3817 | 72698.4282 | 9069.2728 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 109955.2532 | 78724.7104 | 8916.5699 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 129774.6005 | 117174.3371 | 17851.6579 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 135048.4412 | 124955.9314 | 17978.329 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 64887.3003 | 52174.1385 | 8925.829 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 67524.2206 | 57337.5054 | 8989.1645 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 139395.7133 | 97688.6621 | 18182.3266 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 145060.5413 | 101663.349 | 18311.344 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 69697.8567 | 48816.3994 | 9091.1633 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 72530.2706 | 50801.414 | 9155.672 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 158484.9176 | 134328.5704 | 18223.9563 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 165283.0905 | 145949.6259 | 18208.6941 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 79242.4588 | 55647.5827 | 9111.9781 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 82641.5453 | 63088.236 | 9104.347 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 170234.5301 | 119329.2651 | 18561.5211 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 177536.6998 | 124455.3797 | 18545.9762 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 85117.265 | 59623.3305 | 9280.7605 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 88768.3499 | 62182.7349 | 9272.9881 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 186938.4564 | 142698.7456 | 17941.3877 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 194976.5935 | 159611.2 | 17767.3348 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 93469.2282 | 65673.5862 | 8970.6938 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 97488.2968 | 68508.8305 | 8883.6674 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 200797.5318 | 140785.7332 | 18273.7184 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 209431.5931 | 146849.871 | 18096.4415 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 100398.7659 | 70335.9554 | 9136.8592 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 104715.7965 | 73362.9443 | 9048.2207 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 215896.674 | 152426.4937 | 17155.8638 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 224790.0362 | 162662.2305 | 16835.8849 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 107948.337 | 75887.152 | 8577.9319 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 112395.0181 | 79027.8096 | 8417.9425 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 231902.6277 | 162631.7648 | 17473.6441 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 241455.3181 | 169344.5701 | 17147.7383 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 115951.3139 | 81240.8318 | 8736.8221 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 120727.659 | 84590.7447 | 8573.8691 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 152334.8178 | 107294.9201 | 18206.118 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 154866.9218 | 109090.794 | 18217.2274 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 76167.4089 | 53481.8133 | 9103.059 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 77433.4609 | 54373.8721 | 9108.6137 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 163628.4797 | 114692.7556 | 18543.3524 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 166348.3065 | 116602.0342 | 18554.6676 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 81814.2399 | 57308.1474 | 9271.6762 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 83174.1533 | 58261.4353 | 9277.3338 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 195067.2508 | 137615.4862 | 17765.164 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 197969.6474 | 139683.0012 | 17693.3138 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 97533.6254 | 68539.5995 | 8882.582 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 98984.8237 | 69564.3431 | 8846.6569 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 209528.9714 | 146917.1465 | 18094.2305 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 212646.5434 | 149107.6988 | 18021.0494 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 104764.4857 | 73396.8047 | 9047.1153 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 106323.2717 | 74490.0152 | 9010.5247 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 241938.9614 | 170969.3166 | 16135.6493 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 244906.1741 | 173096.4917 | 16004.7382 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 120969.4807 | 85079.7384 | 8067.8246 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 122453.0871 | 86130.6986 | 8002.3691 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 259875.6148 | 182284.9176 | 16434.5321 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 263062.8081 | 184527.467 | 16301.1962 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 129937.8074 | 91049.367 | 8217.266 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 131531.404 | 92167.7584 | 8150.5981 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 293510.4893 | 207763.3111 | 13573.5752 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 296304.1316 | 209788.8202 | 13422.4778 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 146755.2446 | 103301.9463 | 6786.7876 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 148152.0658 | 104297.0454 | 6711.2389 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 315270.5063 | 221220.7637 | 13825.0004 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 318271.2612 | 223337.3158 | 13671.1041 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 157635.2532 | 110477.3698 | 6912.5002 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 159135.6306 | 111531.6317 | 6835.5521 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 172860.7839 | 121847.8165 | 18151.2089 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 173300.7643 | 122162.8059 | 18146.6238 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 86430.3919 | 60711.8558 | 9075.6044 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 86650.3821 | 60867.5894 | 9073.3119 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 185676.1814 | 130168.7619 | 18487.4261 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 186148.7807 | 130501.1944 | 18482.7561 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 92838.0907 | 65035.4855 | 9243.7131 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 93074.3903 | 65201.298 | 9241.3781 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 226051.2015 | 159653.009 | 16787.9567 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 226507.7034 | 159986.9759 | 16770.4588 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 113025.6007 | 79470.6331 | 8393.9783 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 113253.8517 | 79633.9836 | 8385.2294 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 242809.9824 | 170294.1496 | 17098.9222 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 243300.328 | 170640.7007 | 17081.1003 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 121404.9912 | 85065.2057 | 8549.4611 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 121650.164 | 85237.6525 | 8540.5501 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 284899.6026 | 201613.4082 | 14033.9495 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 285328.0025 | 201944.6219 | 14011.2591 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 142449.8013 | 100257.81 | 7016.9748 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 142664.0013 | 100415.5023 | 7005.6296 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 306021.2335 | 214718.1999 | 14293.9022 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 306481.3937 | 215047.4788 | 14270.7915 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 153010.6167 | 107233.1182 | 7146.9511 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 153240.6969 | 107395.9619 | 7135.3958 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 349484.012 | 247771.6646 | 10488.4327 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 349854.4242 | 248101.4622 | 10468.1777 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 174742.006 | 123097.6352 | 5244.2163 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 174927.2121 | 123244.6861 | 5234.0888 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 375393.7438 | 263496.6994 | 10682.7113 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 375791.6173 | 263791.2827 | 10662.0811 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 187696.8719 | 131567.833 | 5341.3557 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 187895.8086 | 131711.0959 | 5331.0406 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 177701.6631 | 125283.1889 | 18093.5367 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 177701.6631 | 125286.2881 | 18093.5367 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 88850.8315 | 62417.7915 | 9046.7684 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 88850.8315 | 62418.5608 | 9046.7684 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 190875.9494 | 133819.3803 | 18428.6857 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 190875.9494 | 133820.0928 | 18428.6857 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 95437.9747 | 66858.0965 | 9214.3429 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 95437.9747 | 66858.2743 | 9214.3429 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 233093.6894 | 164668.2177 | 16509.495 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 233093.6894 | 164678.3037 | 16509.495 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 116546.8447 | 81956.7282 | 8254.7475 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 116546.8447 | 81959.2266 | 8254.7475 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 250374.58 | 175609.0301 | 16815.3026 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 250374.58 | 175611.3413 | 16815.3026 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 125187.29 | 87717.7233 | 8407.6513 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 125187.29 | 87718.3 | 8407.6513 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 294343.4742 | 208358.8588 | 13528.6024 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 294343.4742 | 208387.7833 | 13528.6024 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 147171.7371 | 103596.58 | 6764.3012 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 147171.7371 | 103603.7299 | 6764.3012 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 316165.2464 | 221849.9408 | 13779.1945 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 316165.2464 | 221856.5473 | 13779.1945 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 158082.6232 | 110791.2423 | 6889.5973 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 158082.6232 | 110792.8899 | 6889.5973 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 361451.0175 | 256333.9468 | 9839.5807 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 361451.0175 | 256408.765 | 9839.5807 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 180725.5087 | 127332.0105 | 4919.7904 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 180725.5087 | 127350.4694 | 4919.7904 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 388247.9484 | 272537.1277 | 10021.8406 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 388247.9484 | 272554.1651 | 10021.8406 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 194123.9742 | 136077.4051 | 5010.9203 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 194123.9742 | 136081.6524 | 5010.9203 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 118408.471 | 117151.3914 | 21491.9359 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 127020.3242 | 126013.5471 | 21900.5553 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 59204.2355 | 57936.8788 | 10745.968 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 63510.1621 | 62494.5447 | 10950.2777 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 127186.9319 | 120868.1603 | 21890.0339 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 136437.243 | 131371.8888 | 22306.2222 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 63593.4659 | 57263.6553 | 10945.017 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 68218.6215 | 63143.7716 | 11153.1111 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 145148.2808 | 142743.031 | 22455.9495 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 152785.497 | 150858.772 | 22578.0731 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 72574.1404 | 70144.8813 | 11227.9747 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 76392.7485 | 74445.7562 | 11289.0365 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 155909.1537 | 143785.2522 | 22871.9041 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 164112.571 | 154392.6746 | 22996.2898 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 77954.5769 | 65804.8861 | 11435.952 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 82056.2855 | 72314.6194 | 11498.1449 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 167092.1179 | 162702.655 | 22648.1073 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 176539.9589 | 173024.7739 | 22590.8211 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 83546.059 | 79106.3938 | 11324.0537 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 88269.9795 | 84712.2579 | 11295.4105 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 179479.8433 | 157304.6456 | 23067.6212 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 189628.1199 | 171851.5524 | 23009.2739 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 89739.9217 | 67510.7999 | 11533.8106 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 94814.0599 | 76991.8025 | 11504.6369 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 187349.8358 | 179673.8671 | 22434.0721 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 198449.162 | 192304.2387 | 22180.9195 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 93674.9179 | 85901.0178 | 11217.0361 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 99224.581 | 92996.4717 | 11090.4598 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 201239.4096 | 162382.1853 | 22849.6215 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 213161.6078 | 182017.5891 | 22591.7797 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 100619.7048 | 70490.7334 | 11424.8107 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 106580.8039 | 75347.4321 | 11295.8898 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 126423.8681 | 113817.7747 | 21875.4269 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 131474.0253 | 121376.5286 | 22073.8286 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 63211.934 | 50495.8573 | 10937.7134 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 65737.0127 | 55547.804 | 11036.9143 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 135796.5673 | 95163.565 | 22280.6283 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 141221.1285 | 98969.4376 | 22482.7051 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 67898.2836 | 47555.2758 | 11140.3142 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 70610.5643 | 49456.0403 | 11241.3525 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 153951.7117 | 129780.321 | 22591.3311 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 160481.6382 | 141135.4006 | 22640.3343 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 76975.8558 | 54050.9158 | 11295.6656 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 80240.8191 | 60681.1234 | 11320.1672 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 165365.2454 | 115911.4502 | 23009.7934 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 172379.2818 | 120834.8917 | 23059.7043 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 82682.6227 | 57916.7543 | 11504.8967 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 86189.6409 | 60375.0675 | 11529.8522 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 181308.774 | 137035.0656 | 22533.1665 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 189048.8924 | 153654.8157 | 22401.1478 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 90654.387 | 63688.6296 | 11266.5832 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 94524.4462 | 66418.1159 | 11200.5739 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 194750.4811 | 136539.2935 | 22950.5514 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 203064.4294 | 142378.0089 | 22816.0873 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 97375.2405 | 68216.1156 | 11475.2757 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 101532.2147 | 71130.7297 | 11408.0437 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 209214.9038 | 147669.7799 | 21854.6092 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 217796.481 | 155609.645 | 21542.7334 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 104607.4519 | 73528.7894 | 10927.3046 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 108898.2405 | 76558.5007 | 10771.3667 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 224725.4904 | 157589.4751 | 22259.425 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 233943.2809 | 164066.1659 | 21941.7723 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 112362.7452 | 78724.2666 | 11129.7125 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 116971.6404 | 81956.5443 | 10970.8862 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 148047.9517 | 104257.3512 | 22509.6543 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 150478.2013 | 105980.3591 | 22547.7002 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 74023.9759 | 51972.2614 | 11254.8271 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 75239.1006 | 52828.2819 | 11273.8501 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 159023.7978 | 111460.9929 | 22926.6036 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 161634.219 | 113293.3267 | 22965.3543 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 79511.8989 | 55694.3895 | 11463.3018 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 80817.1095 | 56609.2954 | 11482.6771 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 189136.2158 | 133399.5403 | 22399.3971 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 191932.193 | 135390.2058 | 22340.3587 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 94568.1079 | 66447.7744 | 11199.6986 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 95966.0965 | 67434.6873 | 11170.1793 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 203158.2267 | 142442.8295 | 22814.3042 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 206161.4896 | 144552.8252 | 22754.1722 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 101579.1133 | 71163.3497 | 11407.1521 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 103080.7448 | 72216.4172 | 11377.0861 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 234357.7749 | 165562.5907 | 20825.2741 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 237225.0378 | 167616.594 | 20686.9972 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 117178.8874 | 82401.524 | 10412.637 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 118612.5189 | 83416.709 | 10343.4986 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 251732.3811 | 176561.6844 | 21211.0234 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 254812.2146 | 178728.3493 | 21070.1852 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 125866.1906 | 88193.5015 | 10605.5117 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 127406.1073 | 89274.1343 | 10535.0926 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 284257.0351 | 201142.0204 | 17951.9789 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 286963.7253 | 203102.2994 | 17772.9832 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 142128.5176 | 100027.5655 | 8975.9895 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 143481.8627 | 100991.1557 | 8886.4916 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 305331.0279 | 214230.1118 | 18284.5058 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 308238.3842 | 216280.2926 | 18102.1945 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 152665.5139 | 106990.3127 | 9142.2529 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 154119.1921 | 108011.6379 | 9051.0973 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 167765.1119 | 118231.5823 | 22646.6318 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 168188.159 | 118534.2714 | 22645.4948 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 83882.5559 | 58916.118 | 11323.3159 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 84094.0795 | 59065.8141 | 11322.7474 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 180202.7311 | 126325.986 | 23066.1185 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 180657.1417 | 126645.5839 | 23064.9603 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 90101.3655 | 63116.9409 | 11533.0592 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 90328.5708 | 63276.3618 | 11532.4802 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 219013.8324 | 154639.6155 | 21495.0119 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 219454.499 | 154961.5874 | 21477.5312 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 109506.9162 | 76985.8887 | 10747.5059 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 109727.2495 | 77143.472 | 10738.7656 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 235250.8832 | 164982.7085 | 21893.1669 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 235724.2196 | 165317.1454 | 21875.3624 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 117625.4416 | 82414.5102 | 10946.5834 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 117862.1098 | 82580.952 | 10937.6812 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 275916.3638 | 195188.8965 | 18491.2433 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 276331.2404 | 195508.6795 | 18464.8819 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 137958.1819 | 97079.8891 | 9245.6217 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 138165.6202 | 97232.3646 | 9232.4409 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 296372.0034 | 207932.4627 | 18833.7591 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 296817.6378 | 208251.1276 | 18806.9094 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 148186.0017 | 103848.0822 | 9416.8795 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 148408.8189 | 104005.7307 | 9403.4547 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 338549.5053 | 239923.3603 | 14094.6339 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 338909.1922 | 240241.2702 | 14067.7861 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 169274.7526 | 119222.4764 | 7047.3169 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 169454.5961 | 119364.6987 | 7033.8931 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 363648.5844 | 255230.614 | 14355.7107 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 364034.9375 | 255516.1441 | 14328.3656 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 181824.2922 | 127445.9313 | 7177.8553 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 182017.4687 | 127584.9157 | 7164.1828 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 172420.5645 | 121534.0088 | 22625.3496 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 172420.5645 | 121536.9253 | 22625.3496 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 86210.2822 | 60556.3734 | 11312.6748 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 86210.2822 | 60557.0975 | 11312.6748 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 185203.3255 | 129836.4598 | 23044.442 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 185203.3255 | 129837.1304 | 23044.442 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 92601.6627 | 64869.6606 | 11522.221 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 92601.6627 | 64869.828 | 11522.221 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 225813.4316 | 159479.2334 | 21213.4034 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 225813.4316 | 159488.6938 | 21213.4034 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 112906.7158 | 79385.5941 | 10606.7017 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 112906.7158 | 79387.9381 | 10606.7017 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 242554.585 | 170113.687 | 21606.3421 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 242554.585 | 170115.8558 | 21606.3421 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 121277.2925 | 84975.3962 | 10803.171 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 121277.2925 | 84975.9374 | 10803.171 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 285064.0573 | 201718.6195 | 17898.8056 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 285064.0573 | 201745.7296 | 17898.8056 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 142532.0286 | 100312.9209 | 8949.4028 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 142532.0286 | 100319.6247 | 8949.4028 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 306197.8803 | 214839.5909 | 18230.3475 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 306197.8803 | 214845.7865 | 18230.3475 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 153098.9402 | 107294.3805 | 9115.1738 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 153098.9402 | 107295.9258 | 9115.1738 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 350172.4414 | 248233.8186 | 13223.0407 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 350172.4414 | 248303.9823 | 13223.0407 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 175086.2207 | 123333.7209 | 6611.5203 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 175086.2207 | 123351.0387 | 6611.5203 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 376133.2113 | 264009.8404 | 13467.9729 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 376133.2113 | 264025.8284 | 13467.9729 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 188066.6057 | 131825.5286 | 6733.9864 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 188066.6057 | 131829.5147 | 6733.9864 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 107236.9789 | 105977.9601 | 25628.5592 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 115460.3437 | 114451.9575 | 26403.363 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 53618.4894 | 52350.1631 | 12814.2796 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 57730.1719 | 56713.7499 | 13201.6815 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 115187.2177 | 108866.3631 | 26103.2804 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 124020.239 | 118953.1565 | 26892.436 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 57593.6088 | 51262.7567 | 13051.6402 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 62010.1195 | 56934.4055 | 13446.218 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 132801.1264 | 130391.7918 | 27688.4968 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 140118.0002 | 138187.9144 | 28101.2669 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 66400.5632 | 63969.2617 | 13844.2484 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 70059.0001 | 68110.3275 | 14050.6335 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 142646.617 | 130518.3279 | 28201.3746 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 150505.9426 | 140782.4364 | 28621.7905 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 71323.3085 | 59171.4239 | 14100.6873 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 75252.9713 | 65509.5002 | 14310.8952 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 153840.759 | 149443.3333 | 28688.8879 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 162913.7746 | 159392.0232 | 28954.1975 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 76920.3795 | 72476.7329 | 14344.444 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 81456.8873 | 77895.8826 | 14477.0987 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 165246.067 | 143062.3163 | 29220.296 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 174991.7298 | 157208.1092 | 29490.52 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 82623.0335 | 60389.6352 | 14610.148 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 87495.8649 | 69670.0808 | 14745.26 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 173304.4668 | 165613.8145 | 29147.8458 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 183983.4138 | 177826.363 | 29233.7692 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 86652.2334 | 78870.9916 | 14573.9229 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 91991.7069 | 85757.5338 | 14616.8846 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 186152.7577 | 147279.7612 | 29687.7552 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 197623.4109 | 166466.3657 | 29775.2703 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 93076.3789 | 65202.1849 | 14843.8776 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 98811.7055 | 69223.1166 | 14887.6351 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 114890.4761 | 102264.3156 | 26353.2757 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 119716.9499 | 109603.0505 | 26761.0981 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 57445.2381 | 44719.1278 | 13176.6378 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 59858.4749 | 49661.0649 | 13380.549 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 123408.1231 | 86473.1926 | 26841.421 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 128592.4176 | 90109.7421 | 27256.7975 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 61704.0615 | 43214.7086 | 13420.7105 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 64296.2088 | 45031.0961 | 13628.3987 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 141235.8462 | 117022.258 | 28158.0286 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 147497.5264 | 128116.7483 | 28446.3166 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 70617.9231 | 49573.7493 | 14079.0143 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 73748.7632 | 54171.7972 | 14223.1583 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 151706.6625 | 106325.7569 | 28679.6036 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 158432.5656 | 111045.8725 | 28973.2315 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 75853.3313 | 53130.0849 | 14339.8018 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 79216.2828 | 55487.144 | 14486.6158 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 167496.4322 | 123139.311 | 29053.5795 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 174938.5318 | 139476.1774 | 29168.1841 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 83748.2161 | 58820.4651 | 14526.7898 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 87469.2659 | 61443.358 | 14584.092 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 179914.1323 | 126122.4702 | 29591.7429 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 187907.9675 | 131734.9907 | 29708.4703 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 89957.0661 | 63015.5576 | 14795.8714 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 93953.9838 | 65817.6042 | 14854.2351 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 194350.474 | 137096.9463 | 29216.3933 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 202620.2662 | 142979.9774 | 29136.7727 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 97175.237 | 68284.5573 | 14608.1967 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 101310.1331 | 71202.3886 | 14568.3864 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 208759.0549 | 146374.3419 | 29757.5725 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 217641.9455 | 152614.0555 | 29676.4771 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 104379.5275 | 73126.3696 | 14878.7863 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 108820.9728 | 76240.7969 | 14838.2385 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 135578.4262 | 95427.7652 | 27853.7283 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 137906.8213 | 97076.748 | 27984.1383 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 67789.2131 | 47582.8068 | 13926.8642 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 68953.4106 | 48402.5014 | 13992.0691 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 145629.8177 | 102061.904 | 28369.6667 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 148130.8333 | 103817.0273 | 28502.4922 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 72814.9089 | 51000.6762 | 14184.8333 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 74065.4167 | 51877.1337 | 14251.2461 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 175022.5213 | 123375.1906 | 29169.1575 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 177712.0791 | 125287.5528 | 29196.6575 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 87511.2606 | 61471.9879 | 14584.5788 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 88856.0396 | 62420.7106 | 14598.3287 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 187998.1838 | 131797.4324 | 29709.4618 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 190887.1376 | 133826.5392 | 29737.4711 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 93999.0919 | 65849.0028 | 14854.7309 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 95443.5688 | 66861.8444 | 14868.7355 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 218593.9289 | 154330.4987 | 28832.6505 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 221361.2421 | 156309.5402 | 28761.294 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 109296.9645 | 76835.1562 | 14416.3253 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 110680.621 | 77814.1241 | 14380.647 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 234799.8493 | 164663.4981 | 29366.7216 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 237772.323 | 166753.8707 | 29294.0433 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 117399.9247 | 82255.7781 | 14683.3608 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 118886.1615 | 83298.5506 | 14647.0216 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 266820.9215 | 188678.3642 | 26931.2894 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 269440.6595 | 190571.0686 | 26793.4576 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 133410.4607 | 93860.8391 | 13465.6447 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 134720.3297 | 94792.343 | 13396.7288 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 286602.2513 | 201060.6386 | 27430.1413 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 289416.2091 | 203043.9156 | 27289.7565 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 143301.1256 | 100420.4336 | 13715.0706 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 144708.1046 | 101408.6893 | 13644.8782 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 154486.7803 | 108815.37 | 28710.897 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 154892.8942 | 109105.3499 | 28724.4827 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 77243.3902 | 54238.5046 | 14355.4485 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 77446.4471 | 54382.062 | 14362.2413 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 165939.9825 | 116314.0588 | 29242.7128 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 166376.2045 | 116620.7284 | 29256.5501 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 82969.9913 | 58117.9854 | 14621.3564 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 83188.1023 | 58270.9913 | 14628.2751 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 203793.8037 | 143806.4811 | 29120.9958 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 204218.6352 | 144115.7129 | 29115.0174 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 101896.9019 | 71614.3801 | 14560.4979 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 102109.3176 | 71766.0121 | 14557.5087 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 218902.4857 | 153497.5973 | 29660.408 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 219358.813 | 153819.7501 | 29654.3188 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 109451.2429 | 76682.2767 | 14830.204 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 109679.4065 | 76842.6711 | 14827.1594 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 258750.4656 | 182924.7462 | 27336.3018 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 259151.8189 | 183231.6637 | 27316.8832 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 129375.2328 | 91010.2945 | 13668.1509 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 129575.9094 | 91157.1997 | 13658.4416 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 277933.4752 | 194968.5237 | 27842.6558 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 278364.5837 | 195276.2486 | 27822.8775 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 138966.7376 | 97380.3785 | 13921.3279 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 139182.2918 | 97532.7507 | 13911.4388 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 319432.339 | 226216.9987 | 23677.9663 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 319781.3007 | 226520.2235 | 23653.5841 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 159716.1695 | 112451.1103 | 11838.9831 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 159890.6503 | 112587.8164 | 11826.792 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 343114.1269 | 240782.1479 | 24116.5564 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 343488.9596 | 241057.9914 | 24091.7226 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 171557.0634 | 120240.3206 | 12058.2782 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 171744.4798 | 120374.8689 | 12045.8613 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 158956.8064 | 111982.9849 | 28849.9468 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 158956.8064 | 111985.461 | 28849.9468 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 79478.4032 | 55812.6177 | 14424.9734 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 79478.4032 | 55813.2328 | 14424.9734 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 170741.4034 | 119683.9605 | 29384.3383 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 170741.4034 | 119684.5304 | 29384.3383 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 85370.7017 | 59800.7073 | 14692.1691 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 85370.7017 | 59800.8495 | 14692.1691 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 210350.5144 | 148467.9747 | 29013.2499 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 210350.5144 | 148476.1737 | 29013.2499 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 105175.2572 | 73927.07 | 14506.625 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 105175.2572 | 73929.1028 | 14506.625 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 225945.2919 | 158444.0958 | 29550.6662 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 225945.2919 | 158445.9772 | 29550.6662 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 112972.6459 | 79151.3871 | 14775.3331 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 112972.6459 | 79151.8566 | 14775.3331 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 267601.9808 | 189235.7284 | 26890.5124 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 267601.9808 | 189259.5868 | 26890.5124 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 133800.9904 | 94136.8457 | 13445.2562 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 133800.9904 | 94142.7494 | 13445.2562 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 287441.2161 | 201650.3547 | 27388.6089 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 287441.2161 | 201655.8129 | 27388.6089 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 143720.6081 | 100714.6805 | 13694.3045 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 143720.6081 | 100716.0421 | 13694.3045 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 330711.2058 | 234272.5814 | 22875.9813 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 330711.2058 | 234335.0737 | 22875.9813 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 165355.6029 | 116438.4739 | 11437.9906 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 165355.6029 | 116453.9093 | 11437.9906 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 355229.1761 | 249299.4816 | 23299.7162 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 355229.1761 | 249313.7375 | 23299.7162 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 177614.5881 | 124489.7712 | 11649.8581 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 177614.5881 | 124493.3259 | 11649.8581 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 87882.8273 | 86620.4488 | 27889.144 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 95717.7037 | 94706.5695 | 29271.6126 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 43941.4136 | 42671.4074 | 13944.572 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 47858.8519 | 46841.0559 | 14635.8063 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 94398.2054 | 88073.7421 | 28405.7383 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 102813.9369 | 97743.9025 | 29813.8146 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 47199.1027 | 40866.4462 | 14202.8692 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 51406.9684 | 46329.7785 | 14906.9073 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 112271.3125 | 109855.1861 | 31789.958 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 119267.8438 | 117332.2264 | 32703.697 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 56135.6562 | 53700.9589 | 15894.979 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 59633.9219 | 57682.4835 | 16351.8485 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 120594.7822 | 108459.1978 | 32378.8076 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 128110.0161 | 118380.5682 | 33309.472 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 60297.3911 | 48141.8589 | 16189.4038 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 64055.0081 | 54308.5661 | 16654.736 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 132406.7405 | 127996.4353 | 34200.3273 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 141104.9309 | 137572.67 | 35045.0194 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 66203.3703 | 61753.2839 | 17100.1636 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 70552.4654 | 66986.2059 | 17522.5097 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 142222.9925 | 120025.4074 | 34833.8245 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 151566.0415 | 133771.1323 | 35694.163 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 71111.4963 | 49806.7005 | 17416.9123 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 75783.0208 | 57951.5924 | 17847.0815 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 151076.4384 | 143362.5481 | 35881.3388 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 161335.0061 | 155158.9678 | 36604.8501 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 75538.2192 | 67745.3583 | 17940.6694 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 80667.5031 | 74423.8362 | 18302.4251 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 162276.8077 | 123378.8503 | 36545.9737 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 173295.9159 | 142118.4754 | 37282.8867 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 81138.4038 | 56833.9027 | 18272.9868 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 86647.958 | 60695.7995 | 18641.4434 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 95174.4247 | 82513.9599 | 29179.8919 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 99777.215 | 89635.497 | 29938.0892 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 47587.2124 | 34843.9499 | 14589.946 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 49888.6075 | 39677.2882 | 14969.0446 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 102230.3807 | 71621.306 | 29720.395 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 107174.4085 | 75088.0985 | 30492.6365 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 51115.1904 | 35795.6368 | 14860.1975 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 53587.2043 | 37527.5389 | 15246.3182 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 120337.3213 | 96054.3813 | 32835.9921 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 126330.7552 | 106893.6688 | 33542.4986 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 60168.6606 | 42220.5265 | 16417.9961 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 63165.3776 | 44328.7771 | 16771.2493 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 129258.7815 | 90576.2976 | 33444.2176 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 135696.5512 | 95092.5249 | 34163.8108 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 64629.3908 | 45264.3487 | 16722.1088 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 67848.2756 | 47520.0132 | 17081.9054 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 145501.4309 | 102446.2444 | 35430.5709 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 152645.5117 | 117075.2852 | 36000.7367 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 72750.7154 | 51073.8779 | 17715.2855 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 76322.7558 | 53589.4535 | 18000.3683 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 156288.4853 | 109539.6886 | 36086.8562 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 163962.2075 | 114925.3439 | 36667.5831 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 78144.2426 | 54735.3854 | 18043.4281 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 81981.1038 | 57424.6972 | 18333.7916 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 171303.3848 | 120728.6121 | 37184.5136 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 179261.3919 | 126378.9763 | 37565.8503 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 85651.6924 | 60159.5532 | 18592.2568 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 89630.696 | 62964.6908 | 18782.9251 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 184003.3213 | 128991.0752 | 37873.2874 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 192551.312 | 134993.0585 | 38261.6876 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 92001.6607 | 64448.3155 | 18936.6437 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 96275.656 | 67444.7045 | 19130.8438 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 114926.2411 | 80823.7599 | 32146.6885 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 117152.7818 | 82397.7384 | 32436.3766 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 57463.1205 | 40317.8137 | 16073.3443 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 58576.3909 | 41100.9392 | 16218.1883 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 123446.5395 | 86499.5292 | 32742.146 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 125838.1495 | 88177.2163 | 33037.1999 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 61723.2698 | 43228.0158 | 16371.073 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 62919.0747 | 44065.9686 | 16518.6 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 152726.1673 | 107562.139 | 36006.787 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 155309.3057 | 109394.9662 | 36196.1049 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 76363.0837 | 53617.1157 | 18003.3935 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 77654.6529 | 54527.3425 | 18098.0524 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 164048.8427 | 114985.463 | 36673.7456 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 166823.4875 | 116933.3977 | 36866.5702 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 82024.4214 | 57454.8883 | 18336.8728 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 83411.7438 | 58427.4334 | 18433.2851 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 194647.4235 | 137294.6866 | 38114.2011 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 197314.7868 | 139197.2565 | 38185.5097 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 97323.7117 | 68385.9794 | 19057.1005 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 98657.3934 | 69328.3563 | 19092.7549 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 209078.0194 | 146595.2936 | 38820.1956 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 211943.1333 | 148609.028 | 38892.825 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 104539.0097 | 73237.4274 | 19410.0978 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 105971.5666 | 74242.2532 | 19446.4125 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 241202.1483 | 170395.6815 | 38492.3326 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 243734.9342 | 172218.8504 | 38465.996 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 120601.0742 | 84807.5162 | 19246.1663 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 121867.4671 | 85706.449 | 19232.998 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 259084.1766 | 181717.6455 | 39205.3312 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 261804.7358 | 183633.5708 | 39178.5068 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 129542.0883 | 90769.0537 | 19602.6656 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 130902.3679 | 91724.1281 | 19589.2534 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 133025.7893 | 93617.8275 | 34264.1556 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 133414.97 | 93894.7734 | 34303.986 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 66512.8947 | 46683.6356 | 17132.0778 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 66707.485 | 46820.9736 | 17151.993 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 142887.9358 | 100137.2543 | 34898.8352 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 143305.9692 | 100430.9209 | 34939.4033 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 71443.9679 | 50039.6856 | 17449.4176 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 71652.9846 | 50186.2579 | 17469.7017 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 180391.1156 | 127174.6321 | 37614.3951 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 180800.1119 | 127470.5315 | 37631.6352 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 90195.5578 | 63361.3028 | 18807.1975 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 90400.056 | 63506.8367 | 18815.8176 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 193764.7901 | 135843.6153 | 38311.1316 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 194204.1082 | 136153.348 | 38328.691 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 96882.3951 | 67869.7022 | 19155.5658 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 97102.0541 | 68024.0152 | 19164.3455 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 233401.9078 | 164844.0402 | 38546.0077 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 233789.7378 | 165136.9421 | 38544.3431 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 116700.9539 | 82054.7143 | 19273.0038 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 116894.8689 | 82195.7648 | 19272.1715 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 250705.6488 | 175831.6293 | 39260.0005 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 251122.2314 | 176128.1514 | 39258.3051 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 125352.8244 | 87831.3147 | 19630.0003 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 125561.1157 | 87978.345 | 19629.1526 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 292132.5133 | 206677.168 | 37243.7874 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 292470.7497 | 206963.4356 | 37231.0855 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 146066.2566 | 102789.5806 | 18621.8937 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 146235.3749 | 102920.2097 | 18615.5428 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 313790.3712 | 220156.8675 | 37933.659 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 314153.6835 | 220422.5068 | 37920.722 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 156895.1856 | 109952.3877 | 18966.8295 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 157076.8417 | 110082.3708 | 18960.361 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 137310.3888 | 96649.0049 | 34690.1857 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 137310.3888 | 96650.8493 | 34690.1857 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 68655.1944 | 48191.2026 | 17345.0928 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 68655.1944 | 48191.6611 | 17345.0928 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 147490.1831 | 103366.2098 | 35332.7566 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 147490.1831 | 103366.6349 | 35332.7566 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 73745.0916 | 51652.3162 | 17666.3783 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 73745.0916 | 51652.4223 | 17666.3783 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 186704.9376 | 131655.7528 | 37861.0657 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 186704.9376 | 131662.2 | 37861.0657 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 93352.4688 | 65586.4198 | 18930.5329 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 93352.4688 | 65588.0198 | 18930.5329 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 200546.7006 | 140605.1181 | 38562.3713 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 200546.7006 | 140606.5997 | 38562.3713 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 100273.3503 | 70246.9081 | 19281.1857 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 100273.3503 | 70247.2779 | 19281.1857 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 241957.2449 | 170933.5537 | 38484.9276 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 241957.2449 | 170953.0201 | 38484.9276 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 120978.6224 | 85074.1105 | 19242.4638 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 120978.6224 | 85078.9322 | 19242.4638 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 259895.2538 | 182287.5398 | 39197.7891 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 259895.2538 | 182292.0001 | 39197.7891 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 129947.6269 | 91053.465 | 19598.8945 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 129947.6269 | 91054.5778 | 19598.8945 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 303067.3106 | 214475.0337 | 36808.781 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 303067.3106 | 214527.4091 | 36808.781 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 151533.6553 | 106652.3621 | 18404.3905 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 151533.6553 | 106665.3119 | 18404.3905 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 325535.8427 | 228411.6614 | 37490.595 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 325535.8427 | 228423.6284 | 37490.595 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 162767.9214 | 114071.5301 | 18745.2975 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 162767.9214 | 114074.5147 | 18745.2975 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 40
323.15 | 40
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)