## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| schema_version | 2.0.0 |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| description | DX System with Constant Efficiency |  | ✓
| id | 123e4567-e89b-12d3-a456-426614174000 |  | ✓
| data_timestamp | 2020-05-07T00:00Z |  | ✓
| data_version | 1 |  | ✓
| disclaimer | Example data not to be used for simulation
| notes | An example representation of the ASHRAE 90.1 Appendix G minimum requirements for unitary air-conditioners
description
description.product_information
| outdoor_unit_manufacturer | ABC HVAC
| outdoor_unit_model_number | DX AB12
| indoor_unit_manufacturer | ABC HVAC
| indoor_unit_model_number | DX AB12
| refrigerant | R-410A
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.25 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: The version of the schema the data complies with
Note on B5: Data model name
Note on B6: Schema name or identifier
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Characterization of accuracy, limitations, and applicability of this data
Note on B12: Additional Information
Note on A13: Data group describing product and rating information
Note on A14: Data group describing product information
Note on B15: Outdoor unit manufacturer name
Note on B16: Outdoor unit model number
Note on B17: Indoor unit manufacturer name
Note on B18: Indoor unit model number
Note on B19: Refrigerant used
Note on B20: Type of compressor
Note on A21: Data group containing performance information
Note on B22: Method used to control different speeds of the compressor
Note on B23: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A24: Data group describing cooling performance over a range of conditions
Note on A25: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
283.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 120374.6053 | 119117.867 | 15547.7769 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 129305.0778 | 128298.6187 | 15827.8608 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 60187.3026 | 58920.1166 | 7773.8884 | NORMAL
283.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 64652.5389 | 63637.0805 | 7913.9304 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 127229.7579 | 120910.9937 | 15871.5078 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 136668.8074 | 131603.4854 | 16157.4235 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 63614.8789 | 57285.072 | 7935.7539 | NORMAL
283.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 68334.4037 | 63259.5699 | 8078.7117 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 148227.3776 | 145823.1464 | 16259.2927 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 156244.8759 | 154319.0686 | 16388.3818 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 74113.6888 | 71684.939 | 8129.6463 | NORMAL
283.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 78122.438 | 76175.9046 | 8194.1909 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 156668.7037 | 144545.0534 | 16597.8385 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 165142.7864 | 155423.1633 | 16729.6155 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 78334.3518 | 66184.7867 | 8298.9193 | NORMAL
283.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 82571.3932 | 72829.8637 | 8364.8077 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 171329.457 | 166942.5401 | 16565.8034 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 181334.4838 | 177821.6092 | 16647.0334 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 85664.7285 | 81226.3363 | 8282.9017 | NORMAL
283.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 90667.2419 | 87110.6756 | 8323.5167 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 181086.4116 | 158912.1793 | 16910.7314 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 191661.2097 | 173885.622 | 16993.6526 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 90543.2058 | 68314.5667 | 8455.3657 | NORMAL
283.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 95830.6049 | 78008.8373 | 8496.8263 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 192820.9823 | 185150.7333 | 16715.0426 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 204655.5833 | 198515.8632 | 16766.696 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 96410.4911 | 88639.451 | 8357.5213 | NORMAL
283.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 102327.7917 | 96102.2839 | 8383.348 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 203801.847 | 164947.3015 | 17063.0779 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 216310.4107 | 185169.0319 | 17115.8069 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 101900.9235 | 71389.0464 | 8531.539 | NORMAL
283.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 108155.2054 | 76923.1535 | 8557.9034 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 128685.2685 | 116083.1097 | 15810.1821 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 133938.9765 | 123844.9187 | 15952.3144 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 64342.6342 | 51628.5248 | 7905.0911 | NORMAL
283.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 66969.4882 | 56781.9991 | 7976.1572 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 136013.7008 | 95315.8978 | 16139.3767 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 141566.5996 | 99211.8293 | 16284.4684 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 68006.8504 | 47631.3573 | 8069.6884 | NORMAL
283.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 70783.2998 | 49577.0955 | 8142.2342 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 157471.3758 | 133311.6652 | 16405.7872 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 164349.2874 | 145013.3386 | 16493.1122 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 78735.6879 | 55290.5718 | 8202.8936 | NORMAL
283.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 82174.6437 | 62620.0923 | 8246.5561 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 166439.1336 | 116665.2031 | 16747.3833 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 173708.7319 | 121768.1316 | 16836.5266 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 83219.5668 | 58293.1225 | 8373.6916 | NORMAL
283.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 86854.366 | 60841.0306 | 8418.2633 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 186396.8106 | 142153.8289 | 16679.7917 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 194630.0019 | 159262.9313 | 16723.9024 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 93198.4053 | 65482.5891 | 8339.8959 | NORMAL
283.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 97315.001 | 68386.5731 | 8361.9512 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 197011.8284 | 138127.2382 | 17027.093 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 205713.8876 | 144238.752 | 17072.1222 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 98505.9142 | 69008.8361 | 8513.5465 | NORMAL
283.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 102856.9438 | 72059.5688 | 8536.0611 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 216171.1322 | 152621.933 | 16808.2122 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 225374.6911 | 163251.8203 | 16840.8329 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 108085.5661 | 75984.0367 | 8404.1061 | NORMAL
283.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 112687.3455 | 79234.2726 | 8420.4165 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 228481.7528 | 160228.361 | 17158.1875 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 238209.4405 | 167063.7458 | 17191.4874 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 114240.8764 | 80041.3308 | 8579.0937 | NORMAL
283.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 119104.7203 | 83452.5132 | 8595.7437 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 151268.423 | 106539.1998 | 16311.516 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 153820.0149 | 108348.7146 | 16352.2109 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 75634.2115 | 53106.2747 | 8155.758 | NORMAL
283.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 76910.0074 | 54005.1544 | 8176.1054 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 159882.932 | 112063.9516 | 16651.1492 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 162579.8332 | 113957.0107 | 16692.6914 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 79941.466 | 55995.4772 | 8325.5746 | NORMAL
283.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 81289.9166 | 56940.6984 | 8346.3457 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 194723.0027 | 137370.7302 | 16724.3468 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 197702.0828 | 139492.7112 | 16738.0479 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 97361.5014 | 68418.1726 | 8362.1734 | NORMAL
283.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 98851.0414 | 69469.9512 | 8369.0239 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 205812.1846 | 144306.708 | 17072.5758 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 208960.9188 | 146518.9874 | 17086.5622 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 102906.0923 | 72093.7601 | 8536.2879 | NORMAL
283.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 104480.4594 | 73197.8558 | 8543.2811 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 243193.2 | 171864.1214 | 16918.0861 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 246285.3474 | 174080.7783 | 16934.9091 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 121596.6 | 85522.9014 | 8459.043 | NORMAL
283.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 123142.6737 | 86618.0914 | 8467.4545 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 257042.6867 | 180293.7939 | 17270.3491 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 260310.9272 | 182593.1605 | 17287.5224 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 128521.3434 | 90055.8267 | 8635.1746 | NORMAL
283.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 130155.4636 | 91202.6058 | 8643.7612 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 297277.613 | 210460.2113 | 17496.0018 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 300226.5023 | 212598.1694 | 17550.5003 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 148638.8065 | 104635.2918 | 8748.0009 | NORMAL
283.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 150113.2511 | 105685.6606 | 8775.2501 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 314207.1256 | 220472.8141 | 17860.298 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 317323.9497 | 222670.9398 | 17915.9312 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 157103.5628 | 110104.2924 | 8930.149 | NORMAL
283.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 158661.9748 | 111199.2597 | 8957.9656 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 172041.0382 | 121265.9688 | 16572.4131 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 172488.4297 | 121586.1727 | 16576.4981 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 86020.5191 | 60422.9488 | 8286.2066 | NORMAL
283.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 86244.2148 | 60581.283 | 8288.2491 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 181838.5163 | 127474.3952 | 16917.4787 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 182311.3861 | 127806.9719 | 16921.6487 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 90919.2582 | 63690.3047 | 8458.7393 | NORMAL
283.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 91155.6931 | 63856.2006 | 8460.8244 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 226681.9511 | 160102.4891 | 16845.6857 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 227155.2643 | 160448.503 | 16847.4638 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 113340.9755 | 79693.3709 | 8422.8428 | NORMAL
283.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 113577.6322 | 79862.6747 | 8423.7319 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 239591.147 | 168032.34 | 17196.4412 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 240091.4147 | 168385.7933 | 17198.2563 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 119795.5735 | 83936.4602 | 8598.2206 | NORMAL
283.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 120045.7074 | 84112.369 | 8599.1282 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 288199.7878 | 203974.7045 | 17346.071 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 288650.9984 | 204322.9055 | 17352.9125 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 144099.8939 | 101425.5614 | 8673.0355 | NORMAL
283.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 144325.4992 | 101591.4889 | 8676.4562 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 304612.3319 | 213727.3394 | 17707.2454 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 305089.2383 | 214068.3372 | 17714.2294 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 152306.166 | 106738.8473 | 8853.6227 | NORMAL
283.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 152544.6191 | 106907.5514 | 8857.1147 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 356683.2363 | 252942.3832 | 19260.3185 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 357078.4618 | 253292.8465 | 19277.3939 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 178341.6182 | 125649.8627 | 9630.1592 | NORMAL
283.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 178539.2309 | 125806.4075 | 9638.697 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 376995.8097 | 264624.3219 | 19661.3507 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 377413.5427 | 264933.0164 | 19678.7817 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 188497.9049 | 132130.097 | 9830.6754 | NORMAL
283.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 188706.7714 | 132280.3629 | 9839.3909 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 176968.0945 | 124762.3152 | 16614.54 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 176968.0945 | 124765.3887 | 16614.54 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 88484.0473 | 62159.2084 | 8307.27 | NORMAL
283.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 88484.0473 | 62159.9714 | 8307.27 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 187046.1611 | 131130.3303 | 16960.4827 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 187046.1611 | 131131.0144 | 16960.4827 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 93523.0806 | 65515.6234 | 8480.2414 | NORMAL
283.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 93523.0806 | 65515.7941 | 8480.2414 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 233991.1643 | 165308.0972 | 16874.742 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 233991.1643 | 165318.2618 | 16874.742 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 116995.5822 | 82273.7362 | 8437.371 | NORMAL
283.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 116995.5822 | 82276.2539 | 8437.371 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 247316.6089 | 173460.022 | 17226.1025 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 247316.6089 | 173462.2769 | 17226.1025 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 123658.3045 | 86645.3295 | 8613.0513 | NORMAL
283.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 123658.3045 | 86645.8921 | 8613.0513 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 298156.6982 | 211088.9221 | 17511.9409 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 298156.6982 | 211118.6095 | 17511.9409 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 149078.3491 | 104946.2816 | 8755.9705 | NORMAL
283.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 149078.3491 | 104953.619 | 8755.9705 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 315136.2733 | 221126.1836 | 17876.569 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 315136.2733 | 221132.747 | 17876.569 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 157568.1367 | 110430.2343 | 8938.2845 | NORMAL
283.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 157568.1367 | 110431.8712 | 8938.2845 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 369464.696 | 262093.2974 | 19853.3407 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 369464.696 | 262171.5159 | 19853.3407 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 184732.348 | 130173.8719 | 9926.6704 | NORMAL
283.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 184732.348 | 130193.164 | 9926.6704 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 390505.1543 | 274126.0887 | 20266.7207 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 390505.1543 | 274143.3254 | 20266.7207 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 195252.5772 | 136869.6517 | 10133.3604 | NORMAL
283.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 195252.5772 | 136873.9486 | 10133.3604 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 125427.9501 | 124172.089 | 18179.8051 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 134005.467 | 132999.6622 | 18334.6148 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 62713.975 | 61447.2276 | 9089.9026 | NORMAL
293.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 67002.7335 | 65987.6023 | 9167.3074 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 132570.8831 | 126253.0461 | 18558.3393 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 141636.8766 | 136572.2462 | 18716.3723 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 66285.4415 | 59956.0982 | 9279.1696 | NORMAL
293.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 70818.4383 | 65743.9504 | 9358.1862 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 152212.5911 | 149809.6783 | 18468.381 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 159939.0469 | 158014.2197 | 18457.3562 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 76106.2956 | 73678.205 | 9234.1905 | NORMAL
293.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 79969.5234 | 78023.4801 | 9228.6781 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 160880.8691 | 148758.6123 | 18852.9238 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 169047.3349 | 159328.7477 | 18841.6695 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 80440.4345 | 68291.5661 | 9426.4619 | NORMAL
293.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 84523.6674 | 74782.6559 | 9420.8347 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 174493.1683 | 170108.1526 | 18347.5034 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 184157.653 | 180646.1388 | 18220.713 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 87246.5842 | 82809.1426 | 9173.7517 | NORMAL
293.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 92078.8265 | 88522.9404 | 9110.3565 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 184430.2916 | 162258.0686 | 18729.5293 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 194645.1541 | 176871.0043 | 18600.0989 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 92215.1458 | 69987.5114 | 9364.7647 | NORMAL
293.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 97322.5771 | 79501.5284 | 9300.0495 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 195263.3072 | 187595.6115 | 18032.3467 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 206715.9786 | 200577.9859 | 17799.9673 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 97631.6536 | 89861.89 | 9016.1734 | NORMAL
293.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 103357.9893 | 97133.3453 | 8899.9836 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 206383.2586 | 167531.4118 | 18407.8105 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 218488.1425 | 187348.5894 | 18170.5926 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 103191.6293 | 72294.0299 | 9203.9053 | NORMAL
293.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 109244.0712 | 78012.9322 | 9085.2963 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 133409.8143 | 120815.8759 | 18325.9336 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 138460.2979 | 128372.548 | 18390.3252 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 66704.9072 | 53994.9079 | 9162.9668 | NORMAL
293.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 69230.149 | 59045.8137 | 9195.1626 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 141007.3024 | 98819.3728 | 18707.5104 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 146345.4035 | 102564.9063 | 18773.2427 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 70503.6512 | 49381.1046 | 9353.7552 | NORMAL
293.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 73172.7017 | 51251.6537 | 9386.6213 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 161121.6022 | 136974.0048 | 18452.5673 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 167755.8024 | 148428.9157 | 18411.6381 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 80560.8011 | 56576.3994 | 9226.2837 | NORMAL
293.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 83877.9012 | 64327.8809 | 9205.8191 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 170297.2349 | 119373.2802 | 18836.7808 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 177309.2428 | 124295.6993 | 18794.9994 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 85148.6175 | 59645.3075 | 9418.3904 | NORMAL
293.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 88654.6214 | 62103.01 | 9397.4997 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 189050.849 | 144823.895 | 18142.8098 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 197013.2796 | 161657.7412 | 17999.1024 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 94525.4245 | 66418.5053 | 9071.4049 | NORMAL
293.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 98506.6398 | 69227.2894 | 8999.5512 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 199817.0103 | 140097.1503 | 18520.5737 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 208232.8893 | 146007.948 | 18373.874 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 99908.5051 | 69992.2191 | 9260.2868 | NORMAL
293.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 104116.4446 | 72942.6912 | 9186.937 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 217869.3111 | 153831.2864 | 17545.5401 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 226789.6021 | 164678.6741 | 17327.6698 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 108934.6555 | 76583.5231 | 8772.77 | NORMAL
293.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 113394.8011 | 79733.9494 | 8663.8349 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 230276.6404 | 161489.3787 | 17910.8677 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 239704.9286 | 168114.5857 | 17688.4611 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 115138.3202 | 80670.689 | 8955.4339 | NORMAL
293.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 119852.4643 | 83976.9322 | 8844.2305 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 155142.458 | 109284.9196 | 18468.4668 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 157601.5114 | 111029.4528 | 18464.4678 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 77571.229 | 54470.6213 | 9234.2334 | NORMAL
293.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 78800.7557 | 55337.0609 | 9232.2339 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 163977.5874 | 114937.7842 | 18853.0114 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 166576.6803 | 116762.3308 | 18848.9291 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 81988.7937 | 57430.4982 | 9426.5057 | NORMAL
293.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 83288.3401 | 58341.4748 | 9424.4646 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 197103.2514 | 139063.1951 | 17997.3694 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 199985.6456 | 141116.8958 | 17940.6633 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 98551.6257 | 69257.7938 | 8998.6847 | NORMAL
293.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 99992.8228 | 70275.5825 | 8970.3317 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 208327.9849 | 146073.6316 | 18372.105 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 211374.5271 | 148214.2418 | 18314.2182 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 104163.9924 | 72975.7543 | 9186.0525 | NORMAL
293.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 105687.2636 | 74044.0491 | 9157.1091 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 244074.2271 | 172492.7206 | 16884.5467 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 247075.5664 | 174644.7893 | 16806.3014 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 122037.1135 | 85834.2097 | 8442.2733 | NORMAL
293.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 123537.7832 | 86897.3627 | 8403.1507 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 257973.8869 | 180948.2782 | 17236.1114 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 261146.148 | 183180.2312 | 17156.2369 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 128986.9435 | 90382.4069 | 8618.0557 | NORMAL
293.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 130573.074 | 91495.5361 | 8578.1184 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 296639.325 | 210003.2035 | 15596.6132 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 299509.2151 | 212084.3577 | 15537.0398 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 148319.6625 | 104409.3611 | 7798.3066 | NORMAL
293.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 149754.6076 | 105431.7078 | 7768.5199 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 313532.4881 | 219998.301 | 15921.3609 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 316565.8141 | 222137.6446 | 15860.5472 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 156766.244 | 109867.6035 | 7960.6805 | NORMAL
293.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 158282.9071 | 110933.2634 | 7930.2736 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 175180.244 | 123494.3559 | 18339.7835 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 175612.2511 | 123803.8155 | 18334.8228 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 87590.122 | 61529.366 | 9169.8918 | NORMAL
293.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 87806.1255 | 61682.3216 | 9167.4114 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 185156.4952 | 129803.8882 | 18721.6487 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 185613.1044 | 130125.0877 | 18716.5847 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 92578.2476 | 64853.3223 | 9360.8243 | NORMAL
293.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 92806.5522 | 65013.5283 | 9358.2923 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 228057.0556 | 161082.4835 | 17295.934 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 228515.982 | 161418.3858 | 17284.4027 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 114028.5278 | 80178.9836 | 8647.967 | NORMAL
293.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 114257.991 | 80343.2415 | 8642.2013 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 241044.5617 | 169053.6103 | 17656.0644 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 241529.6232 | 169396.41 | 17644.293 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 120522.2808 | 84446.1239 | 8828.0322 | NORMAL
293.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 120764.8116 | 84616.7082 | 8822.1465 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 287807.0002 | 203693.6319 | 15789.8609 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 288245.9243 | 204032.9593 | 15779.9297 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 143903.5001 | 101286.568 | 7894.9305 | NORMAL
293.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 144122.9622 | 101448.1277 | 7889.9648 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 304197.1756 | 213435.37 | 16118.6324 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 304661.0959 | 213767.217 | 16108.4944 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 152098.5878 | 106593.2032 | 8059.3162 | NORMAL
293.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 152330.5479 | 106757.3471 | 8054.2472 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 354517.6519 | 251386.7026 | 14819.9755 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 354903.1331 | 251729.3027 | 14818.4478 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 177258.826 | 124882.0618 | 7409.9877 | NORMAL
293.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 177451.5666 | 125034.9403 | 7409.2239 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 374706.8986 | 263013.2679 | 15128.5523 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 375114.3324 | 263314.5249 | 15126.9928 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 187353.4493 | 131326.7786 | 7564.2762 | NORMAL
293.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 187557.1662 | 131473.3829 | 7563.4964 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 179938.8337 | 126871.8925 | 18280.741 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 179938.8337 | 126875.0708 | 18280.741 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 89969.4168 | 63206.4417 | 9140.3705 | NORMAL
293.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 89969.4168 | 63207.2305 | 9140.3705 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 190186.0794 | 133334.9822 | 18661.3768 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 190186.0794 | 133335.6895 | 18661.3768 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 95093.0397 | 66616.2701 | 9330.6884 | NORMAL
293.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 95093.0397 | 66616.4467 | 9330.6884 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 235145.5959 | 166131.2478 | 17115.7808 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 235145.5959 | 166141.5138 | 17115.7808 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 117572.7979 | 82681.5233 | 8557.8904 | NORMAL
293.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 117572.7979 | 82684.066 | 8557.8904 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 248536.7836 | 174317.4948 | 17472.1601 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 248536.7836 | 174319.7721 | 17472.1601 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 124268.3918 | 87073.227 | 8736.0801 | NORMAL
293.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 124268.3918 | 87073.7952 | 8736.0801 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 297494.8221 | 210614.9973 | 15578.6795 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 297494.8221 | 210644.5515 | 15578.6795 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 148747.411 | 104711.9946 | 7789.3397 | NORMAL
293.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 148747.411 | 104719.2993 | 7789.3397 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 314436.7044 | 220634.1285 | 15903.0538 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 314436.7044 | 220640.6628 | 15903.0538 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 157218.3522 | 110184.797 | 7951.5269 | NORMAL
293.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 157218.3522 | 110186.4266 | 7951.5269 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 366986.5123 | 260311.8937 | 14800.1319 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 366986.5123 | 260389.0524 | 14800.1319 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 183493.2561 | 129294.955 | 7400.0659 | NORMAL
293.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 183493.2561 | 129313.9875 | 7400.0659 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 387885.8417 | 272282.2274 | 15108.2956 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 387885.8417 | 272299.233 | 15108.2956 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 193942.9209 | 135950.3121 | 7554.1478 | NORMAL
293.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 193942.9209 | 135954.5515 | 7554.1478 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 122897.0626 | 121640.7622 | 22227.8623 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 131121.6239 | 130115.4177 | 22471.0411 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 61448.5313 | 60181.5641 | 11113.9312 | NORMAL
303.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 65560.8119 | 64545.48 | 11235.5205 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 129895.8653 | 123577.564 | 22690.6839 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 138588.803 | 133523.7483 | 22938.926 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 64947.9326 | 58618.3571 | 11345.3419 | NORMAL
303.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 69294.4015 | 64219.7014 | 11469.463 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 148613.5723 | 146209.4689 | 22755.2515 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 156048.9855 | 154123.1263 | 22792.3054 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 74306.7862 | 71878.1003 | 11377.6258 | NORMAL
303.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 78024.4928 | 76077.9334 | 11396.1527 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 157076.8916 | 144953.3763 | 23229.0542 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 164935.7404 | 155216.0624 | 23266.8796 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 78538.4458 | 66388.9482 | 11614.5271 | NORMAL
303.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 82467.8702 | 72726.3133 | 11633.4398 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 170072.6473 | 165684.9753 | 22746.8612 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 179396.5898 | 175882.7813 | 22643.7304 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 85036.3237 | 80597.5539 | 11373.4306 | NORMAL
303.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 89698.2949 | 86141.2616 | 11321.8652 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 179758.0286 | 157582.998 | 23220.4892 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 189612.9555 | 171836.3808 | 23115.211 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 89879.0143 | 67649.9761 | 11610.2446 | NORMAL
303.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 94806.4778 | 76984.2166 | 11557.6055 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 190121.3997 | 182448.3285 | 22463.5595 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 201192.1416 | 195049.5179 | 22218.2746 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 95060.6999 | 87288.2486 | 11231.7797 | NORMAL
303.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 100596.0708 | 94369.1113 | 11109.1373 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 200948.5273 | 162090.9988 | 22931.2886 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 212649.7312 | 181505.2834 | 22680.8965 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 100474.2636 | 70388.76 | 11465.6443 | NORMAL
303.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 106324.8656 | 75091.2792 | 11340.4482 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 130550.1279 | 117951.2138 | 22456.5773 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 135397.387 | 125305.3639 | 22568.2952 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 65275.0639 | 52562.5768 | 11228.2886 | NORMAL
303.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 67698.6935 | 57512.2216 | 11284.1476 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 137984.7611 | 96698.7452 | 22924.161 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 143108.0644 | 100293.3787 | 23038.2051 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 68992.3806 | 48322.004 | 11462.0805 | NORMAL
303.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 71554.0322 | 50117.2387 | 11519.1025 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 157187.5963 | 133026.9439 | 22794.0306 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 163578.085 | 144240.0847 | 22785.4572 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 78593.7981 | 55190.6157 | 11397.0153 | NORMAL
303.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 81789.0425 | 62233.4654 | 11392.7286 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 166139.1933 | 116454.6762 | 23268.6407 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 172893.6108 | 121195.935 | 23259.8888 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 83069.5966 | 58188.0013 | 11634.3204 | NORMAL
303.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 86446.8054 | 60555.3357 | 11629.9444 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 184120.655 | 139863.9276 | 22571.947 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 191812.3249 | 156431.62 | 22429.7482 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 92060.3275 | 64680.0082 | 11285.9735 | NORMAL
303.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 95906.1624 | 67392.7234 | 11214.8741 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 194606.0492 | 136437.8737 | 23041.9329 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 202735.748 | 142147.1779 | 22896.7733 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 97303.0246 | 68165.4852 | 11520.9665 | NORMAL
303.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 101367.874 | 71015.503 | 11448.3867 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 211983.2576 | 149640.2481 | 21930.406 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 220620.2808 | 158457.2796 | 21670.974 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 105991.6288 | 74505.8173 | 10965.203 | NORMAL
303.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 110310.1404 | 77555.4552 | 10835.487 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 224055.385 | 157118.7227 | 22387.034 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 233184.2737 | 163532.8775 | 22122.2002 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 112027.6925 | 78489.3107 | 11193.517 | NORMAL
303.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 116592.1368 | 81690.3966 | 11061.1001 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 151432.2606 | 106655.302 | 22774.6914 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 153798.7757 | 108333.6603 | 22785.8792 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 75716.1303 | 53163.9703 | 11387.3457 | NORMAL
303.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 76899.3878 | 53997.6742 | 11392.9396 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 160056.0999 | 112185.4855 | 23248.8988 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 162557.3845 | 113941.2549 | 23260.3195 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 80028.05 | 56056.165 | 11624.4494 | NORMAL
303.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 81278.6922 | 56932.8309 | 11630.1598 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 191899.2678 | 135363.3455 | 22427.9724 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 194684.9761 | 137347.2512 | 22369.1851 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 95949.6339 | 67422.2174 | 11213.9862 | NORMAL
303.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 97342.4881 | 68405.6419 | 11184.5925 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 202827.6422 | 142210.6651 | 22894.9605 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 205771.9925 | 144279.2713 | 22834.9492 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 101413.8211 | 71047.4566 | 11447.4803 | NORMAL
303.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 102885.9962 | 72079.867 | 11417.4746 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 237371.0218 | 167711.1822 | 21109.9396 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 240281.5532 | 169796.7826 | 21006.2109 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 118685.5109 | 83465.922 | 10554.9698 | NORMAL
303.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 120140.7766 | 84496.5746 | 10503.1055 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 250888.9442 | 175968.9414 | 21549.4841 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 253965.2259 | 178133.0669 | 21443.5956 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 125444.4721 | 87897.7151 | 10774.742 | NORMAL
303.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 126982.613 | 88977.0915 | 10721.7978 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 288416.8047 | 204117.9556 | 19163.6167 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 291207.6957 | 206139.8339 | 19055.2703 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 144208.4024 | 101499.3781 | 9581.8083 | NORMAL
303.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 145603.8478 | 102493.095 | 9527.6351 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 304841.7076 | 213885.9896 | 19562.6354 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 307791.5356 | 215966.0093 | 19452.0331 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 152420.8538 | 106818.6518 | 9781.3177 | NORMAL
303.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 153895.7678 | 107854.8692 | 9726.0165 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 170735.2175 | 120339.1895 | 22741.3292 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 171151.8401 | 120637.4814 | 22737.7046 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 85367.6087 | 59962.7518 | 11370.6646 | NORMAL
303.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 85575.9201 | 60110.224 | 11368.8523 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 180458.3311 | 126505.429 | 23214.842 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 180898.6798 | 126815.1576 | 23211.1419 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 90229.1656 | 63206.5315 | 11607.421 | NORMAL
303.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 90449.3399 | 63361.0242 | 11605.571 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 221847.9279 | 156658.2776 | 21632.2657 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 222292.4674 | 156983.2923 | 21618.1443 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 110923.9639 | 77986.4642 | 10816.1328 | NORMAL
303.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 111146.2337 | 78145.4849 | 10809.0722 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 234481.8334 | 164442.3673 | 22082.6859 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 234951.6888 | 164774.3422 | 22068.2705 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 117240.9167 | 82144.8419 | 11041.3429 | NORMAL
303.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 117475.8444 | 82310.059 | 11034.1352 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 279829.9802 | 197987.2387 | 19498.7053 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 280256.618 | 198316.1923 | 19482.0205 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 139914.9901 | 98464.2404 | 9749.3527 | NORMAL
303.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 140128.309 | 98621.0634 | 9741.0102 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 295765.8764 | 207506.2426 | 19904.7012 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 296216.8105 | 207828.6099 | 19887.6689 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 147882.9382 | 103635.4557 | 9952.3506 | NORMAL
303.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 148108.4053 | 103794.9574 | 9943.8345 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 344767.8352 | 244385.8307 | 17152.5085 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 345143.5721 | 244717.6298 | 17141.0114 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 172383.9176 | 121426.0461 | 8576.2542 | NORMAL
303.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 172571.7861 | 121574.5376 | 8570.5057 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 364401.8444 | 255760.7057 | 17509.6526 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 364798.9791 | 256053.8836 | 17497.9161 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 182200.9222 | 127710.2733 | 8754.8263 | NORMAL
303.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 182399.4895 | 127853.0564 | 8748.9581 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 175325.3405 | 123595.9821 | 22695.3166 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 175325.3405 | 123598.9983 | 22695.3166 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 87662.6703 | 61580.165 | 11347.6583 | NORMAL
303.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 87662.6703 | 61580.9138 | 11347.6583 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 185309.8548 | 129911.2538 | 23167.8713 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 185309.8548 | 129911.9253 | 23167.8713 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 92654.9274 | 64907.0017 | 11583.9357 | NORMAL
303.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 92654.9274 | 64907.1693 | 11583.9357 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 228715.7951 | 161547.5275 | 21408.2291 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 228715.7951 | 161557.2348 | 21408.2291 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 114357.8975 | 80410.5198 | 10704.1146 | NORMAL
303.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 114357.8975 | 80412.9248 | 10704.1146 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 241740.8153 | 169541.8658 | 21853.9845 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 241740.8153 | 169544.0201 | 21853.9845 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 120870.4077 | 84690.032 | 10926.9922 | NORMAL
303.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 120870.4077 | 84690.5695 | 10926.9922 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 289248.7136 | 204712.5262 | 19131.2815 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 289248.7136 | 204740.4471 | 19131.2815 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 144624.3568 | 101793.5801 | 9565.6408 | NORMAL
303.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 144624.3568 | 101800.4833 | 9565.6408 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 305720.9925 | 214504.2081 | 19529.627 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 305720.9925 | 214510.3843 | 19529.627 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 152860.4962 | 107127.0801 | 9764.8135 | NORMAL
303.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 152860.4962 | 107128.6206 | 9764.8135 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 356924.0962 | 253081.9739 | 16798.6595 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 356924.0962 | 253154.9055 | 16798.6595 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 178462.0481 | 125727.0078 | 8399.3297 | NORMAL
303.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 178462.0481 | 125745.0043 | 8399.3297 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 377250.3862 | 264796.1318 | 17148.4358 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 377250.3862 | 264812.2152 | 17148.4358 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 188625.1931 | 132217.6049 | 8574.2179 | NORMAL
303.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 188625.1931 | 132221.6147 | 8574.2179 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 112781.9427 | 111523.8864 | 26721.6547 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 120653.5484 | 119645.8851 | 27276.6388 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 56390.9714 | 55123.1263 | 13360.8273 | NORMAL
313.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 60326.7742 | 59310.7137 | 13638.3194 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 119204.7046 | 112884.5474 | 27278.0445 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 127524.5864 | 122457.9916 | 27844.5844 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 59602.3523 | 53271.8488 | 13639.0222 | NORMAL
313.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 63762.2932 | 58686.823 | 13922.2922 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 137430.3212 | 135022.518 | 28179.2465 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 144574.6919 | 142645.7884 | 28460.6468 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 68715.1606 | 66284.6248 | 14089.6233 | NORMAL
313.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 72287.3459 | 70339.2645 | 14230.3234 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 145256.7711 | 133129.3455 | 28765.9859 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 152808.0029 | 143085.1074 | 29053.2454 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 72628.3856 | 60476.9327 | 14382.9929 | NORMAL
313.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 76404.0015 | 66660.8358 | 14526.6227 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 158067.894 | 153673.0084 | 28846.0123 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 167051.2943 | 163531.5367 | 29007.6698 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 79033.947 | 74591.5705 | 14423.0062 | NORMAL
313.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 83525.6471 | 79965.6393 | 14503.8349 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 167069.6227 | 144886.9677 | 29446.6349 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 176564.614 | 158781.7514 | 29611.6583 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 83534.8113 | 61301.9609 | 14723.3174 | NORMAL
313.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 88282.307 | 70456.902 | 14805.8291 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 177395.2599 | 169708.8843 | 29110.8318 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 188084.0722 | 181930.4592 | 29134.3658 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 88697.63 | 80918.5265 | 14555.4159 | NORMAL
313.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 94042.0361 | 87809.5819 | 14567.1829 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 187497.653 | 148626.0625 | 29716.9683 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 198795.177 | 167639.1141 | 29740.9924 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 93748.8265 | 65673.605 | 14858.4841 | NORMAL
313.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 99397.5885 | 69633.8882 | 14870.4962 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 120106.2091 | 107489.1235 | 27240.9419 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 124750.2437 | 114643.3665 | 27530.6919 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 60053.1045 | 47331.5317 | 13620.471 | NORMAL
313.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 62375.1219 | 52181.2229 | 13765.346 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 126946.0769 | 88954.8523 | 27808.1442 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 131854.5823 | 92398.1438 | 28103.9273 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 63473.0384 | 44454.2645 | 13904.0721 | NORMAL
313.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 65927.2912 | 46174.0743 | 14051.9636 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 145669.358 | 121470.4824 | 28498.8139 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 151816.1354 | 132446.8457 | 28689.9681 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 72834.679 | 51134.496 | 14249.4069 | NORMAL
313.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 75908.0677 | 56336.8459 | 14344.9841 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 153965.0086 | 107910.5337 | 29092.2072 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 160461.8358 | 112470.0527 | 29287.3416 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 76982.5043 | 53921.4888 | 14546.1036 | NORMAL
313.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 80230.9179 | 56198.3105 | 14643.6708 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 171606.2287 | 127273.9266 | 29063.4799 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 179027.1378 | 143584.5676 | 29119.6291 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 85803.1144 | 60268.6827 | 14531.7399 | NORMAL
313.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 89513.5689 | 62884.5498 | 14559.8146 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 181378.9451 | 127150.8265 | 29668.6305 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 189222.4639 | 132657.94 | 29725.9488 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 90689.4726 | 63528.9881 | 14834.3152 | NORMAL
313.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 94611.2319 | 66278.3776 | 14862.9744 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 198512.9718 | 140056.4047 | 29085.608 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 206866.7271 | 146001.2319 | 29001.4029 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 99256.4859 | 69752.7923 | 14542.804 | NORMAL
313.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 103433.3636 | 72700.7586 | 14500.7015 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 209817.9867 | 147118.0678 | 29691.2193 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 218647.4758 | 153320.3803 | 29605.2609 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 104908.9934 | 73497.6134 | 14845.6097 | NORMAL
313.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 109323.7379 | 76593.3451 | 14802.6305 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 140137.8309 | 98655.2107 | 28292.6166 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 142411.8076 | 100266.332 | 28381.4394 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 70068.9155 | 49187.5264 | 14146.3083 | NORMAL
313.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 71205.9038 | 49988.2315 | 14190.7197 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 148118.4694 | 103808.1347 | 28881.7165 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 150521.9457 | 105494.891 | 28972.3887 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 74059.2347 | 51872.7469 | 14440.8582 | NORMAL
313.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 75260.9728 | 52715.0433 | 14486.1944 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 179111.0518 | 126277.9308 | 29120.029 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 181800.0743 | 128190.6775 | 29130.169 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 89555.5259 | 62913.1117 | 14560.0145 | NORMAL
313.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 90900.0372 | 63861.8348 | 14565.0845 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 189311.1566 | 132719.3007 | 29726.357 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 192153.3149 | 134715.6012 | 29736.7082 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 94655.5783 | 66309.2393 | 14863.1785 | NORMAL
313.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 96076.6574 | 67305.6901 | 14868.3541 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 223083.5842 | 157528.0603 | 28739.7352 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 225903.3076 | 159545.4856 | 28682.6277 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 111541.7921 | 78420.1475 | 14369.8676 | NORMAL
313.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 112951.6538 | 79417.8786 | 14341.3138 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 235787.8585 | 165357.6674 | 29338.1449 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 238768.1609 | 167453.5891 | 29279.8483 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 117893.9293 | 82602.2212 | 14669.0724 | NORMAL
313.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 119384.0804 | 83647.7509 | 14639.9241 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 272610.0521 | 192814.7002 | 27384.6373 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 275321.9439 | 194775.047 | 27295.0085 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 136305.026 | 95907.8596 | 13692.3187 | NORMAL
313.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 137660.9719 | 96872.3915 | 13647.5042 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 288134.7842 | 202138.1249 | 27954.8316 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 291001.1142 | 204158.3251 | 27863.3365 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 144067.3921 | 100957.9965 | 13977.4158 | NORMAL
313.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 145500.5571 | 101964.6479 | 13931.6683 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 158705.9587 | 111806.2686 | 28859.8657 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 159107.1968 | 112093.0082 | 28868.3859 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 79352.9793 | 55724.5412 | 14429.9328 | NORMAL
313.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 79553.5984 | 55866.4348 | 14434.1929 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 167744.0241 | 117580.3022 | 29460.7767 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 168168.1122 | 117878.4746 | 29469.4743 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 83872.0121 | 58750.2527 | 14730.3883 | NORMAL
313.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 84084.0561 | 58899.0108 | 14734.7371 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 208054.5677 | 146837.8422 | 28986.4426 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 208484.7205 | 147151.2616 | 28980.8498 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 104027.2839 | 73117.7798 | 14493.2213 | NORMAL
313.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 104242.3602 | 73271.3886 | 14490.4249 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 219902.9622 | 154200.3687 | 29589.9892 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 220357.6115 | 154521.3626 | 29584.2798 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 109951.4811 | 77033.0522 | 14794.9946 | NORMAL
313.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 110178.8057 | 77192.8632 | 14792.1399 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 264268.7279 | 186865.4969 | 27653.4176 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 264683.0793 | 187182.7077 | 27640.3391 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 132134.364 | 92961.032 | 13826.7088 | NORMAL
313.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 132341.5396 | 93112.7811 | 13820.1696 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 279318.4342 | 195942.1466 | 28229.2083 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 279756.3822 | 196254.733 | 28215.8575 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 139659.2171 | 97866.1504 | 14114.6042 | NORMAL
313.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 139878.1911 | 98020.9348 | 14107.9288 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 327433.7861 | 231951.4309 | 25487.9185 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 327799.7788 | 232269.7465 | 25475.3562 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 163716.8931 | 115284.6771 | 12743.9592 | NORMAL
313.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 163899.8894 | 115428.1229 | 12737.6781 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 346080.6474 | 242869.1847 | 26018.6199 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 346467.4828 | 243153.6961 | 26005.796 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 173040.3237 | 121281.216 | 13009.3099 | NORMAL
313.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 173233.7414 | 121420.0315 | 13002.898 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 163127.615 | 114940.5961 | 28945.7568 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 163127.615 | 114943.2048 | 28945.7568 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 81563.8075 | 57281.8659 | 14472.8784 | NORMAL
313.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 81563.8075 | 57282.5137 | 14472.8784 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 172417.4871 | 120860.4763 | 29548.4561 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 172417.4871 | 120861.0575 | 29548.4561 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 86208.7436 | 60388.15 | 14774.2281 | NORMAL
313.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 86208.7436 | 60388.2951 | 14774.2281 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 214701.7619 | 151565.1712 | 28889.9716 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 214701.7619 | 151573.7159 | 28889.9716 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 107350.881 | 75462.757 | 14444.9858 | NORMAL
313.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 107350.881 | 75464.8752 | 14444.9858 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 226928.7041 | 159134.9501 | 29491.5095 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 226928.7041 | 159136.848 | 29491.5095 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 113464.3521 | 79496.1969 | 14745.7547 | NORMAL
313.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 113464.3521 | 79496.6706 | 14745.7547 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 273418.3729 | 193391.7685 | 27358.0265 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 273418.3729 | 193416.6865 | 27358.0265 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 136709.1864 | 96193.5614 | 13679.0132 | NORMAL
313.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 136709.1864 | 96199.7259 | 13679.0132 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 288989.1376 | 202738.6729 | 27927.6666 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 288989.1376 | 202744.1902 | 27927.6666 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 144494.5688 | 101257.6444 | 13963.8333 | NORMAL
313.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 144494.5688 | 101259.0207 | 13963.8333 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 339277.4478 | 240415.4646 | 25087.5978 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 339277.4478 | 240481.2776 | 25087.5978 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 169638.7239 | 119472.9554 | 12543.7989 | NORMAL
313.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 169638.7239 | 119489.2059 | 12543.7989 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 358598.7878 | 251670.407 | 25609.9639 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 358598.7878 | 251684.9353 | 25609.9639 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 179299.3939 | 125672.1787 | 12804.9819 | NORMAL
313.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 179299.3939 | 125675.8013 | 12804.9819 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 81.273 | 95082.5905 | 93821.4618 | 29774.2793 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 1 | 101.325 | 102601.2406 | 101591.0645 | 30874.2983 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 81.273 | 47541.2953 | 46271.914 | 14887.1396 | NORMAL
323.15 | 0 | 283.15 | 5.4 | 2 | 101.325 | 51300.6203 | 50283.3034 | 15437.1491 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 81.273 | 100497.4009 | 94173.9964 | 30394.2299 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 1 | 101.325 | 108444.2268 | 103374.9762 | 31517.1531 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 81.273 | 50248.7005 | 43916.5733 | 15197.115 | NORMAL
323.15 | 0 | 283.15 | 26.8 | 2 | 101.325 | 54222.1134 | 49145.3153 | 15758.5766 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 1 | 81.273 | 118662.8377 | 116248.8258 | 32883.0994 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 1 | 101.325 | 125516.1658 | 123582.2061 | 33613.189 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 2 | 81.273 | 59331.4189 | 56897.7787 | 16441.5497 | NORMAL
323.15 | 0 | 293.15 | 5.4 | 2 | 101.325 | 62758.0829 | 60807.4733 | 16806.5945 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 1 | 81.273 | 125420.5077 | 113286.5198 | 33567.7809 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 1 | 101.325 | 132664.1225 | 122935.8828 | 34313.0722 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 2 | 81.273 | 62710.2538 | 50555.5199 | 16783.8904 | NORMAL
323.15 | 0 | 293.15 | 26.8 | 2 | 101.325 | 66332.0613 | 56586.2235 | 17156.5361 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 1 | 81.273 | 138478.9084 | 134072.2519 | 34810.4834 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 1 | 101.325 | 147121.7664 | 143592.405 | 35487.5063 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 2 | 81.273 | 69239.4542 | 64791.1922 | 17405.2417 | NORMAL
323.15 | 0 | 303.15 | 5.4 | 2 | 101.325 | 73560.8832 | 69996.0735 | 17743.7531 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 1 | 81.273 | 146365.0738 | 124169.9776 | 35535.2962 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 1 | 101.325 | 155500.1296 | 137707.1162 | 36226.4159 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 2 | 81.273 | 73182.5369 | 51258.1227 | 17767.6481 | NORMAL
323.15 | 0 | 303.15 | 26.8 | 2 | 101.325 | 77750.0648 | 59919.5843 | 18113.2079 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 81.273 | 157084.8878 | 149377.279 | 36159.7057 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 1 | 101.325 | 167391.7705 | 161220.8099 | 36744.38 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 81.273 | 78542.4439 | 70752.7238 | 18079.8528 | NORMAL
323.15 | 0 | 313.15 | 5.4 | 2 | 101.325 | 83695.8853 | 77454.7573 | 18372.19 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 81.273 | 166030.6357 | 127136.6028 | 36912.6116 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 1 | 101.325 | 176924.4799 | 145750.0815 | 37509.4599 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 81.273 | 83015.3179 | 58149.4756 | 18456.3058 | NORMAL
323.15 | 0 | 313.15 | 26.8 | 2 | 101.325 | 88462.2399 | 61967.5844 | 18754.7299 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 1 | 81.273 | 102078.0579 | 89429.6049 | 30801.2476 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 1 | 101.325 | 106518.8682 | 96386.5557 | 31405.374 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 2 | 81.273 | 51039.029 | 38301.7724 | 15400.6238 | NORMAL
323.15 | 0.1 | 283.15 | 5.4 | 2 | 101.325 | 53259.4341 | 43052.8175 | 15702.687 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 1 | 81.273 | 107891.2497 | 75590.7507 | 31442.5814 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 1 | 101.325 | 112584.9574 | 78882.3193 | 32059.2868 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 2 | 81.273 | 53945.6248 | 37778.649 | 15721.2907 | NORMAL
323.15 | 0.1 | 283.15 | 26.8 | 2 | 101.325 | 56292.4787 | 39422.9389 | 16029.6434 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 1 | 81.273 | 126566.8874 | 102304.6202 | 33718.9449 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 1 | 101.325 | 132469.9534 | 113049.1986 | 34283.9608 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 2 | 81.273 | 63283.4437 | 44411.7722 | 16859.4725 | NORMAL
323.15 | 0.1 | 293.15 | 5.4 | 2 | 101.325 | 66234.9767 | 46638.0223 | 17141.9804 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 1 | 81.273 | 133774.6811 | 93744.1957 | 34421.0301 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 1 | 101.325 | 140013.9178 | 98121.4692 | 34997.8106 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 2 | 81.273 | 66887.3405 | 46846.6043 | 17210.5151 | NORMAL
323.15 | 0.1 | 293.15 | 26.8 | 2 | 101.325 | 70006.9589 | 49032.787 | 17498.9053 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 1 | 81.273 | 151507.5701 | 107053.8921 | 35797.0764 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 1 | 101.325 | 158657.7185 | 123116.584 | 36255.9254 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 2 | 81.273 | 75753.785 | 53188.5485 | 17898.5382 | NORMAL
323.15 | 0.1 | 303.15 | 5.4 | 2 | 101.325 | 79328.8592 | 55706.8822 | 18127.9627 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 1 | 81.273 | 160135.6981 | 112239.6073 | 36542.4318 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 1 | 101.325 | 167693.0367 | 117543.9158 | 37010.8349 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 2 | 81.273 | 80067.8491 | 56083.6257 | 18271.2159 | NORMAL
323.15 | 0.1 | 303.15 | 26.8 | 2 | 101.325 | 83846.5184 | 58732.2335 | 18505.4174 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 1 | 81.273 | 177458.4537 | 125097.0849 | 37217.335 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 1 | 101.325 | 185528.9411 | 130830.2498 | 37533.0049 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 2 | 81.273 | 88729.2268 | 62328.7309 | 18608.6675 | NORMAL
323.15 | 0.1 | 313.15 | 5.4 | 2 | 101.325 | 92764.4706 | 65174.2434 | 18766.5025 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 1 | 81.273 | 187564.4455 | 131491.2443 | 37992.2625 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 1 | 101.325 | 196094.5351 | 137481.0142 | 38314.5053 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 2 | 81.273 | 93782.2228 | 65696.5524 | 18996.1313 | NORMAL
323.15 | 0.1 | 313.15 | 26.8 | 2 | 101.325 | 98047.2675 | 68686.7552 | 19157.2526 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 1 | 81.273 | 121259.1689 | 85299.4281 | 33168.0605 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 1 | 101.325 | 123440.6072 | 86842.402 | 33399.5341 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 2 | 81.273 | 60629.5844 | 42544.9549 | 16584.0302 | NORMAL
323.15 | 0.5 | 283.15 | 5.4 | 2 | 101.325 | 61720.3036 | 43312.435 | 16699.7671 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 1 | 81.273 | 128164.696 | 89809.016 | 33858.6754 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 1 | 101.325 | 130470.364 | 91426.5564 | 34094.9687 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 2 | 81.273 | 64082.348 | 44881.0636 | 16929.3377 | NORMAL
323.15 | 0.5 | 283.15 | 26.8 | 2 | 101.325 | 65235.182 | 45688.9398 | 17047.4843 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 1 | 81.273 | 158738.6035 | 111823.5062 | 36260.8035 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 1 | 101.325 | 161330.9401 | 113663.9171 | 36413.5621 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 2 | 81.273 | 79369.3017 | 55734.5725 | 18130.4018 | NORMAL
323.15 | 0.5 | 293.15 | 5.4 | 2 | 101.325 | 80665.4701 | 56648.3022 | 18206.7811 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 1 | 81.273 | 167778.528 | 117603.204 | 37015.8145 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 1 | 101.325 | 170518.4943 | 119526.9373 | 37171.7538 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 2 | 81.273 | 83889.264 | 58762.0168 | 18507.9073 | NORMAL
323.15 | 0.5 | 293.15 | 26.8 | 2 | 101.325 | 85259.2472 | 59722.4427 | 18585.8769 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 1 | 81.273 | 201211.9142 | 141961.5503 | 38002.7951 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 1 | 101.325 | 203940.8296 | 143909.3295 | 38066.9327 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 2 | 81.273 | 100605.9571 | 70701.3771 | 19001.3975 | NORMAL
323.15 | 0.5 | 303.15 | 5.4 | 2 | 101.325 | 101970.4148 | 71665.8227 | 19033.4663 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 1 | 81.273 | 212670.6299 | 149118.4704 | 38794.0772 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 1 | 101.325 | 215554.9529 | 151145.8623 | 38859.5503 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 2 | 81.273 | 106335.3149 | 74496.9258 | 19397.0386 | NORMAL
323.15 | 0.5 | 303.15 | 26.8 | 2 | 101.325 | 107777.4764 | 75508.5275 | 19429.7751 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 1 | 81.273 | 249219.0671 | 176113.0628 | 38530.6913 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 1 | 101.325 | 251851.9598 | 178009.9457 | 38529.4626 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 2 | 81.273 | 124609.5336 | 87639.638 | 19265.3456 | NORMAL
323.15 | 0.5 | 313.15 | 5.4 | 2 | 101.325 | 125925.9799 | 88574.5075 | 19264.7313 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 1 | 81.273 | 263411.7178 | 184759.0203 | 39332.9651 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 1 | 101.325 | 266194.5498 | 186718.9742 | 39331.7108 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 2 | 81.273 | 131705.8589 | 92286.7126 | 19666.4826 | NORMAL
323.15 | 0.5 | 313.15 | 26.8 | 2 | 101.325 | 133097.2749 | 93263.6916 | 19665.8554 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 1 | 81.273 | 139092.4675 | 97911.2602 | 34861.5994 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 1 | 101.325 | 139478.3212 | 98186.1338 | 34893.5 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 2 | 81.273 | 69546.2337 | 48818.6144 | 17430.7997 | NORMAL
323.15 | 0.9 | 283.15 | 5.4 | 2 | 101.325 | 69739.1606 | 48954.8516 | 17446.75 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 1 | 81.273 | 147013.5741 | 103031.9828 | 35587.4766 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 1 | 101.325 | 147421.4016 | 103318.5292 | 35620.0414 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 2 | 81.273 | 73506.7871 | 51485.353 | 17793.7383 | NORMAL
323.15 | 0.9 | 283.15 | 26.8 | 2 | 101.325 | 73710.7008 | 51628.3591 | 17810.0207 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 1 | 81.273 | 186676.9753 | 131638.8492 | 37573.6178 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 1 | 101.325 | 187092.7412 | 131940.0944 | 37588.0711 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 2 | 81.273 | 93338.4876 | 65577.2955 | 18786.8089 | NORMAL
323.15 | 0.9 | 293.15 | 5.4 | 2 | 101.325 | 93546.3706 | 65725.349 | 18794.0355 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 1 | 81.273 | 197307.948 | 138331.518 | 38355.9637 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 1 | 101.325 | 197747.3912 | 138641.4025 | 38370.718 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 2 | 81.273 | 98653.974 | 69111.7282 | 19177.9819 | NORMAL
323.15 | 0.9 | 293.15 | 26.8 | 2 | 101.325 | 98873.6956 | 69266.1011 | 19185.359 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 1 | 81.273 | 241123.2433 | 170347.8158 | 38518.2023 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 1 | 101.325 | 241525.3082 | 170652.1543 | 38519.4312 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 2 | 81.273 | 120561.6216 | 84781.724 | 19259.1011 | NORMAL
323.15 | 0.9 | 303.15 | 5.4 | 2 | 101.325 | 120762.6541 | 84928.1201 | 19259.7156 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 1 | 81.273 | 254854.849 | 178747.3502 | 39320.2161 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 1 | 101.325 | 255279.811 | 179049.9062 | 39321.4706 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 2 | 81.273 | 127427.4245 | 89286.3509 | 19660.1081 | NORMAL
323.15 | 0.9 | 303.15 | 26.8 | 2 | 101.325 | 127639.9055 | 89436.3559 | 19660.7353 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 1 | 81.273 | 302515.5047 | 214104.1879 | 38139.5977 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 1 | 101.325 | 302871.7531 | 214406.7803 | 38135.1447 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 2 | 81.273 | 151257.7524 | 106463.0367 | 19069.7989 | NORMAL
323.15 | 0.9 | 313.15 | 5.4 | 2 | 101.325 | 151435.8766 | 106600.8846 | 19067.5724 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 1 | 81.273 | 319743.3073 | 224343.2347 | 38933.7284 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 1 | 101.325 | 320119.8436 | 224618.5866 | 38929.1826 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 2 | 81.273 | 159871.6537 | 112040.7349 | 19466.8642 | NORMAL
323.15 | 0.9 | 313.15 | 26.8 | 2 | 101.325 | 160059.9218 | 112175.46 | 19464.5913 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 81.273 | 143345.6572 | 100921.6039 | 35202.9421 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 1 | 101.325 | 143345.6572 | 100923.615 | 35202.9421 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 81.273 | 71672.8286 | 50315.4736 | 17601.471 | NORMAL
323.15 | 1 | 283.15 | 5.4 | 2 | 101.325 | 71672.8286 | 50315.9735 | 17601.471 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 81.273 | 151508.9766 | 106186.1683 | 35935.9266 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 1 | 101.325 | 151508.9766 | 106186.6169 | 35935.9266 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 81.273 | 75754.4883 | 53060.5931 | 17967.9633 | NORMAL
323.15 | 1 | 283.15 | 26.8 | 2 | 101.325 | 75754.4883 | 53060.7051 | 17967.9633 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 1 | 81.273 | 193103.4965 | 136202.0916 | 37782.284 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 1 | 101.325 | 193103.4965 | 136208.9919 | 37782.284 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 2 | 81.273 | 96551.7482 | 67842.6581 | 18891.142 | NORMAL
323.15 | 1 | 293.15 | 5.4 | 2 | 101.325 | 96551.7482 | 67844.3701 | 18891.142 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 1 | 81.273 | 204100.4499 | 143100.7019 | 38568.9747 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 1 | 101.325 | 204100.4499 | 143102.2366 | 38568.9747 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 2 | 81.273 | 102050.225 | 71492.7078 | 19284.4874 | NORMAL
323.15 | 1 | 293.15 | 26.8 | 2 | 101.325 | 102050.225 | 71493.0909 | 19284.4874 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 1 | 81.273 | 250003.7998 | 176672.3746 | 38530.585 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 1 | 101.325 | 250003.7998 | 176693.17 | 38530.585 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 2 | 81.273 | 125001.8999 | 87916.7767 | 19265.2925 | NORMAL
323.15 | 1 | 303.15 | 5.4 | 2 | 101.325 | 125001.8999 | 87921.926 | 19265.2925 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 1 | 81.273 | 264241.1399 | 185341.8418 | 39332.8567 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 1 | 101.325 | 264241.1399 | 185346.4528 | 39332.8567 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 2 | 81.273 | 132120.5699 | 92577.566 | 19666.4283 | NORMAL
323.15 | 1 | 303.15 | 26.8 | 2 | 101.325 | 132120.5699 | 92578.7164 | 19666.4283 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 81.273 | 314046.5671 | 222333.2298 | 37989.0125 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 1 | 101.325 | 314046.5671 | 222389.514 | 37989.0125 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 81.273 | 157023.2835 | 110537.9212 | 18994.5063 | NORMAL
323.15 | 1 | 313.15 | 5.4 | 2 | 101.325 | 157023.2835 | 110551.8317 | 18994.5063 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 81.273 | 331931.0464 | 232909.6188 | 38780.0077 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 1 | 101.325 | 331931.0464 | 232922.0618 | 38780.0077 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 81.273 | 165965.5232 | 116315.1706 | 19390.0039 | NORMAL
323.15 | 1 | 313.15 | 26.8 | 2 | 101.325 | 165965.5232 | 116318.2738 | 19390.0039 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
283.15 | 40
323.15 | 40
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)