## Table 1
Degradation Coefficient (C_d) |  | 48/50A020 (20 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 265000 | 96000 | 14 | 4000 | 1983.7765 |  | 1
75 | 80 | 72 | 68.6171 | 249000 | 109000 | 13.8 | 4000 | 1983.7765 |  | 1
75 | 80 | 67 | 51.5724 | 223000 | 126000 | 13.6 | 4000 | 1983.7765 |  | 1
75 | 80 | 62 | 36.2232 | 204000 | 147000 | 13.5 | 4000 | 1948.352 |  | 1
75 | 80 | 57 | 22.3618 | 184000 | 166000 | 13.4 | 4000 | 1948.352 |  | 1
75 | 80 | 75 | 79.7527 | 285000 | 107000 | 14.1 | 5000 | 2448.4637 |  | 1
75 | 80 | 72 | 68.6171 | 269000 | 121000 | 14 | 5000 | 2408.8715 |  | 1
75 | 80 | 67 | 51.5724 | 239000 | 140000 | 13.7 | 5000 | 2408.8715 |  | 1
75 | 80 | 62 | 36.2232 | 220000 | 168000 | 13.6 | 5000 | 2408.8715 |  | 1
75 | 80 | 57 | 22.3618 | 199000 | 191000 | 13.5 | 5000 | 2371.3631 |  | 1
75 | 80 | 75 | 79.7527 | 293000 | 109000 | 14.2 | 6000 | 2958.9944 |  | 1
75 | 80 | 72 | 68.6171 | 277000 | 126000 | 14 | 6000 | 2917.3184 |  | 1
75 | 80 | 67 | 51.5724 | 251000 | 153000 | 13.8 | 6000 | 2917.3184 |  | 1
75 | 80 | 62 | 36.2232 | 232000 | 186000 | 13.7 | 6000 | 2917.3184 |  | 1
75 | 80 | 57 | 22.3618 | 212000 | 209000 | 13.6 | 6000 | 2917.3184 |  | 1
75 | 80 | 75 | 79.7527 | 303000 | 115000 | 14.3 | 7000 | 3538.2905 |  | 1
75 | 80 | 72 | 68.6171 | 286000 | 134000 | 14.1 | 7000 | 3538.2905 |  | 1
75 | 80 | 67 | 51.5724 | 260000 | 166000 | 13.9 | 7000 | 3492.4469 |  | 1
75 | 80 | 62 | 36.2232 | 236000 | 197000 | 13.7 | 7000 | 3492.4469 |  | 1
75 | 80 | 57 | 22.3618 | 222000 | 222000 | 13.6 | 7000 | 3492.4469 |  | 1
85 | 80 | 75 | 79.7527 | 249000 | 83000 | 15.5 | 4000 | 1983.7765 |  | 1
85 | 80 | 72 | 68.6171 | 234000 | 96000 | 15.4 | 4000 | 1983.7765 |  | 1
85 | 80 | 67 | 51.5724 | 201000 | 106000 | 15.1 | 4000 | 1948.352 |  | 1
85 | 80 | 62 | 36.2232 | 193000 | 139000 | 15.1 | 4000 | 1948.352 |  | 1
85 | 80 | 57 | 22.3618 | 173000 | 157000 | 15 | 4000 | 1948.352 |  | 1
85 | 80 | 75 | 79.7527 | 265000 | 91000 | 15.7 | 5000 | 2408.8715 |  | 1
85 | 80 | 72 | 68.6171 | 250000 | 105000 | 15.5 | 5000 | 2408.8715 |  | 1
85 | 80 | 67 | 51.5724 | 219000 | 123000 | 15.2 | 5000 | 2408.8715 |  | 1
85 | 80 | 62 | 36.2232 | 207000 | 157000 | 15.2 | 5000 | 2371.3631 |  | 1
85 | 80 | 57 | 22.3618 | 187000 | 179000 | 15.1 | 5000 | 2371.3631 |  | 1
85 | 80 | 75 | 79.7527 | 277000 | 97000 | 15.8 | 6000 | 2917.3184 |  | 1
85 | 80 | 72 | 68.6171 | 262000 | 114000 | 15.6 | 6000 | 2917.3184 |  | 1
85 | 80 | 67 | 51.5724 | 240000 | 145000 | 15.4 | 6000 | 2917.3184 |  | 1
85 | 80 | 62 | 36.2232 | 214000 | 170000 | 15.2 | 6000 | 2917.3184 |  | 1
85 | 80 | 57 | 22.3618 | 199000 | 197000 | 15.1 | 6000 | 2873.5587 |  | 1
85 | 80 | 75 | 79.7527 | 286000 | 102000 | 15.9 | 7000 | 3538.2905 |  | 1
85 | 80 | 72 | 68.6171 | 270000 | 122000 | 15.7 | 7000 | 3492.4469 |  | 1
85 | 80 | 67 | 51.5724 | 248000 | 157000 | 15.5 | 7000 | 3492.4469 |  | 1
85 | 80 | 62 | 36.2232 | 226000 | 191000 | 15.3 | 7000 | 3492.4469 |  | 1
85 | 80 | 57 | 22.3618 | 212000 | 212000 | 15.3 | 7000 | 3492.4469 |  | 1
95 | 80 | 75 | 79.7527 | 235000 | 72000 | 17.3 | 4000 | 1983.7765 |  | 1
95 | 80 | 72 | 68.6171 | 222000 | 87000 | 17.2 | 4000 | 1983.7765 |  | 1
95 | 80 | 67 | 51.5724 | 201000 | 108000 | 17 | 4000 | 1948.352 |  | 1
95 | 80 | 62 | 36.2232 | 177000 | 125000 | 16.8 | 4000 | 1948.352 |  | 1
95 | 80 | 57 | 22.3618 | 162000 | 148000 | 16.7 | 4000 | 1948.352 |  | 1
95 | 80 | 75 | 79.7527 | 251000 | 80000 | 17.5 | 5000 | 2408.8715 |  | 1
95 | 80 | 72 | 68.6171 | 237000 | 95000 | 17.3 | 5000 | 2408.8715 |  | 1
95 | 80 | 67 | 51.5724 | 214000 | 121000 | 17.1 | 5000 | 2408.8715 |  | 1
95 | 80 | 62 | 36.2232 | 192000 | 145000 | 16.9 | 5000 | 2371.3631 |  | 1
95 | 80 | 57 | 22.3618 | 177000 | 170000 | 16.9 | 5000 | 2371.3631 |  | 1
95 | 80 | 75 | 79.7527 | 262000 | 86000 | 17.6 | 6000 | 2917.3184 |  | 1
95 | 80 | 72 | 68.6171 | 247000 | 103000 | 17.4 | 6000 | 2917.3184 |  | 1
95 | 80 | 67 | 51.5724 | 223000 | 132000 | 17.2 | 6000 | 2917.3184 |  | 1
95 | 80 | 62 | 36.2232 | 204000 | 163000 | 17 | 6000 | 2873.5587 |  | 1
95 | 80 | 57 | 22.3618 | 188000 | 188000 | 17 | 6000 | 2873.5587 |  | 1
95 | 80 | 75 | 79.7527 | 270000 | 90000 | 17.7 | 7000 | 3492.4469 |  | 1
95 | 80 | 72 | 68.6171 | 255000 | 110000 | 17.5 | 7000 | 3492.4469 |  | 1
95 | 80 | 67 | 51.5724 | 231000 | 144000 | 17.3 | 7000 | 3492.4469 |  | 1
95 | 80 | 62 | 36.2232 | 210000 | 179000 | 17.1 | 7000 | 3444.5196 |  | 1
95 | 80 | 57 | 22.3618 | 199000 | 199000 | 17 | 7000 | 3444.5196 |  | 1
105 | 80 | 75 | 79.7527 | 221000 | 61000 | 19.3 | 4000 | 1983.7765 |  | 1
105 | 80 | 72 | 68.6171 | 207000 | 75000 | 19.2 | 4000 | 1948.352 |  | 1
105 | 80 | 67 | 51.5724 | 186000 | 97000 | 19 | 4000 | 1948.352 |  | 1
105 | 80 | 62 | 36.2232 | 167000 | 118000 | 18.9 | 4000 | 1948.352 |  | 1
105 | 80 | 57 | 22.3618 | 150000 | 138000 | 18.8 | 4000 | 1948.352 |  | 1
105 | 80 | 75 | 79.7527 | 226000 | 58000 | 19.3 | 5000 | 2408.8715 |  | 1
105 | 80 | 72 | 68.6171 | 220000 | 82000 | 19.3 | 5000 | 2408.8715 |  | 1
105 | 80 | 67 | 51.5724 | 199000 | 109000 | 19.2 | 5000 | 2371.3631 |  | 1
105 | 80 | 62 | 36.2232 | 176000 | 132000 | 18.9 | 5000 | 2371.3631 |  | 1
105 | 80 | 57 | 22.3618 | 163000 | 158000 | 18.9 | 5000 | 2371.3631 |  | 1
105 | 80 | 75 | 79.7527 | 246000 | 72000 | 19.6 | 6000 | 2917.3184 |  | 1
105 | 80 | 72 | 68.6171 | 231000 | 90000 | 19.4 | 6000 | 2917.3184 |  | 1
105 | 80 | 67 | 51.5724 | 209000 | 121000 | 19.2 | 6000 | 2873.5587 |  | 1
105 | 80 | 62 | 36.2232 | 189000 | 151000 | 19.1 | 6000 | 2873.5587 |  | 1
105 | 80 | 57 | 22.3618 | 176000 | 176000 | 19 | 6000 | 2873.5587 |  | 1
105 | 80 | 75 | 79.7527 | 214000 | 38000 | 19 | 7000 | 3492.4469 |  | 1
105 | 80 | 72 | 68.6171 | 238000 | 97000 | 19.5 | 7000 | 3492.4469 |  | 1
105 | 80 | 67 | 51.5724 | 215000 | 131000 | 19.3 | 7000 | 3492.4469 |  | 1
105 | 80 | 62 | 36.2232 | 196000 | 168000 | 19.1 | 7000 | 3444.5196 |  | 1
105 | 80 | 57 | 22.3618 | 181000 | 181000 | 19 | 7000 | 3444.5196 |  | 1
115 | 80 | 75 | 79.7527 | 205000 | 50000 | 21.6 | 4000 | 1948.352 |  | 1
115 | 80 | 72 | 68.6171 | 191000 | 63000 | 21.5 | 4000 | 1948.352 |  | 1
115 | 80 | 67 | 51.5724 | 170000 | 84000 | 21.3 | 4000 | 1948.352 |  | 1
115 | 80 | 62 | 36.2232 | 150000 | 104000 | 21.1 | 4000 | 1948.352 |  | 1
115 | 80 | 57 | 22.3618 | 136000 | 126000 | 21.1 | 4000 | 1948.352 |  | 1
115 | 80 | 75 | 79.7527 | 219000 | 55000 | 21.7 | 5000 | 2408.8715 |  | 1
115 | 80 | 72 | 68.6171 | 205000 | 71000 | 21.6 | 5000 | 2371.3631 |  | 1
115 | 80 | 67 | 51.5724 | 184000 | 97000 | 21.4 | 5000 | 2371.3631 |  | 1
115 | 80 | 62 | 36.2232 | 165000 | 124000 | 21.3 | 5000 | 2371.3631 |  | 1
115 | 80 | 57 | 22.3618 | 151000 | 147000 | 21.2 | 5000 | 2371.3631 |  | 1
115 | 80 | 75 | 79.7527 | 199000 | 31000 | 21.4 | 6000 | 2873.5587 |  | 1
115 | 80 | 72 | 68.6171 | 215000 | 78000 | 21.7 | 6000 | 2917.3184 |  | 1
115 | 80 | 67 | 51.5724 | 192000 | 108000 | 21.5 | 6000 | 2873.5587 |  | 1
115 | 80 | 62 | 36.2232 | 173000 | 140000 | 21.4 | 6000 | 2873.5587 |  | 1
115 | 80 | 57 | 22.3618 | 157000 | 157000 | 21.2 | 6000 | 2873.5587 |  | 1
115 | 80 | 75 | 79.7527 | 222000 | 50000 | 21.6 | 7000 | 3492.4469 |  | 1
115 | 80 | 72 | 68.6171 | 200000 | 63000 | 21.4 | 7000 | 3444.5196 |  | 1
115 | 80 | 67 | 51.5724 | 198000 | 119000 | 21.5 | 7000 | 3444.5196 |  | 1
115 | 80 | 62 | 36.2232 | 178000 | 153000 | 21.4 | 7000 | 3444.5196 |  | 1
115 | 80 | 57 | 22.3618 | 168000 | 168000 | 21.3 | 7000 | 3444.5196 |  | 1
75 | 80 | 75 | 79.7527 | 317000 | 126000 | 14.4 | 8000 | 4192.6034 |  | 1
75 | 80 | 72 | 68.6171 | 299000 | 147000 | 14.3 | 8000 | 4192.6034 |  | 1
75 | 80 | 67 | 51.5724 | 267000 | 177000 | 13.9 | 8000 | 4142.5922 |  | 1
75 | 80 | 62 | 36.2232 | 242000 | 213000 | 13.7 | 8000 | 4142.5922 |  | 1
75 | 80 | 57 | 22.3618 | 235000 | 235000 | 13.7 | 8000 | 4142.5922 |  | 1
75 | 80 | 75 | 79.7527 | 317000 | 126000 | 14.4 | 9000 | 4930.2682 |  | 1
75 | 80 | 72 | 68.6171 | 300000 | 149000 | 14.2 | 9000 | 4930.2682 |  | 1
75 | 80 | 67 | 51.5724 | 273000 | 188000 | 14 | 9000 | 4876.0894 |  | 1
75 | 80 | 62 | 36.2232 | 248000 | 227000 | 13.8 | 9000 | 4876.0894 |  | 1
75 | 80 | 57 | 22.3618 | 243000 | 243000 | 13.8 | 9000 | 4876.0894 |  | 1
75 | 80 | 75 | 79.7527 | 322000 | 130000 | 14.4 | 10000 | 5767.9553 |  | 1
75 | 80 | 72 | 68.6171 | 305000 | 156000 | 14.3 | 10000 | 5767.9553 |  | 1
75 | 80 | 67 | 51.5724 | 280000 | 202000 | 14.1 | 10000 | 5709.6089 |  | 1
75 | 80 | 62 | 36.2232 | 258000 | 246000 | 13.9 | 10000 | 5709.6089 |  | 1
75 | 80 | 57 | 22.3618 | 251000 | 251000 | 13.8 | 10000 | 5709.6089 |  | 1
85 | 80 | 75 | 79.7527 | 294000 | 108000 | 15.9 | 8000 | 4192.6034 |  | 1
85 | 80 | 72 | 68.6171 | 277000 | 129000 | 15.8 | 8000 | 4142.5922 |  | 1
85 | 80 | 67 | 51.5724 | 252000 | 166000 | 15.5 | 8000 | 4142.5922 |  | 1
85 | 80 | 62 | 36.2232 | 232000 | 205000 | 15.4 | 8000 | 4142.5922 |  | 1
85 | 80 | 57 | 22.3618 | 222000 | 222000 | 15.3 | 8000 | 4142.5922 |  | 1
85 | 80 | 75 | 79.7527 | 299000 | 112000 | 16 | 9000 | 4930.2682 |  | 1
85 | 80 | 72 | 68.6171 | 284000 | 138000 | 15.8 | 9000 | 4930.2682 |  | 1
85 | 80 | 67 | 51.5724 | 260000 | 180000 | 15.6 | 9000 | 4876.0894 |  | 1
85 | 80 | 62 | 36.2232 | 238000 | 220000 | 15.5 | 9000 | 4876.0894 |  | 1
85 | 80 | 57 | 22.3618 | 231000 | 231000 | 15.4 | 9000 | 4876.0894 |  | 1
85 | 80 | 75 | 79.7527 | 307000 | 120000 | 16.1 | 10000 | 5767.9553 |  | 1
85 | 80 | 72 | 68.6171 | 290000 | 146000 | 15.9 | 10000 | 5767.9553 |  | 1
85 | 80 | 67 | 51.5724 | 264000 | 190000 | 15.7 | 10000 | 5709.6089 |  | 1
85 | 80 | 62 | 36.2232 | 238000 | 225000 | 15.4 | 10000 | 5709.6089 |  | 1
85 | 80 | 57 | 22.3618 | 234000 | 234000 | 15.4 | 10000 | 5709.6089 |  | 1
95 | 80 | 75 | 79.7527 | 277000 | 95000 | 17.7 | 8000 | 4142.5922 |  | 1
95 | 80 | 72 | 68.6171 | 262000 | 118000 | 17.6 | 8000 | 4142.5922 |  | 1
95 | 80 | 67 | 51.5724 | 236000 | 153000 | 17.3 | 8000 | 4142.5922 |  | 1
95 | 80 | 62 | 36.2232 | 217000 | 194000 | 17.2 | 8000 | 4142.5922 |  | 1
95 | 80 | 57 | 22.3618 | 209000 | 209000 | 17.1 | 8000 | 4092.581 |  | 1
95 | 80 | 75 | 79.7527 | 282000 | 99000 | 17.8 | 9000 | 4930.2682 |  | 1
95 | 80 | 72 | 68.6171 | 267000 | 124000 | 17.6 | 9000 | 4876.0894 |  | 1
95 | 80 | 67 | 51.5724 | 241000 | 165000 | 17.4 | 9000 | 4876.0894 |  | 1
95 | 80 | 62 | 36.2232 | 221000 | 206000 | 17.2 | 9000 | 4876.0894 |  | 1
95 | 80 | 57 | 22.3618 | 216000 | 216000 | 17.2 | 9000 | 4876.0894 |  | 1
95 | 80 | 75 | 79.7527 | 287000 | 104000 | 17.8 | 10000 | 5767.9553 |  | 1
95 | 80 | 72 | 68.6171 | 270000 | 130000 | 17.7 | 10000 | 5709.6089 |  | 1
95 | 80 | 67 | 51.5724 | 246000 | 176000 | 17.4 | 10000 | 5709.6089 |  | 1
95 | 80 | 62 | 36.2232 | 226000 | 214000 | 17.3 | 10000 | 5709.6089 |  | 1
95 | 80 | 57 | 22.3618 | 223000 | 223000 | 17.2 | 10000 | 5709.6089 |  | 1
105 | 80 | 75 | 79.7527 | 248000 | 70000 | 19.6 | 8000 | 4142.5922 |  | 1
105 | 80 | 72 | 68.6171 | 224000 | 84000 | 19.3 | 8000 | 4142.5922 |  | 1
105 | 80 | 67 | 51.5724 | 221000 | 142000 | 19.3 | 8000 | 4142.5922 |  | 1
105 | 80 | 62 | 36.2232 | 198000 | 178000 | 19.1 | 8000 | 4092.581 |  | 1
105 | 80 | 57 | 22.3618 | 195000 | 195000 | 19.2 | 8000 | 4092.581 |  | 1
105 | 80 | 75 | 79.7527 | 230000 | 51000 | 19.3 | 9000 | 4876.0894 |  | 1
105 | 80 | 72 | 68.6171 | 240000 | 101000 | 19.5 | 9000 | 4876.0894 |  | 1
105 | 80 | 67 | 51.5724 | 225000 | 153000 | 19.4 | 9000 | 4876.0894 |  | 1
105 | 80 | 62 | 36.2232 | 186000 | 171000 | 18.9 | 9000 | 4823.9944 |  | 1
105 | 80 | 57 | 22.3618 | 199000 | 199000 | 19.2 | 9000 | 4823.9944 |  | 1
105 | 80 | 75 | 79.7527 | 256000 | 77000 | 19.7 | 10000 | 5709.6089 |  | 1
105 | 80 | 72 | 68.6171 | 217000 | 83000 | 19.2 | 10000 | 5709.6089 |  | 1
105 | 80 | 67 | 51.5724 | 229000 | 163000 | 19.4 | 10000 | 5709.6089 |  | 1
105 | 80 | 62 | 36.2232 | 213000 | 203000 | 19.3 | 10000 | 5709.6089 |  | 1
105 | 80 | 57 | 22.3618 | 207000 | 207000 | 19.2 | 10000 | 5653.3464 |  | 1
115 | 80 | 75 | 79.7527 | 186000 | 14000 | 21.1 | 8000 | 4092.581 |  | 1
115 | 80 | 72 | 68.6171 | 182000 | 46000 | 21.1 | 8000 | 4092.581 |  | 1
115 | 80 | 67 | 51.5724 | 204000 | 130000 | 21.6 | 8000 | 4092.581 |  | 1
115 | 80 | 62 | 36.2232 | 185000 | 166000 | 21.5 | 8000 | 4092.581 |  | 1
115 | 80 | 57 | 22.3618 | 178000 | 178000 | 21.4 | 8000 | 4092.581 |  | 1
115 | 80 | 75 | 79.7527 | 237000 | 63000 | 21.7 | 9000 | 4876.0894 |  | 1
115 | 80 | 72 | 68.6171 | 185000 | 51000 | 21.2 | 9000 | 4823.9944 |  | 1
115 | 80 | 67 | 51.5724 | 208000 | 140000 | 21.6 | 9000 | 4823.9944 |  | 1
115 | 80 | 62 | 36.2232 | 189000 | 175000 | 21.5 | 9000 | 4823.9944 |  | 1
115 | 80 | 57 | 22.3618 | 186000 | 186000 | 21.5 | 9000 | 4823.9944 |  | 1
115 | 80 | 75 | 79.7527 | 205000 | 31000 | 21.3 | 10000 | 5653.3464 |  | 1
115 | 80 | 72 | 68.6171 | 187000 | 56000 | 21.2 | 10000 | 5653.3464 |  | 1
115 | 80 | 67 | 51.5724 | 195000 | 133000 | 21.4 | 10000 | 5653.3464 |  | 1
115 | 80 | 62 | 36.2232 | 195000 | 187000 | 21.5 | 10000 | 5653.3464 |  | 1
115 | 80 | 57 | 22.3618 | 192000 | 192000 | 21.5 | 10000 | 5653.3464 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 2
Degradation Coefficient (C_d) |  | 48/50A025 (25 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 331000 | 118000 | 18 | 5000 | 898.1173 |  | 1
75 | 80 | 72 | 68.6171 | 298000 | 121000 | 17.2 | 5000 | 898.1173 |  | 1
75 | 80 | 67 | 51.5724 | 284000 | 162000 | 17.2 | 5000 | 898.1173 |  | 1
75 | 80 | 62 | 36.2232 | 253000 | 183000 | 16.5 | 5000 | 858.5251 |  | 1
75 | 80 | 57 | 22.3618 | 233000 | 212000 | 16.4 | 5000 | 858.5251 |  | 1
75 | 80 | 75 | 79.7527 | 338000 | 115000 | 17.9 | 6250 | 1358.6369 |  | 1
75 | 80 | 72 | 68.6171 | 321000 | 136000 | 17.6 | 6250 | 1358.6369 |  | 1
75 | 80 | 67 | 51.5724 | 292000 | 170000 | 17.1 | 6250 | 1358.6369 |  | 1
75 | 80 | 62 | 36.2232 | 276000 | 213000 | 17 | 6250 | 1316.9609 |  | 1
75 | 80 | 57 | 22.3618 | 251000 | 242000 | 16.6 | 6250 | 1316.9609 |  | 1
75 | 80 | 75 | 79.7527 | 359000 | 130000 | 18.2 | 7500 | 2056.7095 |  | 1
75 | 80 | 72 | 68.6171 | 334000 | 147000 | 17.8 | 7500 | 1969.1899 |  | 1
75 | 80 | 67 | 51.5724 | 317000 | 198000 | 17.7 | 7500 | 1969.1899 |  | 1
75 | 80 | 62 | 36.2232 | 290000 | 236000 | 17.3 | 7500 | 1969.1899 |  | 1
75 | 80 | 57 | 22.3618 | 267000 | 267000 | 17 | 7500 | 1925.4302 |  | 1
75 | 80 | 75 | 79.7527 | 367000 | 134000 | 18.2 | 8750 | 2829.7989 |  | 1
75 | 80 | 72 | 68.6171 | 358000 | 170000 | 18.4 | 8750 | 2829.7989 |  | 1
75 | 80 | 67 | 51.5724 | 316000 | 202000 | 17.5 | 8750 | 2738.1117 |  | 1
75 | 80 | 62 | 36.2232 | 288000 | 246000 | 17 | 8750 | 2738.1117 |  | 1
75 | 80 | 57 | 22.3618 | 271000 | 271000 | 16.8 | 8750 | 2692.2682 |  | 1
85 | 80 | 75 | 79.7527 | 314000 | 105000 | 19.9 | 5000 | 898.1173 |  | 1
85 | 80 | 72 | 68.6171 | 294000 | 120000 | 19.4 | 5000 | 898.1173 |  | 1
85 | 80 | 67 | 51.5724 | 265000 | 145000 | 18.8 | 5000 | 858.5251 |  | 1
85 | 80 | 62 | 36.2232 | 231000 | 163000 | 18.2 | 5000 | 858.5251 |  | 1
85 | 80 | 57 | 22.3618 | 222000 | 203000 | 18.4 | 5000 | 858.5251 |  | 1
85 | 80 | 75 | 79.7527 | 330000 | 111000 | 20.1 | 6250 | 1358.6369 |  | 1
85 | 80 | 72 | 68.6171 | 314000 | 134000 | 19.9 | 6250 | 1358.6369 |  | 1
85 | 80 | 67 | 51.5724 | 283000 | 163000 | 19.1 | 6250 | 1358.6369 |  | 1
85 | 80 | 62 | 36.2232 | 261000 | 200000 | 18.9 | 6250 | 1316.9609 |  | 1
85 | 80 | 57 | 22.3618 | 229000 | 220000 | 18.1 | 6250 | 1316.9609 |  | 1
85 | 80 | 75 | 79.7527 | 332000 | 107000 | 19.9 | 7500 | 1969.1899 |  | 1
85 | 80 | 72 | 68.6171 | 315000 | 132000 | 19.6 | 7500 | 1969.1899 |  | 1
85 | 80 | 67 | 51.5724 | 288000 | 173000 | 19.2 | 7500 | 1969.1899 |  | 1
85 | 80 | 62 | 36.2232 | 274000 | 223000 | 19.2 | 7500 | 1925.4302 |  | 1
85 | 80 | 57 | 22.3618 | 252000 | 252000 | 18.8 | 7500 | 1925.4302 |  | 1
85 | 80 | 75 | 79.7527 | 356000 | 128000 | 20.7 | 8750 | 2829.7989 |  | 1
85 | 80 | 72 | 68.6171 | 337000 | 154000 | 20.3 | 8750 | 2738.1117 |  | 1
85 | 80 | 67 | 51.5724 | 305000 | 195000 | 19.5 | 8750 | 2738.1117 |  | 1
85 | 80 | 62 | 36.2232 | 272000 | 233000 | 18.9 | 8750 | 2692.2682 |  | 1
85 | 80 | 57 | 22.3618 | 260000 | 260000 | 18.6 | 8750 | 2692.2682 |  | 1
95 | 80 | 75 | 79.7527 | 285000 | 79000 | 21.5 | 5000 | 898.1173 |  | 1
95 | 80 | 72 | 68.6171 | 281000 | 110000 | 21.7 | 5000 | 898.1173 |  | 1
95 | 80 | 67 | 51.5724 | 255000 | 138000 | 21.2 | 5000 | 858.5251 |  | 1
95 | 80 | 62 | 36.2232 | 232000 | 166000 | 20.8 | 5000 | 858.5251 |  | 1
95 | 80 | 57 | 22.3618 | 208000 | 190000 | 20.3 | 5000 | 821.0168 |  | 1
95 | 80 | 75 | 79.7527 | 312000 | 98000 | 22.4 | 6250 | 1358.6369 |  | 1
95 | 80 | 72 | 68.6171 | 297000 | 120000 | 22 | 6250 | 1358.6369 |  | 1
95 | 80 | 67 | 51.5724 | 265000 | 149000 | 21.2 | 6250 | 1316.9609 |  | 1
95 | 80 | 62 | 36.2232 | 248000 | 189000 | 21.1 | 6250 | 1316.9609 |  | 1
95 | 80 | 57 | 22.3618 | 226000 | 218000 | 20.8 | 6250 | 1316.9609 |  | 1
95 | 80 | 75 | 79.7527 | 325000 | 105000 | 22.6 | 7500 | 1969.1899 |  | 1
95 | 80 | 72 | 68.6171 | 309000 | 129000 | 22.2 | 7500 | 1969.1899 |  | 1
95 | 80 | 67 | 51.5724 | 271000 | 159000 | 21.3 | 7500 | 1925.4302 |  | 1
95 | 80 | 62 | 36.2232 | 258000 | 211000 | 21.2 | 7500 | 1925.4302 |  | 1
95 | 80 | 57 | 22.3618 | 239000 | 239000 | 20.9 | 7500 | 1925.4302 |  | 1
95 | 80 | 75 | 79.7527 | 336000 | 112000 | 22.9 | 8750 | 2738.1117 |  | 1
95 | 80 | 72 | 68.6171 | 318000 | 139000 | 22.4 | 8750 | 2738.1117 |  | 1
95 | 80 | 67 | 51.5724 | 280000 | 174000 | 21.4 | 8750 | 2692.2682 |  | 1
95 | 80 | 62 | 36.2232 | 256000 | 219000 | 21 | 8750 | 2692.2682 |  | 1
95 | 80 | 57 | 22.3618 | 254000 | 254000 | 21.2 | 8750 | 2692.2682 |  | 1
105 | 80 | 75 | 79.7527 | 267000 | 66000 | 23.9 | 5000 | 858.5251 |  | 1
105 | 80 | 72 | 68.6171 | 264000 | 97000 | 24.1 | 5000 | 858.5251 |  | 1
105 | 80 | 67 | 51.5724 | 229000 | 115000 | 23.1 | 5000 | 858.5251 |  | 1
105 | 80 | 62 | 36.2232 | 217000 | 153000 | 23.1 | 5000 | 858.5251 |  | 1
105 | 80 | 57 | 22.3618 | 196000 | 180000 | 22.8 | 5000 | 821.0168 |  | 1
105 | 80 | 75 | 79.7527 | 294000 | 83000 | 24.8 | 6250 | 1358.6369 |  | 1
105 | 80 | 72 | 68.6171 | 279000 | 106000 | 24.5 | 6250 | 1316.9609 |  | 1
105 | 80 | 67 | 51.5724 | 253000 | 140000 | 23.9 | 6250 | 1316.9609 |  | 1
105 | 80 | 62 | 36.2232 | 231000 | 176000 | 23.4 | 6250 | 1316.9609 |  | 1
105 | 80 | 57 | 22.3618 | 212000 | 205000 | 23.2 | 6250 | 1316.9609 |  | 1
105 | 80 | 75 | 79.7527 | 293000 | 76000 | 24.4 | 7500 | 1969.1899 |  | 1
105 | 80 | 72 | 68.6171 | 278000 | 102000 | 24.1 | 7500 | 1925.4302 |  | 1
105 | 80 | 67 | 51.5724 | 254000 | 145000 | 23.6 | 7500 | 1925.4302 |  | 1
105 | 80 | 62 | 36.2232 | 228000 | 183000 | 23.1 | 7500 | 1925.4302 |  | 1
105 | 80 | 57 | 22.3618 | 222000 | 222000 | 23.4 | 7500 | 1925.4302 |  | 1
105 | 80 | 75 | 79.7527 | 309000 | 93000 | 25.1 | 8750 | 2738.1117 |  | 1
105 | 80 | 72 | 68.6171 | 293000 | 120000 | 24.6 | 8750 | 2738.1117 |  | 1
105 | 80 | 67 | 51.5724 | 267000 | 166000 | 24 | 8750 | 2692.2682 |  | 1
105 | 80 | 62 | 36.2232 | 235000 | 201000 | 23.2 | 8750 | 2692.2682 |  | 1
105 | 80 | 57 | 22.3618 | 236000 | 236000 | 23.7 | 8750 | 2692.2682 |  | 1
115 | 80 | 75 | 79.7527 | 253000 | 58000 | 26.6 | 5000 | 858.5251 |  | 1
115 | 80 | 72 | 68.6171 | 245000 | 83000 | 26.9 | 5000 | 858.5251 |  | 1
115 | 80 | 67 | 51.5724 | 221000 | 112000 | 26.4 | 5000 | 858.5251 |  | 1
115 | 80 | 62 | 36.2232 | 189000 | 129000 | 25.2 | 5000 | 821.0168 |  | 1
115 | 80 | 57 | 22.3618 | 170000 | 155000 | 24.7 | 5000 | 821.0168 |  | 1
115 | 80 | 75 | 79.7527 | 259000 | 55000 | 26.7 | 6250 | 1316.9609 |  | 1
115 | 80 | 72 | 68.6171 | 252000 | 85000 | 26.7 | 6250 | 1316.9609 |  | 1
115 | 80 | 67 | 51.5724 | 223000 | 114000 | 25.9 | 6250 | 1316.9609 |  | 1
115 | 80 | 62 | 36.2232 | 201000 | 149000 | 25.5 | 6250 | 1277.3687 |  | 1
115 | 80 | 57 | 22.3618 | 184000 | 178000 | 25.1 | 6250 | 1277.3687 |  | 1
115 | 80 | 75 | 79.7527 | 268000 | 60000 | 26.9 | 7500 | 1925.4302 |  | 1
115 | 80 | 72 | 68.6171 | 255000 | 86000 | 26.6 | 7500 | 1925.4302 |  | 1
115 | 80 | 67 | 51.5724 | 244000 | 140000 | 26.7 | 7500 | 1925.4302 |  | 1
115 | 80 | 62 | 36.2232 | 211000 | 169000 | 25.7 | 7500 | 1925.4302 |  | 1
115 | 80 | 57 | 22.3618 | 196000 | 196000 | 25.3 | 7500 | 1885.838 |  | 1
115 | 80 | 75 | 79.7527 | 276000 | 64000 | 27.1 | 8750 | 2692.2682 |  | 1
115 | 80 | 72 | 68.6171 | 262000 | 93000 | 26.8 | 8750 | 2692.2682 |  | 1
115 | 80 | 67 | 51.5724 | 239000 | 141000 | 26.3 | 8750 | 2692.2682 |  | 1
115 | 80 | 62 | 36.2232 | 218000 | 187000 | 25.8 | 8750 | 2692.2682 |  | 1
115 | 80 | 57 | 22.3618 | 220000 | 220000 | 26.3 | 8750 | 2692.2682 |  | 1
75 | 80 | 75 | 79.7527 | 371000 | 136000 | 18.4 | 10000 | 3771.676 |  | 1
75 | 80 | 72 | 68.6171 | 353000 | 166000 | 18.1 | 10000 | 3771.676 |  | 1
75 | 80 | 67 | 51.5724 | 336000 | 229000 | 18 | 10000 | 3679.9888 |  | 1
75 | 80 | 62 | 36.2232 | 306000 | 276000 | 17.6 | 10000 | 3679.9888 |  | 1
75 | 80 | 57 | 22.3618 | 295000 | 295000 | 17.4 | 10000 | 3679.9888 |  | 1
75 | 80 | 75 | 79.7527 | 378000 | 142000 | 18.4 | 11250 | 4936.5196 |  | 1
75 | 80 | 72 | 68.6171 | 372000 | 189000 | 18.6 | 11250 | 4936.5196 |  | 1
75 | 80 | 67 | 51.5724 | 342000 | 244000 | 18.1 | 11250 | 4840.6648 |  | 1
75 | 80 | 62 | 36.2232 | 313000 | 294000 | 17.7 | 11250 | 4840.6648 |  | 1
75 | 80 | 57 | 22.3618 | 306000 | 306000 | 17.6 | 11250 | 4840.6648 |  | 1
75 | 80 | 75 | 79.7527 | 383000 | 148000 | 18.6 | 12500 | 6286.8212 |  | 1
75 | 80 | 72 | 68.6171 | 365000 | 184000 | 18.3 | 12500 | 6286.8212 |  | 1
75 | 80 | 67 | 51.5724 | 348000 | 258000 | 18.2 | 12500 | 6190.9665 |  | 1
75 | 80 | 62 | 36.2232 | 309000 | 299000 | 17.4 | 12500 | 6190.9665 |  | 1
75 | 80 | 57 | 22.3618 | 316000 | 316000 | 17.7 | 12500 | 6190.9665 |  | 1
85 | 80 | 75 | 79.7527 | 349000 | 119000 | 20.2 | 10000 | 3679.9888 |  | 1
85 | 80 | 72 | 68.6171 | 332000 | 151000 | 19.9 | 10000 | 3679.9888 |  | 1
85 | 80 | 67 | 51.5724 | 305000 | 203000 | 19.5 | 10000 | 3679.9888 |  | 1
85 | 80 | 62 | 36.2232 | 279000 | 252000 | 19 | 10000 | 3634.1453 |  | 1
85 | 80 | 57 | 22.3618 | 269000 | 269000 | 18.8 | 10000 | 3634.1453 |  | 1
85 | 80 | 75 | 79.7527 | 355000 | 125000 | 20.3 | 11250 | 4936.5196 |  | 1
85 | 80 | 72 | 68.6171 | 338000 | 159000 | 20.1 | 11250 | 4840.6648 |  | 1
85 | 80 | 67 | 51.5724 | 311000 | 217000 | 19.6 | 11250 | 4840.6648 |  | 1
85 | 80 | 62 | 36.2232 | 285000 | 268000 | 19.1 | 11250 | 4840.6648 |  | 1
85 | 80 | 57 | 22.3618 | 289000 | 289000 | 19.4 | 11250 | 4840.6648 |  | 1
85 | 80 | 75 | 79.7527 | 374000 | 144000 | 21 | 12500 | 6286.8212 |  | 1
85 | 80 | 72 | 68.6171 | 343000 | 168000 | 20.1 | 12500 | 6190.9665 |  | 1
85 | 80 | 67 | 51.5724 | 316000 | 230000 | 19.7 | 12500 | 6190.9665 |  | 1
85 | 80 | 62 | 36.2232 | 303000 | 294000 | 19.7 | 12500 | 6190.9665 |  | 1
85 | 80 | 57 | 22.3618 | 288000 | 288000 | 19.2 | 12500 | 6190.9665 |  | 1
95 | 80 | 75 | 79.7527 | 327000 | 103000 | 22.2 | 10000 | 3679.9888 |  | 1
95 | 80 | 72 | 68.6171 | 312000 | 135000 | 22 | 10000 | 3679.9888 |  | 1
95 | 80 | 67 | 51.5724 | 286000 | 188000 | 21.6 | 10000 | 3679.9888 |  | 1
95 | 80 | 62 | 36.2232 | 262000 | 237000 | 21.1 | 10000 | 3634.1453 |  | 1
95 | 80 | 57 | 22.3618 | 254000 | 254000 | 20.9 | 10000 | 3634.1453 |  | 1
95 | 80 | 75 | 79.7527 | 333000 | 108000 | 22.5 | 11250 | 4840.6648 |  | 1
95 | 80 | 72 | 68.6171 | 317000 | 143000 | 22.2 | 11250 | 4840.6648 |  | 1
95 | 80 | 67 | 51.5724 | 291000 | 202000 | 21.7 | 11250 | 4840.6648 |  | 1
95 | 80 | 62 | 36.2232 | 268000 | 252000 | 21.2 | 11250 | 4792.7374 |  | 1
95 | 80 | 57 | 22.3618 | 263000 | 263000 | 21.1 | 11250 | 4792.7374 |  | 1
95 | 80 | 75 | 79.7527 | 352000 | 128000 | 23.1 | 12500 | 6286.8212 |  | 1
95 | 80 | 72 | 68.6171 | 333000 | 163000 | 22.7 | 12500 | 6190.9665 |  | 1
95 | 80 | 67 | 51.5724 | 304000 | 223000 | 22 | 12500 | 6190.9665 |  | 1
95 | 80 | 62 | 36.2232 | 274000 | 265000 | 21.3 | 12500 | 6143.0391 |  | 1
95 | 80 | 57 | 22.3618 | 271000 | 271000 | 21.3 | 12500 | 6143.0391 |  | 1
105 | 80 | 75 | 79.7527 | 315000 | 98000 | 25.2 | 10000 | 3679.9888 |  | 1
105 | 80 | 72 | 68.6171 | 290000 | 119000 | 24.4 | 10000 | 3679.9888 |  | 1
105 | 80 | 67 | 51.5724 | 263000 | 169000 | 23.8 | 10000 | 3634.1453 |  | 1
105 | 80 | 62 | 36.2232 | 254000 | 231000 | 24 | 10000 | 3634.1453 |  | 1
105 | 80 | 57 | 22.3618 | 246000 | 246000 | 23.8 | 10000 | 3634.1453 |  | 1
105 | 80 | 75 | 79.7527 | 323000 | 106000 | 25.5 | 11250 | 4840.6648 |  | 1
105 | 80 | 72 | 68.6171 | 307000 | 139000 | 25.1 | 11250 | 4840.6648 |  | 1
105 | 80 | 67 | 51.5724 | 269000 | 182000 | 23.9 | 11250 | 4792.7374 |  | 1
105 | 80 | 62 | 36.2232 | 260000 | 244000 | 24.1 | 11250 | 4792.7374 |  | 1
105 | 80 | 57 | 22.3618 | 254000 | 254000 | 24 | 11250 | 4792.7374 |  | 1
105 | 80 | 75 | 79.7527 | 325000 | 109000 | 25.5 | 12500 | 6190.9665 |  | 1
105 | 80 | 72 | 68.6171 | 296000 | 132000 | 24.5 | 12500 | 6190.9665 |  | 1
105 | 80 | 67 | 51.5724 | 273000 | 195000 | 24 | 12500 | 6143.0391 |  | 1
105 | 80 | 62 | 36.2232 | 253000 | 244000 | 23.6 | 12500 | 6143.0391 |  | 1
105 | 80 | 57 | 22.3618 | 251000 | 251000 | 23.5 | 12500 | 6143.0391 |  | 1
115 | 80 | 75 | 79.7527 | 281000 | 69000 | 27.2 | 10000 | 3679.9888 |  | 1
115 | 80 | 72 | 68.6171 | 281000 | 114000 | 27.5 | 10000 | 3679.9888 |  | 1
115 | 80 | 67 | 51.5724 | 257000 | 167000 | 27 | 10000 | 3634.1453 |  | 1
115 | 80 | 62 | 36.2232 | 237000 | 214000 | 26.7 | 10000 | 3634.1453 |  | 1
115 | 80 | 57 | 22.3618 | 230000 | 230000 | 26.5 | 10000 | 3634.1453 |  | 1
115 | 80 | 75 | 79.7527 | 286000 | 73000 | 27.4 | 11250 | 4840.6648 |  | 1
115 | 80 | 72 | 68.6171 | 285000 | 121000 | 27.6 | 11250 | 4840.6648 |  | 1
115 | 80 | 67 | 51.5724 | 249000 | 167000 | 26.5 | 11250 | 4792.7374 |  | 1
115 | 80 | 62 | 36.2232 | 230000 | 215000 | 26.1 | 11250 | 4792.7374 |  | 1
115 | 80 | 57 | 22.3618 | 238000 | 238000 | 26.6 | 11250 | 4792.7374 |  | 1
115 | 80 | 75 | 79.7527 | 290000 | 77000 | 27.4 | 12500 | 6190.9665 |  | 1
115 | 80 | 72 | 68.6171 | 289000 | 129000 | 27.7 | 12500 | 6190.9665 |  | 1
115 | 80 | 67 | 51.5724 | 266000 | 192000 | 27.2 | 12500 | 6143.0391 |  | 1
115 | 80 | 62 | 36.2232 | 235000 | 227000 | 26.2 | 12500 | 6143.0391 |  | 1
115 | 80 | 57 | 22.3618 | 233000 | 233000 | 26.1 | 12500 | 6143.0391 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 3
Degradation Coefficient (C_d) |  | 48/50A027 (27 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 329000 | 117000 | 17.7 | 5400 | 1039.8156 |  | 1
75 | 80 | 72 | 68.6171 | 312000 | 135000 | 17.5 | 5400 | 1039.8156 |  | 1
75 | 80 | 67 | 51.5724 | 279000 | 159000 | 16.8 | 5400 | 1000.2235 |  | 1
75 | 80 | 62 | 36.2232 | 257000 | 190000 | 16.6 | 5400 | 1000.2235 |  | 1
75 | 80 | 57 | 22.3618 | 232000 | 215000 | 16.3 | 5400 | 1000.2235 |  | 1
75 | 80 | 75 | 79.7527 | 343000 | 121000 | 17.8 | 6750 | 1585.7709 |  | 1
75 | 80 | 72 | 68.6171 | 320000 | 138000 | 17.5 | 6750 | 1585.7709 |  | 1
75 | 80 | 67 | 51.5724 | 292000 | 172000 | 17 | 6750 | 1585.7709 |  | 1
75 | 80 | 62 | 36.2232 | 265000 | 206000 | 16.6 | 6750 | 1542.0112 |  | 1
75 | 80 | 57 | 22.3618 | 251000 | 245000 | 16.7 | 6750 | 1542.0112 |  | 1
75 | 80 | 75 | 79.7527 | 363000 | 137000 | 18.4 | 8100 | 2398.4525 |  | 1
75 | 80 | 72 | 68.6171 | 343000 | 159000 | 18 | 8100 | 2310.933 |  | 1
75 | 80 | 67 | 51.5724 | 313000 | 198000 | 17.4 | 8100 | 2310.933 |  | 1
75 | 80 | 62 | 36.2232 | 284000 | 236000 | 16.9 | 8100 | 2310.933 |  | 1
75 | 80 | 57 | 22.3618 | 263000 | 263000 | 16.6 | 8100 | 2267.1732 |  | 1
75 | 80 | 75 | 79.7527 | 360000 | 131000 | 18.2 | 9450 | 3346.581 |  | 1
75 | 80 | 72 | 68.6171 | 343000 | 159000 | 17.8 | 9450 | 3254.8939 |  | 1
75 | 80 | 67 | 51.5724 | 312000 | 204000 | 17.5 | 9450 | 3254.8939 |  | 1
75 | 80 | 62 | 36.2232 | 286000 | 251000 | 17 | 9450 | 3254.8939 |  | 1
75 | 80 | 57 | 22.3618 | 271000 | 271000 | 16.7 | 9450 | 3209.0503 |  | 1
85 | 80 | 75 | 79.7527 | 311000 | 103000 | 19.6 | 5400 | 1039.8156 |  | 1
85 | 80 | 72 | 68.6171 | 295000 | 122000 | 19.4 | 5400 | 1039.8156 |  | 1
85 | 80 | 67 | 51.5724 | 267000 | 150000 | 18.9 | 5400 | 1000.2235 |  | 1
85 | 80 | 62 | 36.2232 | 234000 | 169000 | 18.2 | 5400 | 1000.2235 |  | 1
85 | 80 | 57 | 22.3618 | 211000 | 196000 | 17.8 | 5400 | 1000.2235 |  | 1
85 | 80 | 75 | 79.7527 | 329000 | 112000 | 20 | 6750 | 1585.7709 |  | 1
85 | 80 | 72 | 68.6171 | 310000 | 132000 | 19.6 | 6750 | 1585.7709 |  | 1
85 | 80 | 67 | 51.5724 | 284000 | 168000 | 19.3 | 6750 | 1585.7709 |  | 1
85 | 80 | 62 | 36.2232 | 258000 | 202000 | 18.8 | 6750 | 1542.0112 |  | 1
85 | 80 | 57 | 22.3618 | 227000 | 222000 | 18 | 6750 | 1542.0112 |  | 1
85 | 80 | 75 | 79.7527 | 342000 | 120000 | 20.2 | 8100 | 2310.933 |  | 1
85 | 80 | 72 | 68.6171 | 324000 | 144000 | 19.9 | 8100 | 2310.933 |  | 1
85 | 80 | 67 | 51.5724 | 295000 | 184000 | 19.3 | 8100 | 2310.933 |  | 1
85 | 80 | 62 | 36.2232 | 269000 | 225000 | 18.9 | 8100 | 2267.1732 |  | 1
85 | 80 | 57 | 22.3618 | 242000 | 242000 | 18.3 | 8100 | 2267.1732 |  | 1
85 | 80 | 75 | 79.7527 | 339000 | 114000 | 20 | 9450 | 3254.8939 |  | 1
85 | 80 | 72 | 68.6171 | 322000 | 143000 | 19.7 | 9450 | 3254.8939 |  | 1
85 | 80 | 67 | 51.5724 | 305000 | 200000 | 19.5 | 9450 | 3254.8939 |  | 1
85 | 80 | 62 | 36.2232 | 278000 | 246000 | 19.1 | 9450 | 3209.0503 |  | 1
85 | 80 | 57 | 22.3618 | 255000 | 255000 | 18.5 | 9450 | 3209.0503 |  | 1
95 | 80 | 75 | 79.7527 | 283000 | 78000 | 21.4 | 5400 | 1039.8156 |  | 1
95 | 80 | 72 | 68.6171 | 267000 | 97000 | 21.1 | 5400 | 1000.2235 |  | 1
95 | 80 | 67 | 51.5724 | 242000 | 127000 | 20.6 | 5400 | 1000.2235 |  | 1
95 | 80 | 62 | 36.2232 | 219000 | 156000 | 20.2 | 5400 | 1000.2235 |  | 1
95 | 80 | 57 | 22.3618 | 197000 | 184000 | 19.8 | 5400 | 960.6313 |  | 1
95 | 80 | 75 | 79.7527 | 309000 | 96000 | 22.1 | 6750 | 1585.7709 |  | 1
95 | 80 | 72 | 68.6171 | 292000 | 117000 | 21.7 | 6750 | 1585.7709 |  | 1
95 | 80 | 67 | 51.5724 | 266000 | 153000 | 21.2 | 6750 | 1542.0112 |  | 1
95 | 80 | 62 | 36.2232 | 233000 | 180000 | 20.5 | 6750 | 1542.0112 |  | 1
95 | 80 | 57 | 22.3618 | 213000 | 208000 | 20.1 | 6750 | 1542.0112 |  | 1
95 | 80 | 75 | 79.7527 | 316000 | 98000 | 22.1 | 8100 | 2310.933 |  | 1
95 | 80 | 72 | 68.6171 | 293000 | 117000 | 21.6 | 8100 | 2310.933 |  | 1
95 | 80 | 67 | 51.5724 | 267000 | 160000 | 21.1 | 8100 | 2267.1732 |  | 1
95 | 80 | 62 | 36.2232 | 243000 | 201000 | 20.7 | 8100 | 2267.1732 |  | 1
95 | 80 | 57 | 22.3618 | 237000 | 237000 | 20.8 | 8100 | 2267.1732 |  | 1
95 | 80 | 75 | 79.7527 | 329000 | 109000 | 22.5 | 9450 | 3254.8939 |  | 1
95 | 80 | 72 | 68.6171 | 309000 | 134000 | 22 | 9450 | 3254.8939 |  | 1
95 | 80 | 67 | 51.5724 | 284000 | 184000 | 21.5 | 9450 | 3254.8939 |  | 1
95 | 80 | 62 | 36.2232 | 260000 | 230000 | 21.1 | 9450 | 3209.0503 |  | 1
95 | 80 | 57 | 22.3618 | 251000 | 251000 | 21.1 | 9450 | 3209.0503 |  | 1
105 | 80 | 75 | 79.7527 | 275000 | 74000 | 24.2 | 5400 | 1000.2235 |  | 1
105 | 80 | 72 | 68.6171 | 260000 | 93000 | 23.8 | 5400 | 1000.2235 |  | 1
105 | 80 | 67 | 51.5724 | 229000 | 116000 | 23 | 5400 | 1000.2235 |  | 1
105 | 80 | 62 | 36.2232 | 204000 | 144000 | 22.5 | 5400 | 960.6313 |  | 1
105 | 80 | 57 | 22.3618 | 192000 | 179000 | 22.5 | 5400 | 960.6313 |  | 1
105 | 80 | 75 | 79.7527 | 278000 | 69000 | 24 | 6750 | 1542.0112 |  | 1
105 | 80 | 72 | 68.6171 | 263000 | 92000 | 23.7 | 6750 | 1542.0112 |  | 1
105 | 80 | 67 | 51.5724 | 247000 | 137000 | 23.5 | 6750 | 1542.0112 |  | 1
105 | 80 | 62 | 36.2232 | 217000 | 166000 | 22.8 | 6750 | 1542.0112 |  | 1
105 | 80 | 57 | 22.3618 | 208000 | 204000 | 22.8 | 6750 | 1502.419 |  | 1
105 | 80 | 75 | 79.7527 | 294000 | 81000 | 24.4 | 8100 | 2310.933 |  | 1
105 | 80 | 72 | 68.6171 | 282000 | 110000 | 24.2 | 8100 | 2310.933 |  | 1
105 | 80 | 67 | 51.5724 | 258000 | 154000 | 23.8 | 8100 | 2267.1732 |  | 1
105 | 80 | 62 | 36.2232 | 236000 | 197000 | 23.3 | 8100 | 2267.1732 |  | 1
105 | 80 | 57 | 22.3618 | 222000 | 222000 | 23.1 | 8100 | 2267.1732 |  | 1
105 | 80 | 75 | 79.7527 | 299000 | 84000 | 24.5 | 9450 | 3254.8939 |  | 1
105 | 80 | 72 | 68.6171 | 289000 | 118000 | 24.3 | 9450 | 3254.8939 |  | 1
105 | 80 | 67 | 51.5724 | 265000 | 168000 | 23.9 | 9450 | 3209.0503 |  | 1
105 | 80 | 62 | 36.2232 | 241000 | 215000 | 23.4 | 9450 | 3209.0503 |  | 1
105 | 80 | 57 | 22.3618 | 233000 | 233000 | 23.3 | 9450 | 3209.0503 |  | 1
115 | 80 | 75 | 79.7527 | 245000 | 48000 | 26.4 | 5400 | 1000.2235 |  | 1
115 | 80 | 72 | 68.6171 | 241000 | 78000 | 26.4 | 5400 | 1000.2235 |  | 1
115 | 80 | 67 | 51.5724 | 217000 | 108000 | 25.9 | 5400 | 1000.2235 |  | 1
115 | 80 | 62 | 36.2232 | 196000 | 139000 | 25.5 | 5400 | 960.6313 |  | 1
115 | 80 | 57 | 22.3618 | 169000 | 157000 | 24.7 | 5400 | 960.6313 |  | 1
115 | 80 | 75 | 79.7527 | 267000 | 63000 | 27 | 6750 | 1542.0112 |  | 1
115 | 80 | 72 | 68.6171 | 251000 | 84000 | 26.6 | 6750 | 1542.0112 |  | 1
115 | 80 | 67 | 51.5724 | 230000 | 124000 | 26.1 | 6750 | 1542.0112 |  | 1
115 | 80 | 62 | 36.2232 | 200000 | 152000 | 25.4 | 6750 | 1502.419 |  | 1
115 | 80 | 57 | 22.3618 | 192000 | 189000 | 25.4 | 6750 | 1502.419 |  | 1
115 | 80 | 75 | 79.7527 | 276000 | 67000 | 27.2 | 8100 | 2267.1732 |  | 1
115 | 80 | 72 | 68.6171 | 253000 | 85000 | 26.5 | 8100 | 2267.1732 |  | 1
115 | 80 | 67 | 51.5724 | 230000 | 130000 | 26 | 8100 | 2267.1732 |  | 1
115 | 80 | 62 | 36.2232 | 209000 | 172000 | 25.6 | 8100 | 2225.4972 |  | 1
115 | 80 | 57 | 22.3618 | 196000 | 196000 | 25.3 | 8100 | 2225.4972 |  | 1
115 | 80 | 75 | 79.7527 | 283000 | 72000 | 27.3 | 9450 | 3254.8939 |  | 1
115 | 80 | 72 | 68.6171 | 267000 | 101000 | 27 | 9450 | 3209.0503 |  | 1
115 | 80 | 67 | 51.5724 | 245000 | 152000 | 26.4 | 9450 | 3209.0503 |  | 1
115 | 80 | 62 | 36.2232 | 216000 | 189000 | 25.7 | 9450 | 3209.0503 |  | 1
115 | 80 | 57 | 22.3618 | 216000 | 216000 | 25.9 | 9450 | 3209.0503 |  | 1
75 | 80 | 75 | 79.7527 | 368000 | 137000 | 18.2 | 10800 | 4494.7542 |  | 1
75 | 80 | 72 | 68.6171 | 351000 | 169000 | 18 | 10800 | 4494.7542 |  | 1
75 | 80 | 67 | 51.5724 | 332000 | 232000 | 17.8 | 10800 | 4398.8994 |  | 1
75 | 80 | 62 | 36.2232 | 302000 | 278000 | 17.3 | 10800 | 4398.8994 |  | 1
75 | 80 | 57 | 22.3618 | 284000 | 284000 | 16.9 | 10800 | 4398.8994 |  | 1
75 | 80 | 75 | 79.7527 | 375000 | 144000 | 18.4 | 12150 | 5878.3966 |  | 1
75 | 80 | 72 | 68.6171 | 359000 | 181000 | 18 | 12150 | 5878.3966 |  | 1
75 | 80 | 67 | 51.5724 | 338000 | 246000 | 17.9 | 12150 | 5782.5419 |  | 1
75 | 80 | 62 | 36.2232 | 311000 | 298000 | 17.5 | 12150 | 5782.5419 |  | 1
75 | 80 | 57 | 22.3618 | 302000 | 302000 | 17.2 | 12150 | 5782.5419 |  | 1
75 | 80 | 75 | 79.7527 | 393000 | 163000 | 18.9 | 13500 | 7528.7654 |  | 1
75 | 80 | 72 | 68.6171 | 374000 | 199000 | 18.5 | 13500 | 7528.7654 |  | 1
75 | 80 | 67 | 51.5724 | 343000 | 260000 | 18 | 13500 | 7432.9106 |  | 1
75 | 80 | 62 | 36.2232 | 315000 | 309000 | 17.5 | 13500 | 7432.9106 |  | 1
75 | 80 | 57 | 22.3618 | 303000 | 303000 | 17.2 | 13500 | 7432.9106 |  | 1
85 | 80 | 75 | 79.7527 | 346000 | 120000 | 20.1 | 10800 | 4398.8994 |  | 1
85 | 80 | 72 | 68.6171 | 329000 | 152000 | 19.8 | 10800 | 4398.8994 |  | 1
85 | 80 | 67 | 51.5724 | 302000 | 205000 | 19.4 | 10800 | 4398.8994 |  | 1
85 | 80 | 62 | 36.2232 | 284000 | 263000 | 19.2 | 10800 | 4398.8994 |  | 1
85 | 80 | 57 | 22.3618 | 276000 | 276000 | 19.1 | 10800 | 4350.9721 |  | 1
85 | 80 | 75 | 79.7527 | 351000 | 126000 | 20.2 | 12150 | 5878.3966 |  | 1
85 | 80 | 72 | 68.6171 | 340000 | 167000 | 20 | 12150 | 5782.5419 |  | 1
85 | 80 | 67 | 51.5724 | 317000 | 229000 | 19.7 | 12150 | 5782.5419 |  | 1
85 | 80 | 62 | 36.2232 | 288000 | 275000 | 19.1 | 12150 | 5782.5419 |  | 1
85 | 80 | 57 | 22.3618 | 288000 | 288000 | 19.3 | 12150 | 5782.5419 |  | 1
85 | 80 | 75 | 79.7527 | 356000 | 131000 | 20.2 | 13500 | 7528.7654 |  | 1
85 | 80 | 72 | 68.6171 | 340000 | 170000 | 20 | 13500 | 7432.9106 |  | 1
85 | 80 | 67 | 51.5724 | 312000 | 233000 | 19.5 | 13500 | 7432.9106 |  | 1
85 | 80 | 62 | 36.2232 | 288000 | 283000 | 19.1 | 13500 | 7432.9106 |  | 1
85 | 80 | 57 | 22.3618 | 286000 | 286000 | 19.1 | 13500 | 7432.9106 |  | 1
95 | 80 | 75 | 79.7527 | 328000 | 107000 | 22.2 | 10800 | 4398.8994 |  | 1
95 | 80 | 72 | 68.6171 | 317000 | 144000 | 22.1 | 10800 | 4398.8994 |  | 1
95 | 80 | 67 | 51.5724 | 290000 | 198000 | 21.7 | 10800 | 4398.8994 |  | 1
95 | 80 | 62 | 36.2232 | 267000 | 247000 | 21.3 | 10800 | 4350.9721 |  | 1
95 | 80 | 57 | 22.3618 | 250000 | 250000 | 20.8 | 10800 | 4350.9721 |  | 1
95 | 80 | 75 | 79.7527 | 342000 | 121000 | 22.8 | 12150 | 5782.5419 |  | 1
95 | 80 | 72 | 68.6171 | 324000 | 155000 | 22.3 | 12150 | 5782.5419 |  | 1
95 | 80 | 67 | 51.5724 | 295000 | 211000 | 21.7 | 12150 | 5782.5419 |  | 1
95 | 80 | 62 | 36.2232 | 264000 | 252000 | 21.1 | 12150 | 5734.6145 |  | 1
95 | 80 | 57 | 22.3618 | 269000 | 269000 | 21.3 | 12150 | 5734.6145 |  | 1
95 | 80 | 75 | 79.7527 | 345000 | 125000 | 22.7 | 13500 | 7432.9106 |  | 1
95 | 80 | 72 | 68.6171 | 329000 | 164000 | 22.4 | 13500 | 7432.9106 |  | 1
95 | 80 | 67 | 51.5724 | 300000 | 225000 | 21.8 | 13500 | 7432.9106 |  | 1
95 | 80 | 62 | 36.2232 | 270000 | 265000 | 21.2 | 13500 | 7384.9832 |  | 1
95 | 80 | 57 | 22.3618 | 278000 | 278000 | 21.5 | 13500 | 7384.9832 |  | 1
105 | 80 | 75 | 79.7527 | 310000 | 94000 | 24.8 | 10800 | 4398.8994 |  | 1
105 | 80 | 72 | 68.6171 | 295000 | 127000 | 24.5 | 10800 | 4398.8994 |  | 1
105 | 80 | 67 | 51.5724 | 262000 | 174000 | 23.7 | 10800 | 4350.9721 |  | 1
105 | 80 | 62 | 36.2232 | 240000 | 221000 | 23.3 | 10800 | 4350.9721 |  | 1
105 | 80 | 57 | 22.3618 | 244000 | 244000 | 23.5 | 10800 | 4350.9721 |  | 1
105 | 80 | 75 | 79.7527 | 306000 | 90000 | 24.6 | 12150 | 5782.5419 |  | 1
105 | 80 | 72 | 68.6171 | 301000 | 137000 | 24.6 | 12150 | 5782.5419 |  | 1
105 | 80 | 67 | 51.5724 | 274000 | 194000 | 24 | 12150 | 5734.6145 |  | 1
105 | 80 | 62 | 36.2232 | 255000 | 244000 | 23.7 | 12150 | 5734.6145 |  | 1
105 | 80 | 57 | 22.3618 | 242000 | 242000 | 23.3 | 12150 | 5734.6145 |  | 1
105 | 80 | 75 | 79.7527 | 310000 | 95000 | 24.7 | 13500 | 7432.9106 |  | 1
105 | 80 | 72 | 68.6171 | 295000 | 135000 | 24.4 | 13500 | 7432.9106 |  | 1
105 | 80 | 67 | 51.5724 | 271000 | 201000 | 23.9 | 13500 | 7384.9832 |  | 1
105 | 80 | 62 | 36.2232 | 257000 | 255000 | 23.7 | 13500 | 7384.9832 |  | 1
105 | 80 | 57 | 22.3618 | 250000 | 250000 | 23.5 | 13500 | 7384.9832 |  | 1
115 | 80 | 75 | 79.7527 | 288000 | 77000 | 27.4 | 10800 | 4398.8994 |  | 1
115 | 80 | 72 | 68.6171 | 273000 | 110000 | 27.1 | 10800 | 4350.9721 |  | 1
115 | 80 | 67 | 51.5724 | 242000 | 158000 | 26.3 | 10800 | 4350.9721 |  | 1
115 | 80 | 62 | 36.2232 | 222000 | 204000 | 25.8 | 10800 | 4350.9721 |  | 1
115 | 80 | 57 | 22.3618 | 226000 | 226000 | 26.1 | 10800 | 4350.9721 |  | 1
115 | 80 | 75 | 79.7527 | 295000 | 84000 | 27.7 | 12150 | 5782.5419 |  | 1
115 | 80 | 72 | 68.6171 | 277000 | 117000 | 27.1 | 12150 | 5734.6145 |  | 1
115 | 80 | 67 | 51.5724 | 253000 | 178000 | 26.6 | 12150 | 5734.6145 |  | 1
115 | 80 | 62 | 36.2232 | 237000 | 228000 | 26.3 | 12150 | 5734.6145 |  | 1
115 | 80 | 57 | 22.3618 | 234000 | 234000 | 26.3 | 12150 | 5734.6145 |  | 1
115 | 80 | 75 | 79.7527 | 296000 | 86000 | 27.6 | 13500 | 7432.9106 |  | 1
115 | 80 | 72 | 68.6171 | 281000 | 126000 | 27.3 | 13500 | 7432.9106 |  | 1
115 | 80 | 67 | 51.5724 | 257000 | 191000 | 26.7 | 13500 | 7384.9832 |  | 1
115 | 80 | 62 | 36.2232 | 241000 | 241000 | 26.4 | 13500 | 7384.9832 |  | 1
115 | 80 | 57 | 22.3618 | 241000 | 241000 | 26.4 | 13500 | 7384.9832 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 4
Degradation Coefficient (C_d) |  | 48/50A030 (30 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 347000 | 126000 | 19.8 | 6000 | 1250.2793 |  | 1
75 | 80 | 72 | 68.6171 | 329000 | 146000 | 19.4 | 6000 | 1250.2793 |  | 1
75 | 80 | 67 | 51.5724 | 302000 | 178000 | 18.9 | 6000 | 1250.2793 |  | 1
75 | 80 | 62 | 36.2232 | 276000 | 208000 | 18.5 | 6000 | 1208.6034 |  | 1
75 | 80 | 57 | 22.3618 | 248000 | 234000 | 18.1 | 6000 | 1208.6034 |  | 1
75 | 80 | 75 | 79.7527 | 360000 | 132000 | 20.1 | 7500 | 2056.7095 |  | 1
75 | 80 | 72 | 68.6171 | 342000 | 155000 | 19.7 | 7500 | 1969.1899 |  | 1
75 | 80 | 67 | 51.5724 | 314000 | 193000 | 19.2 | 7500 | 1969.1899 |  | 1
75 | 80 | 62 | 36.2232 | 292000 | 235000 | 18.8 | 7500 | 1969.1899 |  | 1
75 | 80 | 57 | 22.3618 | 265000 | 260000 | 18.3 | 7500 | 1925.4302 |  | 1
75 | 80 | 75 | 79.7527 | 373000 | 140000 | 20.3 | 9000 | 2996.5028 |  | 1
75 | 80 | 72 | 68.6171 | 355000 | 167000 | 20 | 9000 | 2996.5028 |  | 1
75 | 80 | 67 | 51.5724 | 329000 | 215000 | 19.4 | 9000 | 2904.8156 |  | 1
75 | 80 | 62 | 36.2232 | 304000 | 260000 | 19 | 9000 | 2904.8156 |  | 1
75 | 80 | 57 | 22.3618 | 285000 | 285000 | 18.7 | 9000 | 2904.8156 |  | 1
75 | 80 | 75 | 79.7527 | 387000 | 152000 | 20.6 | 10500 | 4221.7765 |  | 1
75 | 80 | 72 | 68.6171 | 367000 | 181000 | 20.2 | 10500 | 4221.7765 |  | 1
75 | 80 | 67 | 51.5724 | 337000 | 231000 | 19.6 | 10500 | 4130.0894 |  | 1
75 | 80 | 62 | 36.2232 | 313000 | 282000 | 19.1 | 10500 | 4130.0894 |  | 1
75 | 80 | 57 | 22.3618 | 298000 | 298000 | 18.9 | 10500 | 4130.0894 |  | 1
85 | 80 | 75 | 79.7527 | 326000 | 109000 | 22 | 6000 | 1250.2793 |  | 1
85 | 80 | 72 | 68.6171 | 309000 | 130000 | 21.6 | 6000 | 1250.2793 |  | 1
85 | 80 | 67 | 51.5724 | 285000 | 164000 | 21.2 | 6000 | 1250.2793 |  | 1
85 | 80 | 62 | 36.2232 | 262000 | 197000 | 20.8 | 6000 | 1208.6034 |  | 1
85 | 80 | 57 | 22.3618 | 239000 | 226000 | 20.5 | 6000 | 1208.6034 |  | 1
85 | 80 | 75 | 79.7527 | 345000 | 121000 | 22.3 | 7500 | 1969.1899 |  | 1
85 | 80 | 72 | 68.6171 | 322000 | 139000 | 21.9 | 7500 | 1969.1899 |  | 1
85 | 80 | 67 | 51.5724 | 301000 | 183000 | 21.4 | 7500 | 1969.1899 |  | 1
85 | 80 | 62 | 36.2232 | 277000 | 223000 | 21 | 7500 | 1925.4302 |  | 1
85 | 80 | 57 | 22.3618 | 251000 | 247000 | 20.6 | 7500 | 1925.4302 |  | 1
85 | 80 | 75 | 79.7527 | 354000 | 126000 | 22.5 | 9000 | 2996.5028 |  | 1
85 | 80 | 72 | 68.6171 | 337000 | 153000 | 22.2 | 9000 | 2904.8156 |  | 1
85 | 80 | 67 | 51.5724 | 311000 | 200000 | 21.6 | 9000 | 2904.8156 |  | 1
85 | 80 | 62 | 36.2232 | 287000 | 246000 | 21.2 | 9000 | 2904.8156 |  | 1
85 | 80 | 57 | 22.3618 | 271000 | 271000 | 21 | 9000 | 2858.9721 |  | 1
85 | 80 | 75 | 79.7527 | 365000 | 135000 | 22.7 | 10500 | 4221.7765 |  | 1
85 | 80 | 72 | 68.6171 | 347000 | 165000 | 22.4 | 10500 | 4130.0894 |  | 1
85 | 80 | 67 | 51.5724 | 318000 | 215000 | 21.8 | 10500 | 4130.0894 |  | 1
85 | 80 | 62 | 36.2232 | 295000 | 267000 | 21.3 | 10500 | 4130.0894 |  | 1
85 | 80 | 57 | 22.3618 | 285000 | 285000 | 21.2 | 10500 | 4130.0894 |  | 1
95 | 80 | 75 | 79.7527 | 309000 | 97000 | 24.6 | 6000 | 1250.2793 |  | 1
95 | 80 | 72 | 68.6171 | 294000 | 118000 | 24.2 | 6000 | 1250.2793 |  | 1
95 | 80 | 67 | 51.5724 | 267000 | 149000 | 23.8 | 6000 | 1208.6034 |  | 1
95 | 80 | 62 | 36.2232 | 243000 | 182000 | 23.4 | 6000 | 1208.6034 |  | 1
95 | 80 | 57 | 22.3618 | 224000 | 214000 | 23.1 | 6000 | 1208.6034 |  | 1
95 | 80 | 75 | 79.7527 | 325000 | 105000 | 24.9 | 7500 | 1969.1899 |  | 1
95 | 80 | 72 | 68.6171 | 308000 | 129000 | 24.5 | 7500 | 1969.1899 |  | 1
95 | 80 | 67 | 51.5724 | 282000 | 168000 | 24 | 7500 | 1969.1899 |  | 1
95 | 80 | 62 | 36.2232 | 259000 | 209000 | 23.6 | 7500 | 1925.4302 |  | 1
95 | 80 | 57 | 22.3618 | 242000 | 239000 | 23.4 | 7500 | 1925.4302 |  | 1
95 | 80 | 75 | 79.7527 | 335000 | 112000 | 25.1 | 9000 | 2904.8156 |  | 1
95 | 80 | 72 | 68.6171 | 319000 | 140000 | 24.7 | 9000 | 2904.8156 |  | 1
95 | 80 | 67 | 51.5724 | 293000 | 186000 | 24.2 | 9000 | 2904.8156 |  | 1
95 | 80 | 62 | 36.2232 | 270000 | 232000 | 23.8 | 9000 | 2858.9721 |  | 1
95 | 80 | 57 | 22.3618 | 252000 | 252000 | 23.5 | 9000 | 2858.9721 |  | 1
95 | 80 | 75 | 79.7527 | 343000 | 119000 | 25.3 | 10500 | 4130.0894 |  | 1
95 | 80 | 72 | 68.6171 | 327000 | 150000 | 24.9 | 10500 | 4130.0894 |  | 1
95 | 80 | 67 | 51.5724 | 300000 | 202000 | 24.3 | 10500 | 4130.0894 |  | 1
95 | 80 | 62 | 36.2232 | 276000 | 251000 | 23.9 | 10500 | 4084.2458 |  | 1
95 | 80 | 57 | 22.3618 | 269000 | 269000 | 23.8 | 10500 | 4084.2458 |  | 1
105 | 80 | 75 | 79.7527 | 295000 | 87000 | 27.6 | 6000 | 1250.2793 |  | 1
105 | 80 | 72 | 68.6171 | 257000 | 86000 | 26.9 | 6000 | 1208.6034 |  | 1
105 | 80 | 67 | 51.5724 | 236000 | 122000 | 26.5 | 6000 | 1208.6034 |  | 1
105 | 80 | 62 | 36.2232 | 228000 | 170000 | 26.4 | 6000 | 1208.6034 |  | 1
105 | 80 | 57 | 22.3618 | 210000 | 201000 | 26.3 | 6000 | 1169.0112 |  | 1
105 | 80 | 75 | 79.7527 | 305000 | 90000 | 27.8 | 7500 | 1969.1899 |  | 1
105 | 80 | 72 | 68.6171 | 278000 | 103000 | 27.3 | 7500 | 1925.4302 |  | 1
105 | 80 | 67 | 51.5724 | 264000 | 155000 | 27 | 7500 | 1925.4302 |  | 1
105 | 80 | 62 | 36.2232 | 242000 | 195000 | 26.6 | 7500 | 1925.4302 |  | 1
105 | 80 | 57 | 22.3618 | 227000 | 225000 | 26.4 | 7500 | 1925.4302 |  | 1
105 | 80 | 75 | 79.7527 | 315000 | 97000 | 28 | 9000 | 2904.8156 |  | 1
105 | 80 | 72 | 68.6171 | 295000 | 121000 | 27.6 | 9000 | 2904.8156 |  | 1
105 | 80 | 67 | 51.5724 | 274000 | 172000 | 27.2 | 9000 | 2858.9721 |  | 1
105 | 80 | 62 | 36.2232 | 252000 | 219000 | 26.8 | 9000 | 2858.9721 |  | 1
105 | 80 | 57 | 22.3618 | 241000 | 241000 | 26.6 | 9000 | 2858.9721 |  | 1
105 | 80 | 75 | 79.7527 | 323000 | 104000 | 28.2 | 10500 | 4130.0894 |  | 1
105 | 80 | 72 | 68.6171 | 307000 | 135000 | 27.8 | 10500 | 4130.0894 |  | 1
105 | 80 | 67 | 51.5724 | 284000 | 191000 | 27.3 | 10500 | 4130.0894 |  | 1
105 | 80 | 62 | 36.2232 | 259000 | 239000 | 26.9 | 10500 | 4084.2458 |  | 1
105 | 80 | 57 | 22.3618 | 253000 | 253000 | 26.8 | 10500 | 4084.2458 |  | 1
115 | 80 | 75 | 79.7527 | 271000 | 69000 | 30.9 | 6000 | 1208.6034 |  | 1
115 | 80 | 72 | 68.6171 | 254000 | 88000 | 30.6 | 6000 | 1208.6034 |  | 1
115 | 80 | 67 | 51.5724 | 233000 | 124000 | 30.3 | 6000 | 1208.6034 |  | 1
115 | 80 | 62 | 36.2232 | 212000 | 157000 | 30 | 6000 | 1208.6034 |  | 1
115 | 80 | 57 | 22.3618 | 196000 | 187000 | 29.9 | 6000 | 1169.0112 |  | 1
115 | 80 | 75 | 79.7527 | 274000 | 66000 | 31 | 7500 | 1925.4302 |  | 1
115 | 80 | 72 | 68.6171 | 268000 | 99000 | 30.8 | 7500 | 1925.4302 |  | 1
115 | 80 | 67 | 51.5724 | 246000 | 141000 | 30.4 | 7500 | 1925.4302 |  | 1
115 | 80 | 62 | 36.2232 | 223000 | 180000 | 30.1 | 7500 | 1925.4302 |  | 1
115 | 80 | 57 | 22.3618 | 207000 | 207000 | 29.9 | 7500 | 1885.838 |  | 1
115 | 80 | 75 | 79.7527 | 293000 | 81000 | 31.4 | 9000 | 2904.8156 |  | 1
115 | 80 | 72 | 68.6171 | 279000 | 111000 | 31 | 9000 | 2858.9721 |  | 1
115 | 80 | 67 | 51.5724 | 256000 | 159000 | 30.5 | 9000 | 2858.9721 |  | 1
115 | 80 | 62 | 36.2232 | 233000 | 203000 | 30.2 | 9000 | 2858.9721 |  | 1
115 | 80 | 57 | 22.3618 | 224000 | 224000 | 30.1 | 9000 | 2858.9721 |  | 1
115 | 80 | 75 | 79.7527 | 287000 | 73000 | 31.2 | 10500 | 4130.0894 |  | 1
115 | 80 | 72 | 68.6171 | 286000 | 120000 | 31.1 | 10500 | 4130.0894 |  | 1
115 | 80 | 67 | 51.5724 | 262000 | 174000 | 30.6 | 10500 | 4084.2458 |  | 1
115 | 80 | 62 | 36.2232 | 241000 | 220000 | 30.2 | 10500 | 4084.2458 |  | 1
115 | 80 | 57 | 22.3618 | 235000 | 235000 | 30.2 | 10500 | 4084.2458 |  | 1
75 | 80 | 75 | 79.7527 | 395000 | 159000 | 20.8 | 12000 | 5703.3575 |  | 1
75 | 80 | 72 | 68.6171 | 375000 | 192000 | 20.4 | 12000 | 5703.3575 |  | 1
75 | 80 | 67 | 51.5724 | 346000 | 248000 | 19.8 | 12000 | 5607.5028 |  | 1
75 | 80 | 62 | 36.2232 | 320000 | 301000 | 19.3 | 12000 | 5607.5028 |  | 1
75 | 80 | 57 | 22.3618 | 313000 | 313000 | 19.1 | 12000 | 5607.5028 |  | 1
75 | 80 | 75 | 79.7527 | 396000 | 160000 | 20.8 | 13500 | 7528.7654 |  | 1
75 | 80 | 72 | 68.6171 | 381000 | 202000 | 20.5 | 13500 | 7528.7654 |  | 1
75 | 80 | 67 | 51.5724 | 348000 | 260000 | 19.8 | 13500 | 7432.9106 |  | 1
75 | 80 | 62 | 36.2232 | 321000 | 311000 | 19.3 | 13500 | 7432.9106 |  | 1
75 | 80 | 57 | 22.3618 | 322000 | 322000 | 19.3 | 13500 | 7432.9106 |  | 1
75 | 80 | 75 | 79.7527 | 401000 | 166000 | 20.9 | 15000 | 9739.676 |  | 1
75 | 80 | 72 | 68.6171 | 387000 | 211000 | 20.6 | 15000 | 9635.486 |  | 1
75 | 80 | 67 | 51.5724 | 355000 | 277000 | 19.9 | 15000 | 9635.486 |  | 1
75 | 80 | 62 | 36.2232 | 328000 | 324000 | 19.4 | 15000 | 9535.4637 |  | 1
75 | 80 | 57 | 22.3618 | 326000 | 326000 | 19.4 | 15000 | 9535.4637 |  | 1
85 | 80 | 75 | 79.7527 | 369000 | 139000 | 22.9 | 12000 | 5703.3575 |  | 1
85 | 80 | 72 | 68.6171 | 352000 | 174000 | 22.5 | 12000 | 5703.3575 |  | 1
85 | 80 | 67 | 51.5724 | 324000 | 231000 | 21.9 | 12000 | 5607.5028 |  | 1
85 | 80 | 62 | 36.2232 | 298000 | 284000 | 21.4 | 12000 | 5607.5028 |  | 1
85 | 80 | 57 | 22.3618 | 296000 | 296000 | 21.4 | 12000 | 5607.5028 |  | 1
85 | 80 | 75 | 79.7527 | 378000 | 149000 | 23 | 13500 | 7528.7654 |  | 1
85 | 80 | 72 | 68.6171 | 357000 | 183000 | 22.6 | 13500 | 7528.7654 |  | 1
85 | 80 | 67 | 51.5724 | 330000 | 246000 | 22 | 13500 | 7432.9106 |  | 1
85 | 80 | 62 | 36.2232 | 309000 | 300000 | 21.6 | 13500 | 7432.9106 |  | 1
85 | 80 | 57 | 22.3618 | 306000 | 306000 | 21.5 | 13500 | 7432.9106 |  | 1
85 | 80 | 75 | 79.7527 | 379000 | 151000 | 23.1 | 15000 | 9635.486 |  | 1
85 | 80 | 72 | 68.6171 | 362000 | 192000 | 22.7 | 15000 | 9635.486 |  | 1
85 | 80 | 67 | 51.5724 | 334000 | 261000 | 22.1 | 15000 | 9535.4637 |  | 1
85 | 80 | 62 | 36.2232 | 315000 | 314000 | 21.7 | 15000 | 9535.4637 |  | 1
85 | 80 | 57 | 22.3618 | 312000 | 312000 | 21.6 | 15000 | 9535.4637 |  | 1
95 | 80 | 75 | 79.7527 | 350000 | 125000 | 25.4 | 12000 | 5607.5028 |  | 1
95 | 80 | 72 | 68.6171 | 333000 | 159000 | 25 | 12000 | 5607.5028 |  | 1
95 | 80 | 67 | 51.5724 | 307000 | 218000 | 24.5 | 12000 | 5607.5028 |  | 1
95 | 80 | 62 | 36.2232 | 285000 | 270000 | 24 | 12000 | 5607.5028 |  | 1
95 | 80 | 57 | 22.3618 | 280000 | 280000 | 24 | 12000 | 5559.5754 |  | 1
95 | 80 | 75 | 79.7527 | 354000 | 130000 | 25.5 | 13500 | 7528.7654 |  | 1
95 | 80 | 72 | 68.6171 | 338000 | 169000 | 25.1 | 13500 | 7432.9106 |  | 1
95 | 80 | 67 | 51.5724 | 311000 | 233000 | 24.6 | 13500 | 7432.9106 |  | 1
95 | 80 | 62 | 36.2232 | 289000 | 280000 | 24.1 | 13500 | 7432.9106 |  | 1
95 | 80 | 57 | 22.3618 | 286000 | 286000 | 24.1 | 13500 | 7432.9106 |  | 1
95 | 80 | 75 | 79.7527 | 359000 | 137000 | 25.6 | 15000 | 9635.486 |  | 1
95 | 80 | 72 | 68.6171 | 342000 | 178000 | 25.2 | 15000 | 9535.4637 |  | 1
95 | 80 | 67 | 51.5724 | 315000 | 247000 | 24.6 | 15000 | 9535.4637 |  | 1
95 | 80 | 62 | 36.2232 | 294000 | 294000 | 24.2 | 15000 | 9535.4637 |  | 1
95 | 80 | 57 | 22.3618 | 296000 | 296000 | 24.2 | 15000 | 9535.4637 |  | 1
105 | 80 | 75 | 79.7527 | 331000 | 112000 | 28.4 | 12000 | 5607.5028 |  | 1
105 | 80 | 72 | 68.6171 | 315000 | 147000 | 28 | 12000 | 5607.5028 |  | 1
105 | 80 | 67 | 51.5724 | 273000 | 189000 | 27.2 | 12000 | 5559.5754 |  | 1
105 | 80 | 62 | 36.2232 | 266000 | 252000 | 27 | 12000 | 5559.5754 |  | 1
105 | 80 | 57 | 22.3618 | 260000 | 260000 | 26.9 | 12000 | 5559.5754 |  | 1
105 | 80 | 75 | 79.7527 | 337000 | 119000 | 28.5 | 13500 | 7432.9106 |  | 1
105 | 80 | 72 | 68.6171 | 301000 | 137000 | 27.8 | 13500 | 7432.9106 |  | 1
105 | 80 | 67 | 51.5724 | 294000 | 221000 | 27.5 | 13500 | 7432.9106 |  | 1
105 | 80 | 62 | 36.2232 | 274000 | 267000 | 27.1 | 13500 | 7384.9832 |  | 1
105 | 80 | 57 | 22.3618 | 271000 | 271000 | 27.1 | 13500 | 7384.9832 |  | 1
105 | 80 | 75 | 79.7527 | 341000 | 124000 | 28.6 | 15000 | 9535.4637 |  | 1
105 | 80 | 72 | 68.6171 | 321000 | 162000 | 28.1 | 15000 | 9535.4637 |  | 1
105 | 80 | 67 | 51.5724 | 296000 | 233000 | 27.5 | 15000 | 9535.4637 |  | 1
105 | 80 | 62 | 36.2232 | 278000 | 278000 | 27.2 | 15000 | 9485.4525 |  | 1
105 | 80 | 57 | 22.3618 | 277000 | 277000 | 27.2 | 15000 | 9485.4525 |  | 1
115 | 80 | 75 | 79.7527 | 307000 | 94000 | 31.7 | 12000 | 5607.5028 |  | 1
115 | 80 | 72 | 68.6171 | 291000 | 129000 | 31.3 | 12000 | 5607.5028 |  | 1
115 | 80 | 67 | 51.5724 | 268000 | 190000 | 30.7 | 12000 | 5559.5754 |  | 1
115 | 80 | 62 | 36.2232 | 248000 | 235000 | 30.3 | 12000 | 5559.5754 |  | 1
115 | 80 | 57 | 22.3618 | 243000 | 243000 | 30.3 | 12000 | 5559.5754 |  | 1
115 | 80 | 75 | 79.7527 | 311000 | 99000 | 31.8 | 13500 | 7432.9106 |  | 1
115 | 80 | 72 | 68.6171 | 295000 | 138000 | 31.4 | 13500 | 7432.9106 |  | 1
115 | 80 | 67 | 51.5724 | 271000 | 203000 | 30.8 | 13500 | 7384.9832 |  | 1
115 | 80 | 62 | 36.2232 | 254000 | 248000 | 30.4 | 13500 | 7384.9832 |  | 1
115 | 80 | 57 | 22.3618 | 251000 | 251000 | 30.4 | 13500 | 7384.9832 |  | 1
115 | 80 | 75 | 79.7527 | 313000 | 104000 | 31.9 | 15000 | 9535.4637 |  | 1
115 | 80 | 72 | 68.6171 | 299000 | 147000 | 31.4 | 15000 | 9535.4637 |  | 1
115 | 80 | 67 | 51.5724 | 274000 | 217000 | 30.8 | 15000 | 9485.4525 |  | 1
115 | 80 | 62 | 36.2232 | 258000 | 258000 | 30.5 | 15000 | 9485.4525 |  | 1
115 | 80 | 57 | 22.3618 | 258000 | 258000 | 30.5 | 15000 | 9485.4525 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 5
Degradation Coefficient (C_d) |  | 48/50A035 (35 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 413000 | 132000 | 23.6 | 7000 | 2110.8883 |  | 1
75 | 80 | 72 | 68.6171 | 378000 | 145000 | 23 | 7000 | 2006.6983 |  | 1
75 | 80 | 67 | 51.5724 | 346000 | 188000 | 22.8 | 7000 | 1902.5084 |  | 1
75 | 80 | 62 | 36.2232 | 305000 | 220000 | 22.3 | 7000 | 1902.5084 |  | 1
75 | 80 | 57 | 22.3618 | 268000 | 249000 | 22 | 7000 | 1850.4134 |  | 1
75 | 80 | 75 | 79.7527 | 417000 | 125000 | 23.7 | 8750 | 3200.7151 |  | 1
75 | 80 | 72 | 68.6171 | 409000 | 171000 | 23.5 | 8750 | 3200.7151 |  | 1
75 | 80 | 67 | 51.5724 | 369000 | 216000 | 23 | 8750 | 3081.9385 |  | 1
75 | 80 | 62 | 36.2232 | 329000 | 259000 | 22.6 | 8750 | 2961.0782 |  | 1
75 | 80 | 57 | 22.3618 | 286000 | 282000 | 21.7 | 8750 | 2961.0782 |  | 1
75 | 80 | 75 | 79.7527 | 450000 | 153000 | 24.1 | 10500 | 4592.6927 |  | 1
75 | 80 | 72 | 68.6171 | 404000 | 166000 | 23.4 | 10500 | 4592.6927 |  | 1
75 | 80 | 67 | 51.5724 | 385000 | 242000 | 23.2 | 10500 | 4461.4134 |  | 1
75 | 80 | 62 | 36.2232 | 346000 | 294000 | 22.7 | 10500 | 4332.2179 |  | 1
75 | 80 | 57 | 22.3618 | 318000 | 318000 | 22.2 | 10500 | 4332.2179 |  | 1
75 | 80 | 75 | 79.7527 | 460000 | 161000 | 24.3 | 12250 | 6361.838 |  | 1
75 | 80 | 72 | 68.6171 | 433000 | 199000 | 23.9 | 12250 | 6361.838 |  | 1
75 | 80 | 67 | 51.5724 | 389000 | 260000 | 23.2 | 12250 | 6220.1397 |  | 1
75 | 80 | 62 | 36.2232 | 360000 | 327000 | 22.9 | 12250 | 6220.1397 |  | 1
75 | 80 | 57 | 22.3618 | 345000 | 345000 | 22.8 | 12250 | 6074.2737 |  | 1
85 | 80 | 75 | 79.7527 | 373000 | 96000 | 25.9 | 7000 | 2006.6983 |  | 1
85 | 80 | 72 | 68.6171 | 356000 | 126000 | 25.8 | 7000 | 2006.6983 |  | 1
85 | 80 | 67 | 51.5724 | 316000 | 161000 | 25.3 | 7000 | 1902.5084 |  | 1
85 | 80 | 62 | 36.2232 | 277000 | 194000 | 25 | 7000 | 1850.4134 |  | 1
85 | 80 | 57 | 22.3618 | 240000 | 224000 | 24.7 | 7000 | 1850.4134 |  | 1
85 | 80 | 75 | 79.7527 | 397000 | 109000 | 26.3 | 8750 | 3081.9385 |  | 1
85 | 80 | 72 | 68.6171 | 353000 | 119000 | 25.6 | 8750 | 3081.9385 |  | 1
85 | 80 | 67 | 51.5724 | 337000 | 187000 | 25.5 | 8750 | 2961.0782 |  | 1
85 | 80 | 62 | 36.2232 | 288000 | 221000 | 24.7 | 8750 | 2961.0782 |  | 1
85 | 80 | 57 | 22.3618 | 257000 | 254000 | 24.2 | 8750 | 2900.648 |  | 1
85 | 80 | 75 | 79.7527 | 393000 | 101000 | 26.3 | 10500 | 4461.4134 |  | 1
85 | 80 | 72 | 68.6171 | 386000 | 152000 | 26.1 | 10500 | 4461.4134 |  | 1
85 | 80 | 67 | 51.5724 | 351000 | 212000 | 25.7 | 10500 | 4461.4134 |  | 1
85 | 80 | 62 | 36.2232 | 314000 | 265000 | 25.2 | 10500 | 4332.2179 |  | 1
85 | 80 | 57 | 22.3618 | 291000 | 291000 | 24.9 | 10500 | 4332.2179 |  | 1
85 | 80 | 75 | 79.7527 | 402000 | 107000 | 26.5 | 12250 | 6361.838 |  | 1
85 | 80 | 72 | 68.6171 | 377000 | 146000 | 26 | 12250 | 6220.1397 |  | 1
85 | 80 | 67 | 51.5724 | 343000 | 217000 | 25.5 | 12250 | 6074.2737 |  | 1
85 | 80 | 62 | 36.2232 | 327000 | 297000 | 25.4 | 12250 | 6074.2737 |  | 1
85 | 80 | 57 | 22.3618 | 304000 | 304000 | 24.9 | 12250 | 6074.2737 |  | 1
95 | 80 | 75 | 79.7527 | 347000 | 75000 | 29 | 7000 | 1902.5084 |  | 1
95 | 80 | 72 | 68.6171 | 324000 | 98000 | 28.7 | 7000 | 1902.5084 |  | 1
95 | 80 | 67 | 51.5724 | 285000 | 134000 | 28.2 | 7000 | 1902.5084 |  | 1
95 | 80 | 62 | 36.2232 | 246000 | 167000 | 27.9 | 7000 | 1850.4134 |  | 1
95 | 80 | 57 | 22.3618 | 200000 | 184000 | 26.8 | 7000 | 1796.2346 |  | 1
95 | 80 | 75 | 79.7527 | 344000 | 61000 | 28.9 | 8750 | 2961.0782 |  | 1
95 | 80 | 72 | 68.6171 | 320000 | 90000 | 28.5 | 8750 | 2961.0782 |  | 1
95 | 80 | 67 | 51.5724 | 303000 | 158000 | 28.4 | 8750 | 2961.0782 |  | 1
95 | 80 | 62 | 36.2232 | 267000 | 203000 | 28 | 8750 | 2900.648 |  | 1
95 | 80 | 57 | 22.3618 | 222000 | 220000 | 27.2 | 8750 | 2900.648 |  | 1
95 | 80 | 75 | 79.7527 | 355000 | 67000 | 29.1 | 10500 | 4461.4134 |  | 1
95 | 80 | 72 | 68.6171 | 329000 | 100000 | 28.6 | 10500 | 4332.2179 |  | 1
95 | 80 | 67 | 51.5724 | 297000 | 162000 | 28.2 | 10500 | 4332.2179 |  | 1
95 | 80 | 62 | 36.2232 | 280000 | 235000 | 28.1 | 10500 | 4267.6201 |  | 1
95 | 80 | 57 | 22.3618 | 263000 | 263000 | 28 | 10500 | 4267.6201 |  | 1
95 | 80 | 75 | 79.7527 | 361000 | 72000 | 29.3 | 12250 | 6220.1397 |  | 1
95 | 80 | 72 | 68.6171 | 337000 | 112000 | 28.8 | 12250 | 6074.2737 |  | 1
95 | 80 | 67 | 51.5724 | 303000 | 181000 | 28.2 | 12250 | 6074.2737 |  | 1
95 | 80 | 62 | 36.2232 | 292000 | 265000 | 28.2 | 12250 | 6074.2737 |  | 1
95 | 80 | 57 | 22.3618 | 272000 | 272000 | 27.8 | 12250 | 6001.3408 |  | 1
105 | 80 | 75 | 79.7527 | 306000 | 38000 | 32.1 | 7000 | 1902.5084 |  | 1
105 | 80 | 72 | 68.6171 | 281000 | 60000 | 31.7 | 7000 | 1902.5084 |  | 1
105 | 80 | 67 | 51.5724 | 253000 | 106000 | 31.6 | 7000 | 1850.4134 |  | 1
105 | 80 | 62 | 36.2232 | 214000 | 139000 | 31.3 | 7000 | 1850.4134 |  | 1
105 | 80 | 57 | 22.3618 | 182000 | 168000 | 31.2 | 7000 | 1796.2346 |  | 1
105 | 80 | 75 | 79.7527 | 307000 | 30000 | 32.1 | 8750 | 2961.0782 |  | 1
105 | 80 | 72 | 68.6171 | 278000 | 53000 | 31.5 | 8750 | 2900.648 |  | 1
105 | 80 | 67 | 51.5724 | 269000 | 129000 | 31.7 | 8750 | 2900.648 |  | 1
105 | 80 | 62 | 36.2232 | 234000 | 174000 | 31.4 | 8750 | 2900.648 |  | 1
105 | 80 | 57 | 22.3618 | 206000 | 206000 | 31.2 | 8750 | 2842.3017 |  | 1
105 | 80 | 75 | 79.7527 | 314000 | 31000 | 32.3 | 10500 | 4332.2179 |  | 1
105 | 80 | 72 | 68.6171 | 313000 | 89000 | 32.3 | 10500 | 4332.2179 |  | 1
105 | 80 | 67 | 51.5724 | 249000 | 119000 | 31.1 | 10500 | 4267.6201 |  | 1
105 | 80 | 62 | 36.2232 | 247000 | 206000 | 31.5 | 10500 | 4267.6201 |  | 1
105 | 80 | 57 | 22.3618 | 231000 | 231000 | 31.4 | 10500 | 4267.6201 |  | 1
105 | 80 | 75 | 79.7527 | 319000 | 35000 | 32.4 | 12250 | 6074.2737 |  | 1
105 | 80 | 72 | 68.6171 | 296000 | 75000 | 31.9 | 12250 | 6074.2737 |  | 1
105 | 80 | 67 | 51.5724 | 284000 | 167000 | 31.8 | 12250 | 6074.2737 |  | 1
105 | 80 | 62 | 36.2232 | 259000 | 233000 | 31.6 | 12250 | 6001.3408 |  | 1
105 | 80 | 57 | 22.3618 | 250000 | 250000 | 31.5 | 12250 | 6001.3408 |  | 1
115 | 80 | 75 | 79.7527 | 281000 | 20000 | 36.5 | 7000 | 1902.5084 |  | 1
115 | 80 | 72 | 68.6171 | 249000 | 34000 | 35.7 | 7000 | 1850.4134 |  | 1
115 | 80 | 67 | 51.5724 | 221000 | 79000 | 35.7 | 7000 | 1850.4134 |  | 1
115 | 80 | 62 | 36.2232 | 173000 | 102000 | 34.8 | 7000 | 1796.2346 |  | 1
115 | 80 | 57 | 22.3618 | 143000 | 130000 | 34.6 | 7000 | 1796.2346 |  | 1
115 | 80 | 75 | 79.7527 | 291000 | 19000 | 36.5 | 8750 | 2961.0782 |  | 1
115 | 80 | 72 | 68.6171 | 242000 | 23000 | 35.3 | 8750 | 2900.648 |  | 1
115 | 80 | 67 | 51.5724 | 226000 | 91000 | 35.2 | 8750 | 2900.648 |  | 1
115 | 80 | 62 | 36.2232 | 201000 | 146000 | 35.5 | 8750 | 2842.3017 |  | 1
115 | 80 | 57 | 22.3618 | 165000 | 165000 | 34.6 | 8750 | 2842.3017 |  | 1
115 | 80 | 72 | 68.6171 | 251000 | 33000 | 35.4 | 10500 | 4267.6201 |  | 1
115 | 80 | 67 | 51.5724 | 219000 | 95000 | 34.9 | 10500 | 4267.6201 |  | 1
115 | 80 | 62 | 36.2232 | 213000 | 175000 | 35.5 | 10500 | 4267.6201 |  | 1
115 | 80 | 57 | 22.3618 | 172000 | 172000 | 34.4 | 10500 | 4200.9385 |  | 1
115 | 80 | 72 | 68.6171 | 253000 | 39000 | 35.5 | 12250 | 6001.3408 |  | 1
115 | 80 | 67 | 51.5724 | 247000 | 136000 | 35.5 | 12250 | 6001.3408 |  | 1
115 | 80 | 62 | 36.2232 | 223000 | 199000 | 35.4 | 12250 | 6001.3408 |  | 1
115 | 80 | 57 | 22.3618 | 204000 | 204000 | 34.9 | 12250 | 5928.4078 |  | 1
75 | 80 | 75 | 79.7527 | 452000 | 154000 | 24.2 | 14000 | 8485.2291 |  | 1
75 | 80 | 72 | 68.6171 | 443000 | 214000 | 24 | 14000 | 8485.2291 |  | 1
75 | 80 | 67 | 51.5724 | 399000 | 284000 | 23.4 | 14000 | 8331.0279 |  | 1
75 | 80 | 62 | 36.2232 | 372000 | 356000 | 23.1 | 14000 | 8331.0279 |  | 1
75 | 80 | 57 | 22.3618 | 365000 | 365000 | 23 | 14000 | 8331.0279 |  | 1
75 | 80 | 75 | 79.7527 | 460000 | 163000 | 24.4 | 15750 | 11035.7989 |  | 1
75 | 80 | 72 | 68.6171 | 434000 | 213000 | 24 | 15750 | 11035.7989 |  | 1
75 | 80 | 67 | 51.5724 | 410000 | 311000 | 23.5 | 15750 | 11035.7989 |  | 1
75 | 80 | 62 | 36.2232 | 383000 | 379000 | 23.2 | 15750 | 10869.095 |  | 1
75 | 80 | 57 | 22.3618 | 381000 | 381000 | 23.2 | 15750 | 10869.095 |  | 1
75 | 80 | 75 | 79.7527 | 465000 | 171000 | 24.5 | 17500 | 13990.6257 |  | 1
75 | 80 | 72 | 68.6171 | 438000 | 225000 | 24.1 | 17500 | 13990.6257 |  | 1
75 | 80 | 67 | 51.5724 | 414000 | 330000 | 23.6 | 17500 | 13990.6257 |  | 1
75 | 80 | 62 | 36.2232 | 384000 | 384000 | 23.1 | 17500 | 13813.5028 |  | 1
75 | 80 | 57 | 22.3618 | 394000 | 394000 | 23.4 | 17500 | 13813.5028 |  | 1
85 | 80 | 75 | 79.7527 | 409000 | 115000 | 26.6 | 14000 | 8485.2291 |  | 1
85 | 80 | 72 | 68.6171 | 384000 | 159000 | 26.2 | 14000 | 8331.0279 |  | 1
85 | 80 | 67 | 51.5724 | 351000 | 240000 | 25.7 | 14000 | 8331.0279 |  | 1
85 | 80 | 62 | 36.2232 | 338000 | 323000 | 25.5 | 14000 | 8172.6592 |  | 1
85 | 80 | 57 | 22.3618 | 333000 | 333000 | 25.5 | 14000 | 8172.6592 |  | 1
85 | 80 | 75 | 79.7527 | 415000 | 123000 | 26.8 | 15750 | 11035.7989 |  | 1
85 | 80 | 72 | 68.6171 | 391000 | 175000 | 26.3 | 15750 | 10869.095 |  | 1
85 | 80 | 67 | 51.5724 | 371000 | 276000 | 25.9 | 15750 | 10869.095 |  | 1
85 | 80 | 62 | 36.2232 | 349000 | 345000 | 25.7 | 15750 | 10702.3911 |  | 1
85 | 80 | 57 | 22.3618 | 337000 | 337000 | 25.4 | 15750 | 10702.3911 |  | 1
85 | 80 | 75 | 79.7527 | 420000 | 131000 | 26.9 | 17500 | 13990.6257 |  | 1
85 | 80 | 72 | 68.6171 | 394000 | 185000 | 26.4 | 17500 | 13813.5028 |  | 1
85 | 80 | 67 | 51.5724 | 378000 | 299000 | 26.1 | 17500 | 13813.5028 |  | 1
85 | 80 | 62 | 36.2232 | 350000 | 350000 | 25.6 | 17500 | 13634.2961 |  | 1
85 | 80 | 57 | 22.3618 | 358000 | 358000 | 25.9 | 17500 | 13813.5028 |  | 1
95 | 80 | 75 | 79.7527 | 367000 | 78000 | 29.4 | 14000 | 8331.0279 |  | 1
95 | 80 | 72 | 68.6171 | 342000 | 122000 | 28.9 | 14000 | 8172.6592 |  | 1
95 | 80 | 67 | 51.5724 | 299000 | 193000 | 28.1 | 14000 | 8172.6592 |  | 1
95 | 80 | 62 | 36.2232 | 304000 | 290000 | 28.4 | 14000 | 8172.6592 |  | 1
95 | 80 | 57 | 22.3618 | 299000 | 299000 | 28.3 | 14000 | 8172.6592 |  | 1
95 | 80 | 75 | 79.7527 | 371000 | 84000 | 29.5 | 15750 | 10869.095 |  | 1
95 | 80 | 72 | 68.6171 | 347000 | 135000 | 29 | 15750 | 10702.3911 |  | 1
95 | 80 | 67 | 51.5724 | 313000 | 221000 | 28.4 | 15750 | 10702.3911 |  | 1
95 | 80 | 62 | 36.2232 | 304000 | 301000 | 28.3 | 15750 | 10702.3911 |  | 1
95 | 80 | 57 | 22.3618 | 303000 | 303000 | 28.2 | 15750 | 10702.3911 |  | 1
95 | 80 | 75 | 79.7527 | 374000 | 91000 | 29.6 | 17500 | 13813.5028 |  | 1
95 | 80 | 72 | 68.6171 | 351000 | 147000 | 29.1 | 17500 | 13813.5028 |  | 1
95 | 80 | 67 | 51.5724 | 318000 | 242000 | 28.5 | 17500 | 13634.2961 |  | 1
95 | 80 | 62 | 36.2232 | 316000 | 316000 | 28.4 | 17500 | 13634.2961 |  | 1
95 | 80 | 57 | 22.3618 | 323000 | 323000 | 28.6 | 17500 | 13634.2961 |  | 1
105 | 80 | 75 | 79.7527 | 320000 | 37000 | 32.5 | 14000 | 8172.6592 |  | 1
105 | 80 | 72 | 68.6171 | 299000 | 85000 | 32 | 14000 | 8172.6592 |  | 1
105 | 80 | 67 | 51.5724 | 291000 | 189000 | 31.9 | 14000 | 8172.6592 |  | 1
105 | 80 | 62 | 36.2232 | 260000 | 247000 | 31.4 | 14000 | 8093.4749 |  | 1
105 | 80 | 57 | 22.3618 | 254000 | 254000 | 31.3 | 14000 | 8093.4749 |  | 1
105 | 80 | 75 | 79.7527 | 325000 | 44000 | 32.7 | 15750 | 10702.3911 |  | 1
105 | 80 | 72 | 68.6171 | 302000 | 95000 | 32 | 15750 | 10702.3911 |  | 1
105 | 80 | 67 | 51.5724 | 268000 | 182000 | 31.4 | 15750 | 10619.0391 |  | 1
105 | 80 | 62 | 36.2232 | 278000 | 276000 | 31.8 | 15750 | 10619.0391 |  | 1
105 | 80 | 57 | 22.3618 | 275000 | 275000 | 31.7 | 15750 | 10619.0391 |  | 1
105 | 80 | 75 | 79.7527 | 328000 | 50000 | 32.8 | 17500 | 13634.2961 |  | 1
105 | 80 | 72 | 68.6171 | 305000 | 107000 | 32.1 | 17500 | 13634.2961 |  | 1
105 | 80 | 67 | 51.5724 | 262000 | 191000 | 31.3 | 17500 | 13544.6927 |  | 1
105 | 80 | 62 | 36.2232 | 287000 | 287000 | 31.9 | 17500 | 13634.2961 |  | 1
105 | 80 | 57 | 22.3618 | 281000 | 281000 | 31.7 | 17500 | 13634.2961 |  | 1
115 | 80 | 72 | 68.6171 | 256000 | 48000 | 35.5 | 14000 | 8093.4749 |  | 1
115 | 80 | 67 | 51.5724 | 227000 | 130000 | 34.9 | 14000 | 8093.4749 |  | 1
115 | 80 | 62 | 36.2232 | 234000 | 222000 | 35.5 | 14000 | 8093.4749 |  | 1
115 | 80 | 57 | 22.3618 | 229000 | 229000 | 35.5 | 14000 | 8093.4749 |  | 1
115 | 80 | 75 | 79.7527 | 279000 | 4000 | 36.4 | 15750 | 10619.0391 |  | 1
115 | 80 | 72 | 68.6171 | 257000 | 57000 | 35.6 | 15750 | 10619.0391 |  | 1
115 | 80 | 67 | 51.5724 | 268000 | 188000 | 36.1 | 15750 | 10619.0391 |  | 1
115 | 80 | 62 | 36.2232 | 238000 | 238000 | 35.5 | 15750 | 10619.0391 |  | 1
115 | 80 | 57 | 22.3618 | 240000 | 240000 | 35.5 | 15750 | 10619.0391 |  | 1
115 | 80 | 75 | 79.7527 | 278000 | 7000 | 36.5 | 17500 | 13544.6927 |  | 1
115 | 80 | 72 | 68.6171 | 256000 | 64000 | 35.6 | 17500 | 13544.6927 |  | 1
115 | 80 | 67 | 51.5724 | 270000 | 205000 | 36 | 17500 | 13544.6927 |  | 1
115 | 80 | 62 | 36.2232 | 243000 | 243000 | 35.4 | 17500 | 13544.6927 |  | 1
115 | 80 | 57 | 22.3618 | 249000 | 249000 | 35.6 | 17500 | 13544.6927 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 6
Degradation Coefficient (C_d) |  | 48/50A040 (40 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 501000 | 189000 | 26.5 | 8000 | 3136.1173 |  | 1
75 | 80 | 72 | 68.6171 | 473000 | 214000 | 26.1 | 8000 | 2973.581 |  | 1
75 | 80 | 67 | 51.5724 | 429000 | 253000 | 25.7 | 8000 | 2973.581 |  | 1
75 | 80 | 62 | 36.2232 | 379000 | 281000 | 24.9 | 8000 | 2811.0447 |  | 1
75 | 80 | 57 | 22.3618 | 352000 | 327000 | 25 | 8000 | 2811.0447 |  | 1
75 | 80 | 75 | 79.7527 | 528000 | 202000 | 26.8 | 10000 | 4776.067 |  | 1
75 | 80 | 72 | 68.6171 | 499000 | 231000 | 26.4 | 10000 | 4592.6927 |  | 1
75 | 80 | 67 | 51.5724 | 455000 | 281000 | 25.9 | 10000 | 4592.6927 |  | 1
75 | 80 | 62 | 36.2232 | 403000 | 319000 | 25.2 | 10000 | 4592.6927 |  | 1
75 | 80 | 57 | 22.3618 | 374000 | 368000 | 25.1 | 10000 | 4409.3184 |  | 1
75 | 80 | 75 | 79.7527 | 549000 | 214000 | 27.1 | 12000 | 6957.8045 |  | 1
75 | 80 | 72 | 68.6171 | 519000 | 249000 | 26.7 | 12000 | 6957.8045 |  | 1
75 | 80 | 67 | 51.5724 | 474000 | 307000 | 26.2 | 12000 | 6753.5922 |  | 1
75 | 80 | 62 | 36.2232 | 420000 | 352000 | 25.4 | 12000 | 6753.5922 |  | 1
75 | 80 | 57 | 22.3618 | 387000 | 387000 | 25 | 12000 | 6549.3799 |  | 1
75 | 80 | 75 | 79.7527 | 562000 | 224000 | 27.3 | 14000 | 9741.7598 |  | 1
75 | 80 | 72 | 68.6171 | 534000 | 265000 | 26.9 | 14000 | 9741.7598 |  | 1
75 | 80 | 67 | 51.5724 | 488000 | 331000 | 26.3 | 14000 | 9520.8771 |  | 1
75 | 80 | 62 | 36.2232 | 446000 | 395000 | 26 | 14000 | 9520.8771 |  | 1
75 | 80 | 57 | 22.3618 | 408000 | 408000 | 25.3 | 14000 | 9520.8771 |  | 1
85 | 80 | 75 | 79.7527 | 478000 | 172000 | 29.4 | 8000 | 2973.581 |  | 1
85 | 80 | 72 | 68.6171 | 444000 | 190000 | 28.9 | 8000 | 2973.581 |  | 1
85 | 80 | 67 | 51.5724 | 410000 | 239000 | 28.9 | 8000 | 2973.581 |  | 1
85 | 80 | 62 | 36.2232 | 369000 | 276000 | 28.4 | 8000 | 2811.0447 |  | 1
85 | 80 | 57 | 22.3618 | 330000 | 309000 | 27.9 | 8000 | 2648.5084 |  | 1
85 | 80 | 75 | 79.7527 | 497000 | 177000 | 29.5 | 10000 | 4592.6927 |  | 1
85 | 80 | 72 | 68.6171 | 477000 | 215000 | 29.4 | 10000 | 4592.6927 |  | 1
85 | 80 | 67 | 51.5724 | 422000 | 253000 | 28.6 | 10000 | 4592.6927 |  | 1
85 | 80 | 62 | 36.2232 | 382000 | 302000 | 28.2 | 10000 | 4409.3184 |  | 1
85 | 80 | 57 | 22.3618 | 344000 | 338000 | 27.9 | 10000 | 4225.9441 |  | 1
85 | 80 | 75 | 79.7527 | 523000 | 195000 | 30 | 12000 | 6957.8045 |  | 1
85 | 80 | 72 | 68.6171 | 492000 | 229000 | 29.6 | 12000 | 6753.5922 |  | 1
85 | 80 | 67 | 51.5724 | 440000 | 279000 | 28.9 | 12000 | 6753.5922 |  | 1
85 | 80 | 62 | 36.2232 | 397000 | 334000 | 28.4 | 12000 | 6549.3799 |  | 1
85 | 80 | 57 | 22.3618 | 363000 | 363000 | 28.1 | 12000 | 6549.3799 |  | 1
85 | 80 | 75 | 79.7527 | 527000 | 196000 | 30.1 | 14000 | 9741.7598 |  | 1
85 | 80 | 72 | 68.6171 | 498000 | 236000 | 29.7 | 14000 | 9520.8771 |  | 1
85 | 80 | 67 | 51.5724 | 462000 | 311000 | 29.2 | 14000 | 9520.8771 |  | 1
85 | 80 | 62 | 36.2232 | 424000 | 378000 | 29.1 | 14000 | 9520.8771 |  | 1
85 | 80 | 57 | 22.3618 | 383000 | 383000 | 28.2 | 14000 | 9299.9944 |  | 1
95 | 80 | 75 | 79.7527 | 442000 | 142000 | 32.6 | 8000 | 2973.581 |  | 1
95 | 80 | 72 | 68.6171 | 416000 | 168000 | 32.3 | 8000 | 2973.581 |  | 1
95 | 80 | 67 | 51.5724 | 375000 | 209000 | 31.9 | 8000 | 2811.0447 |  | 1
95 | 80 | 62 | 36.2232 | 348000 | 259000 | 31.9 | 8000 | 2648.5084 |  | 1
95 | 80 | 57 | 22.3618 | 310000 | 292000 | 31.6 | 8000 | 2648.5084 |  | 1
95 | 80 | 75 | 79.7527 | 476000 | 164000 | 33.1 | 10000 | 4592.6927 |  | 1
95 | 80 | 72 | 68.6171 | 451000 | 196000 | 32.9 | 10000 | 4592.6927 |  | 1
95 | 80 | 67 | 51.5724 | 398000 | 235000 | 32.1 | 10000 | 4409.3184 |  | 1
95 | 80 | 62 | 36.2232 | 358000 | 284000 | 31.7 | 10000 | 4409.3184 |  | 1
95 | 80 | 57 | 22.3618 | 332000 | 326000 | 31.7 | 10000 | 4225.9441 |  | 1
95 | 80 | 75 | 79.7527 | 484000 | 164000 | 33.1 | 12000 | 6753.5922 |  | 1
95 | 80 | 72 | 68.6171 | 457000 | 201000 | 32.8 | 12000 | 6753.5922 |  | 1
95 | 80 | 67 | 51.5724 | 426000 | 271000 | 32.6 | 12000 | 6753.5922 |  | 1
95 | 80 | 62 | 36.2232 | 386000 | 328000 | 32.3 | 12000 | 6549.3799 |  | 1
95 | 80 | 57 | 22.3618 | 344000 | 344000 | 31.7 | 12000 | 6345.1676 |  | 1
95 | 80 | 75 | 79.7527 | 506000 | 184000 | 33.5 | 14000 | 9741.7598 |  | 1
95 | 80 | 72 | 68.6171 | 480000 | 226000 | 33.2 | 14000 | 9520.8771 |  | 1
95 | 80 | 67 | 51.5724 | 437000 | 293000 | 32.7 | 14000 | 9520.8771 |  | 1
95 | 80 | 62 | 36.2232 | 395000 | 354000 | 32.3 | 14000 | 9299.9944 |  | 1
95 | 80 | 57 | 22.3618 | 363000 | 363000 | 31.8 | 14000 | 9299.9944 |  | 1
105 | 80 | 75 | 79.7527 | 415000 | 122000 | 36.6 | 8000 | 2973.581 |  | 1
105 | 80 | 72 | 68.6171 | 402000 | 160000 | 36.7 | 8000 | 2973.581 |  | 1
105 | 80 | 67 | 51.5724 | 363000 | 203000 | 36.4 | 8000 | 2811.0447 |  | 1
105 | 80 | 62 | 36.2232 | 314000 | 231000 | 35.9 | 8000 | 2648.5084 |  | 1
105 | 80 | 57 | 22.3618 | 288000 | 275000 | 35.9 | 8000 | 2648.5084 |  | 1
105 | 80 | 75 | 79.7527 | 438000 | 133000 | 36.8 | 10000 | 4592.6927 |  | 1
105 | 80 | 72 | 68.6171 | 413000 | 165000 | 36.6 | 10000 | 4592.6927 |  | 1
105 | 80 | 67 | 51.5724 | 384000 | 227000 | 36.5 | 10000 | 4409.3184 |  | 1
105 | 80 | 62 | 36.2232 | 347000 | 278000 | 36.4 | 10000 | 4225.9441 |  | 1
105 | 80 | 57 | 22.3618 | 316000 | 311000 | 36.2 | 10000 | 4225.9441 |  | 1
105 | 80 | 75 | 79.7527 | 464000 | 153000 | 37.2 | 12000 | 6753.5922 |  | 1
105 | 80 | 72 | 68.6171 | 439000 | 190000 | 37 | 12000 | 6753.5922 |  | 1
105 | 80 | 67 | 51.5724 | 400000 | 252000 | 36.7 | 12000 | 6549.3799 |  | 1
105 | 80 | 62 | 36.2232 | 361000 | 309000 | 36.4 | 12000 | 6549.3799 |  | 1
105 | 80 | 57 | 22.3618 | 325000 | 325000 | 36 | 12000 | 6345.1676 |  | 1
105 | 80 | 75 | 79.7527 | 467000 | 153000 | 37.2 | 14000 | 9520.8771 |  | 1
105 | 80 | 72 | 68.6171 | 449000 | 202000 | 37.1 | 14000 | 9520.8771 |  | 1
105 | 80 | 67 | 51.5724 | 410000 | 274000 | 36.8 | 14000 | 9520.8771 |  | 1
105 | 80 | 62 | 36.2232 | 374000 | 338000 | 36.5 | 14000 | 9299.9944 |  | 1
105 | 80 | 57 | 22.3618 | 342000 | 342000 | 36.1 | 14000 | 9079.1117 |  | 1
115 | 80 | 75 | 79.7527 | 388000 | 103000 | 41.2 | 8000 | 2811.0447 |  | 1
115 | 80 | 72 | 68.6171 | 376000 | 141000 | 41.5 | 8000 | 2811.0447 |  | 1
115 | 80 | 67 | 51.5724 | 339000 | 184000 | 41.4 | 8000 | 2648.5084 |  | 1
115 | 80 | 62 | 36.2232 | 304000 | 226000 | 41.4 | 8000 | 2648.5084 |  | 1
115 | 80 | 57 | 22.3618 | 273000 | 260000 | 41.5 | 8000 | 2567.2402 |  | 1
115 | 80 | 75 | 79.7527 | 410000 | 113000 | 41.4 | 10000 | 4592.6927 |  | 1
115 | 80 | 72 | 68.6171 | 394000 | 154000 | 41.5 | 10000 | 4409.3184 |  | 1
115 | 80 | 67 | 51.5724 | 356000 | 207000 | 41.4 | 10000 | 4409.3184 |  | 1
115 | 80 | 62 | 36.2232 | 311000 | 247000 | 40.9 | 10000 | 4225.9441 |  | 1
115 | 80 | 57 | 22.3618 | 295000 | 291000 | 41.3 | 10000 | 4225.9441 |  | 1
115 | 80 | 75 | 79.7527 | 433000 | 130000 | 41.8 | 12000 | 6753.5922 |  | 1
115 | 80 | 72 | 68.6171 | 410000 | 169000 | 41.6 | 12000 | 6753.5922 |  | 1
115 | 80 | 67 | 51.5724 | 371000 | 231000 | 41.4 | 12000 | 6549.3799 |  | 1
115 | 80 | 62 | 36.2232 | 324000 | 277000 | 41 | 12000 | 6345.1676 |  | 1
115 | 80 | 57 | 22.3618 | 303000 | 303000 | 40.9 | 12000 | 6345.1676 |  | 1
115 | 80 | 75 | 79.7527 | 445000 | 140000 | 41.9 | 14000 | 9520.8771 |  | 1
115 | 80 | 72 | 68.6171 | 421000 | 183000 | 41.7 | 14000 | 9520.8771 |  | 1
115 | 80 | 67 | 51.5724 | 383000 | 254000 | 41.6 | 14000 | 9299.9944 |  | 1
115 | 80 | 62 | 36.2232 | 334000 | 303000 | 41 | 14000 | 9079.1117 |  | 1
115 | 80 | 57 | 22.3618 | 330000 | 330000 | 41.4 | 14000 | 9079.1117 |  | 1
75 | 80 | 75 | 79.7527 | 568000 | 228000 | 27.4 | 16000 | 13192.5307 |  | 1
75 | 80 | 72 | 68.6171 | 537000 | 272000 | 26.9 | 16000 | 13192.5307 |  | 1
75 | 80 | 67 | 51.5724 | 490000 | 345000 | 26.3 | 16000 | 12954.9777 |  | 1
75 | 80 | 62 | 36.2232 | 445000 | 410000 | 25.7 | 16000 | 12954.9777 |  | 1
75 | 80 | 57 | 22.3618 | 416000 | 416000 | 25.4 | 16000 | 12954.9777 |  | 1
75 | 80 | 75 | 79.7527 | 583000 | 243000 | 27.6 | 18000 | 17360.1285 |  | 1
75 | 80 | 72 | 68.6171 | 553000 | 293000 | 27.2 | 18000 | 17360.1285 |  | 1
75 | 80 | 67 | 51.5724 | 509000 | 377000 | 26.6 | 18000 | 17360.1285 |  | 1
75 | 80 | 62 | 36.2232 | 465000 | 445000 | 26.1 | 18000 | 17105.905 |  | 1
75 | 80 | 57 | 22.3618 | 452000 | 452000 | 25.9 | 18000 | 17105.905 |  | 1
75 | 80 | 75 | 79.7527 | 591000 | 252000 | 27.7 | 20000 | 22313.3184 |  | 1
75 | 80 | 72 | 68.6171 | 554000 | 300000 | 27.2 | 20000 | 22313.3184 |  | 1
75 | 80 | 67 | 51.5724 | 516000 | 400000 | 26.8 | 20000 | 22313.3184 |  | 1
75 | 80 | 62 | 36.2232 | 469000 | 465000 | 26 | 20000 | 22046.5922 |  | 1
75 | 80 | 57 | 22.3618 | 464000 | 464000 | 26 | 20000 | 22046.5922 |  | 1
85 | 80 | 75 | 79.7527 | 539000 | 206000 | 30.2 | 16000 | 13192.5307 |  | 1
85 | 80 | 72 | 68.6171 | 509000 | 251000 | 29.8 | 16000 | 13192.5307 |  | 1
85 | 80 | 67 | 51.5724 | 463000 | 325000 | 29.2 | 16000 | 12954.9777 |  | 1
85 | 80 | 62 | 36.2232 | 421000 | 391000 | 28.7 | 16000 | 12954.9777 |  | 1
85 | 80 | 57 | 22.3618 | 405000 | 405000 | 28.5 | 16000 | 12954.9777 |  | 1
85 | 80 | 75 | 79.7527 | 553000 | 222000 | 30.5 | 18000 | 17360.1285 |  | 1
85 | 80 | 72 | 68.6171 | 519000 | 266000 | 29.9 | 18000 | 17360.1285 |  | 1
85 | 80 | 67 | 51.5724 | 469000 | 345000 | 29.2 | 18000 | 17105.905 |  | 1
85 | 80 | 62 | 36.2232 | 439000 | 422000 | 29.2 | 18000 | 17105.905 |  | 1
85 | 80 | 57 | 22.3618 | 433000 | 433000 | 29.1 | 18000 | 17105.905 |  | 1
85 | 80 | 75 | 79.7527 | 561000 | 231000 | 30.6 | 20000 | 22313.3184 |  | 1
85 | 80 | 72 | 68.6171 | 531000 | 285000 | 30.1 | 20000 | 22313.3184 |  | 1
85 | 80 | 67 | 51.5724 | 478000 | 368000 | 29.4 | 20000 | 22046.5922 |  | 1
85 | 80 | 62 | 36.2232 | 46000 | 45000 | 29.2 | 20000 | 20854.6592 |  | 1
85 | 80 | 57 | 22.3618 | 444000 | 444000 | 29.2 | 20000 | 22046.5922 |  | 1
95 | 80 | 75 | 79.7527 | 515000 | 192000 | 33.6 | 16000 | 13192.5307 |  | 1
95 | 80 | 72 | 68.6171 | 489000 | 239000 | 33.3 | 16000 | 12954.9777 |  | 1
95 | 80 | 67 | 51.5724 | 448000 | 317000 | 32.9 | 16000 | 12954.9777 |  | 1
95 | 80 | 62 | 36.2232 | 409000 | 384000 | 32.6 | 16000 | 12954.9777 |  | 1
95 | 80 | 57 | 22.3618 | 394000 | 394000 | 32.4 | 16000 | 12717.4246 |  | 1
95 | 80 | 75 | 79.7527 | 517000 | 194000 | 33.7 | 18000 | 17360.1285 |  | 1
95 | 80 | 72 | 68.6171 | 488000 | 244000 | 33.2 | 18000 | 17105.905 |  | 1
95 | 80 | 67 | 51.5724 | 455000 | 338000 | 32.9 | 18000 | 17105.905 |  | 1
95 | 80 | 62 | 36.2232 | 404000 | 394000 | 32.2 | 18000 | 17105.905 |  | 1
95 | 80 | 57 | 22.3618 | 409000 | 409000 | 32.5 | 18000 | 17105.905 |  | 1
95 | 80 | 75 | 79.7527 | 525000 | 204000 | 33.8 | 20000 | 22313.3184 |  | 1
95 | 80 | 72 | 68.6171 | 495000 | 257000 | 33.3 | 20000 | 22046.5922 |  | 1
95 | 80 | 67 | 51.5724 | 449000 | 347000 | 32.7 | 20000 | 22046.5922 |  | 1
95 | 80 | 62 | 36.2232 | 424000 | 423000 | 32.7 | 20000 | 22046.5922 |  | 1
95 | 80 | 57 | 22.3618 | 425000 | 425000 | 32.9 | 20000 | 22046.5922 |  | 1
105 | 80 | 75 | 79.7527 | 484000 | 169000 | 37.5 | 16000 | 12954.9777 |  | 1
105 | 80 | 72 | 68.6171 | 460000 | 218000 | 37.2 | 16000 | 12954.9777 |  | 1
105 | 80 | 67 | 51.5724 | 420000 | 297000 | 36.9 | 16000 | 12954.9777 |  | 1
105 | 80 | 62 | 36.2232 | 369000 | 351000 | 36.2 | 16000 | 12717.4246 |  | 1
105 | 80 | 57 | 22.3618 | 359000 | 359000 | 36.1 | 16000 | 12717.4246 |  | 1
105 | 80 | 75 | 79.7527 | 488000 | 175000 | 37.5 | 18000 | 17105.905 |  | 1
105 | 80 | 72 | 68.6171 | 464000 | 229000 | 37.2 | 18000 | 17105.905 |  | 1
105 | 80 | 67 | 51.5724 | 426000 | 318000 | 37 | 18000 | 17105.905 |  | 1
105 | 80 | 62 | 36.2232 | 384000 | 374000 | 36.4 | 18000 | 16853.7654 |  | 1
105 | 80 | 57 | 22.3618 | 385000 | 385000 | 36.6 | 18000 | 16853.7654 |  | 1
105 | 80 | 75 | 79.7527 | 491000 | 179000 | 37.5 | 20000 | 22046.5922 |  | 1
105 | 80 | 72 | 68.6171 | 471000 | 243000 | 37.3 | 20000 | 22046.5922 |  | 1
105 | 80 | 67 | 51.5724 | 431000 | 337000 | 37 | 20000 | 22046.5922 |  | 1
105 | 80 | 62 | 36.2232 | 399000 | 399000 | 36.8 | 20000 | 21779.8659 |  | 1
105 | 80 | 57 | 22.3618 | 396000 | 396000 | 36.7 | 20000 | 21779.8659 |  | 1
115 | 80 | 75 | 79.7527 | 445000 | 139000 | 41.8 | 16000 | 12954.9777 |  | 1
115 | 80 | 72 | 68.6171 | 429000 | 195000 | 41.8 | 16000 | 12954.9777 |  | 1
115 | 80 | 67 | 51.5724 | 390000 | 275000 | 41.6 | 16000 | 12717.4246 |  | 1
115 | 80 | 62 | 36.2232 | 357000 | 339000 | 41.5 | 16000 | 12717.4246 |  | 1
115 | 80 | 57 | 22.3618 | 335000 | 335000 | 40.9 | 16000 | 12479.8715 |  | 1
115 | 80 | 75 | 79.7527 | 458000 | 153000 | 42 | 18000 | 17105.905 |  | 1
115 | 80 | 72 | 68.6171 | 435000 | 208000 | 41.8 | 18000 | 17105.905 |  | 1
115 | 80 | 67 | 51.5724 | 397000 | 296000 | 41.6 | 18000 | 16853.7654 |  | 1
115 | 80 | 62 | 36.2232 | 365000 | 356000 | 41.5 | 18000 | 16853.7654 |  | 1
115 | 80 | 57 | 22.3618 | 355000 | 355000 | 41.4 | 18000 | 16853.7654 |  | 1
115 | 80 | 75 | 79.7527 | 464000 | 161000 | 42.1 | 20000 | 22046.5922 |  | 1
115 | 80 | 72 | 68.6171 | 432000 | 212000 | 41.7 | 20000 | 22046.5922 |  | 1
115 | 80 | 67 | 51.5724 | 401000 | 314000 | 41.7 | 20000 | 22046.5922 |  | 1
115 | 80 | 62 | 36.2232 | 375000 | 375000 | 41.6 | 20000 | 21779.8659 |  | 1
115 | 80 | 57 | 22.3618 | 366000 | 366000 | 41.4 | 20000 | 21779.8659 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 7
Degradation Coefficient (C_d) |  | 48/50A050 (50 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 601000 | 218000 | 31.4 | 10000 | 4865.6704 |  | 1
75 | 80 | 72 | 68.6171 | 568000 | 251000 | 30.8 | 10000 | 4865.6704 |  | 1
75 | 80 | 67 | 51.5724 | 523000 | 311000 | 30.1 | 10000 | 4865.6704 |  | 1
75 | 80 | 62 | 36.2232 | 479000 | 367000 | 29.5 | 10000 | 4678.1285 |  | 1
75 | 80 | 57 | 22.3618 | 438000 | 418000 | 28.9 | 10000 | 4678.1285 |  | 1
75 | 80 | 75 | 79.7527 | 624000 | 229000 | 31.9 | 12500 | 7745.4804 |  | 1
75 | 80 | 72 | 68.6171 | 596000 | 274000 | 31.4 | 12500 | 7745.4804 |  | 1
75 | 80 | 67 | 51.5724 | 547000 | 342000 | 30.5 | 12500 | 7745.4804 |  | 1
75 | 80 | 62 | 36.2232 | 507000 | 416000 | 29.9 | 12500 | 7745.4804 |  | 1
75 | 80 | 57 | 22.3618 | 471000 | 468000 | 29.4 | 12500 | 7532.933 |  | 1
75 | 80 | 75 | 79.7527 | 643000 | 241000 | 32.5 | 15000 | 11563 |  | 1
75 | 80 | 72 | 68.6171 | 608000 | 287000 | 31.8 | 15000 | 11563 |  | 1
75 | 80 | 67 | 51.5724 | 567000 | 377000 | 30.9 | 15000 | 11563 |  | 1
75 | 80 | 62 | 36.2232 | 521000 | 455000 | 30.1 | 15000 | 11563 |  | 1
75 | 80 | 57 | 22.3618 | 494000 | 494000 | 29.7 | 15000 | 11333.7821 |  | 1
75 | 80 | 75 | 79.7527 | 651000 | 247000 | 32.6 | 17500 | 16528.6927 |  | 1
75 | 80 | 72 | 68.6171 | 604000 | 289000 | 31.7 | 17500 | 16528.6927 |  | 1
75 | 80 | 67 | 51.5724 | 582000 | 410000 | 31.2 | 17500 | 16528.6927 |  | 1
75 | 80 | 62 | 36.2232 | 542000 | 501000 | 30.4 | 17500 | 16528.6927 |  | 1
75 | 80 | 57 | 22.3618 | 524000 | 524000 | 30.1 | 17500 | 16528.6927 |  | 1
85 | 80 | 75 | 79.7527 | 567000 | 192000 | 34.6 | 10000 | 4865.6704 |  | 1
85 | 80 | 72 | 68.6171 | 541000 | 230000 | 34.2 | 10000 | 4865.6704 |  | 1
85 | 80 | 67 | 51.5724 | 498000 | 291000 | 33.5 | 10000 | 4678.1285 |  | 1
85 | 80 | 62 | 36.2232 | 455000 | 348000 | 32.8 | 10000 | 4678.1285 |  | 1
85 | 80 | 57 | 22.3618 | 417000 | 399000 | 32.3 | 10000 | 4678.1285 |  | 1
85 | 80 | 75 | 79.7527 | 596000 | 209000 | 35.2 | 12500 | 7745.4804 |  | 1
85 | 80 | 72 | 68.6171 | 570000 | 254000 | 34.7 | 12500 | 7745.4804 |  | 1
85 | 80 | 67 | 51.5724 | 522000 | 324000 | 33.9 | 12500 | 7745.4804 |  | 1
85 | 80 | 62 | 36.2232 | 481000 | 396000 | 33.2 | 12500 | 7532.933 |  | 1
85 | 80 | 57 | 22.3618 | 449000 | 446000 | 32.8 | 12500 | 7532.933 |  | 1
85 | 80 | 75 | 79.7527 | 620000 | 429000 | 35.8 | 15000 | 11563 |  | 1
85 | 80 | 72 | 68.6171 | 586000 | 272000 | 35 | 15000 | 11563 |  | 1
85 | 80 | 67 | 51.5724 | 540000 | 356000 | 34.2 | 15000 | 11563 |  | 1
85 | 80 | 62 | 36.2232 | 495000 | 434000 | 33.4 | 15000 | 11333.7821 |  | 1
85 | 80 | 57 | 22.3618 | 472000 | 472000 | 33.1 | 15000 | 11333.7821 |  | 1
85 | 80 | 75 | 79.7527 | 610000 | 428000 | 35.6 | 17500 | 16528.6927 |  | 1
85 | 80 | 72 | 68.6171 | 599000 | 426000 | 35.5 | 17500 | 16528.6927 |  | 1
85 | 80 | 67 | 51.5724 | 554000 | 414000 | 34.5 | 17500 | 16528.6927 |  | 1
85 | 80 | 62 | 36.2232 | 510000 | 474000 | 33.7 | 17500 | 16528.6927 |  | 1
85 | 80 | 57 | 22.3618 | 496000 | 496000 | 33.4 | 17500 | 16278.6369 |  | 1
95 | 80 | 75 | 79.7527 | 540000 | 172000 | 38.6 | 10000 | 4865.6704 |  | 1
95 | 80 | 72 | 68.6171 | 513000 | 209000 | 38.1 | 10000 | 4865.6704 |  | 1
95 | 80 | 67 | 51.5724 | 469000 | 268000 | 37.3 | 10000 | 4678.1285 |  | 1
95 | 80 | 62 | 36.2232 | 428000 | 326000 | 36.7 | 10000 | 4678.1285 |  | 1
95 | 80 | 57 | 22.3618 | 395000 | 380000 | 36.4 | 10000 | 4492.6704 |  | 1
95 | 80 | 75 | 79.7527 | 565000 | 185000 | 39.1 | 12500 | 7745.4804 |  | 1
95 | 80 | 72 | 68.6171 | 497000 | 189000 | 38 | 12500 | 7532.933 |  | 1
95 | 80 | 67 | 51.5724 | 495000 | 304000 | 37.8 | 12500 | 7532.933 |  | 1
95 | 80 | 62 | 36.2232 | 454000 | 375000 | 37.1 | 12500 | 7532.933 |  | 1
95 | 80 | 57 | 22.3618 | 426000 | 426000 | 36.7 | 12500 | 7532.933 |  | 1
95 | 80 | 75 | 79.7527 | 565000 | 180000 | 39.2 | 15000 | 11563 |  | 1
95 | 80 | 72 | 68.6171 | 555000 | 250000 | 38.9 | 15000 | 11563 |  | 1
95 | 80 | 67 | 51.5724 | 512000 | 336000 | 38.1 | 15000 | 11563 |  | 1
95 | 80 | 62 | 36.2232 | 470000 | 415000 | 37.3 | 15000 | 11333.7821 |  | 1
95 | 80 | 57 | 22.3618 | 452000 | 452000 | 37 | 15000 | 11333.7821 |  | 1
95 | 80 | 75 | 79.7527 | 591000 | 205000 | 39.7 | 17500 | 16528.6927 |  | 1
95 | 80 | 72 | 68.6171 | 568000 | 269000 | 39 | 17500 | 16528.6927 |  | 1
95 | 80 | 67 | 51.5724 | 524000 | 367000 | 38.3 | 17500 | 16528.6927 |  | 1
95 | 80 | 62 | 36.2232 | 482000 | 451000 | 37.6 | 17500 | 16278.6369 |  | 1
95 | 80 | 57 | 22.3618 | 477000 | 477000 | 37.5 | 17500 | 16278.6369 |  | 1
105 | 80 | 75 | 79.7527 | 512000 | 153000 | 43.2 | 10000 | 4865.6704 |  | 1
105 | 80 | 72 | 68.6171 | 484000 | 189000 | 42.7 | 10000 | 4678.1285 |  | 1
105 | 80 | 67 | 51.5724 | 444000 | 250000 | 42.1 | 10000 | 4678.1285 |  | 1
105 | 80 | 62 | 36.2232 | 405000 | 309000 | 41.6 | 10000 | 4678.1285 |  | 1
105 | 80 | 57 | 22.3618 | 378000 | 364000 | 41.5 | 10000 | 4492.6704 |  | 1
105 | 80 | 75 | 79.7527 | 533000 | 163000 | 43.6 | 12500 | 7745.4804 |  | 1
105 | 80 | 72 | 68.6171 | 506000 | 207000 | 43 | 12500 | 7745.4804 |  | 1
105 | 80 | 67 | 51.5724 | 465000 | 281000 | 42.4 | 12500 | 7532.933 |  | 1
105 | 80 | 62 | 36.2232 | 424000 | 352000 | 41.8 | 12500 | 7532.933 |  | 1
105 | 80 | 57 | 22.3618 | 400000 | 400000 | 41.5 | 12500 | 7322.4693 |  | 1
105 | 80 | 75 | 79.7527 | 548000 | 174000 | 43.9 | 15000 | 11563 |  | 1
105 | 80 | 72 | 68.6171 | 523000 | 227000 | 43.3 | 15000 | 11563 |  | 1
105 | 80 | 67 | 51.5724 | 482000 | 315000 | 42.6 | 15000 | 11333.7821 |  | 1
105 | 80 | 62 | 36.2232 | 440000 | 392000 | 42 | 15000 | 11333.7821 |  | 1
105 | 80 | 57 | 22.3618 | 423000 | 423000 | 41.7 | 15000 | 11333.7821 |  | 1
105 | 80 | 75 | 79.7527 | 524000 | 149000 | 43.6 | 17500 | 16528.6927 |  | 1
105 | 80 | 72 | 68.6171 | 535000 | 246000 | 43.6 | 17500 | 16528.6927 |  | 1
105 | 80 | 67 | 51.5724 | 494000 | 346000 | 42.8 | 17500 | 16278.6369 |  | 1
105 | 80 | 62 | 36.2232 | 455000 | 430000 | 42.2 | 17500 | 16278.6369 |  | 1
105 | 80 | 57 | 22.3618 | 445000 | 445000 | 42 | 17500 | 16278.6369 |  | 1
115 | 80 | 75 | 79.7527 | 477000 | 127000 | 48.5 | 10000 | 4678.1285 |  | 1
115 | 80 | 72 | 68.6171 | 454000 | 167000 | 48.1 | 10000 | 4678.1285 |  | 1
115 | 80 | 67 | 51.5724 | 421000 | 236000 | 47.8 | 10000 | 4678.1285 |  | 1
115 | 80 | 62 | 36.2232 | 385000 | 296000 | 47.5 | 10000 | 4492.6704 |  | 1
115 | 80 | 57 | 22.3618 | 350000 | 337000 | 47.2 | 10000 | 4309.2961 |  | 1
115 | 80 | 75 | 79.7527 | 500000 | 139000 | 48.9 | 12500 | 7532.933 |  | 1
115 | 80 | 72 | 68.6171 | 474000 | 184000 | 48.4 | 12500 | 7532.933 |  | 1
115 | 80 | 67 | 51.5724 | 432000 | 257000 | 47.8 | 12500 | 7532.933 |  | 1
115 | 80 | 62 | 36.2232 | 398000 | 332000 | 47.5 | 12500 | 7322.4693 |  | 1
115 | 80 | 57 | 22.3618 | 377000 | 377000 | 47.3 | 12500 | 7322.4693 |  | 1
115 | 80 | 75 | 79.7527 | 515000 | 150000 | 49.2 | 15000 | 11563 |  | 1
115 | 80 | 72 | 68.6171 | 489000 | 203000 | 48.7 | 15000 | 11333.7821 |  | 1
115 | 80 | 67 | 51.5724 | 450000 | 292000 | 48 | 15000 | 11333.7821 |  | 1
115 | 80 | 62 | 36.2232 | 413000 | 372000 | 47.6 | 15000 | 11333.7821 |  | 1
115 | 80 | 57 | 22.3618 | 401000 | 401000 | 47.4 | 15000 | 11333.7821 |  | 1
115 | 80 | 75 | 79.7527 | 533000 | 168000 | 49.5 | 17500 | 16528.6927 |  | 1
115 | 80 | 72 | 68.6171 | 502000 | 223000 | 48.9 | 17500 | 16528.6927 |  | 1
115 | 80 | 67 | 51.5724 | 459000 | 320000 | 48.1 | 17500 | 16278.6369 |  | 1
115 | 80 | 62 | 36.2232 | 427000 | 404000 | 47.7 | 17500 | 16278.6369 |  | 1
115 | 80 | 57 | 22.3618 | 421000 | 421000 | 47.6 | 17500 | 16278.6369 |  | 1
75 | 80 | 75 | 79.7527 | 657000 | 255000 | 32.7 | 20000 | 22669.648 |  | 1
75 | 80 | 72 | 68.6171 | 628000 | 320000 | 32.2 | 20000 | 22669.648 |  | 1
75 | 80 | 67 | 51.5724 | 564000 | 412000 | 31 | 20000 | 22669.648 |  | 1
75 | 80 | 62 | 36.2232 | 549000 | 530000 | 30.6 | 20000 | 22669.648 |  | 1
75 | 80 | 57 | 22.3618 | 544000 | 544000 | 30.5 | 20000 | 22669.648 |  | 1
75 | 80 | 75 | 79.7527 | 666000 | 267000 | 32.9 | 22500 | 22669.648 |  | 1
75 | 80 | 72 | 68.6171 | 640000 | 343000 | 32.4 | 22500 | 22669.648 |  | 1
75 | 80 | 67 | 51.5724 | 592000 | 460000 | 31.5 | 22500 | 22669.648 |  | 1
75 | 80 | 62 | 36.2232 | 561000 | 557000 | 30.8 | 22500 | 22669.648 |  | 1
75 | 80 | 57 | 22.3618 | 559000 | 559000 | 30.7 | 22500 | 22669.648 |  | 1
75 | 80 | 75 | 79.7527 | 671000 | 276000 | 33 | 25000 | 22669.648 |  | 1
75 | 80 | 72 | 68.6171 | 646000 | 360000 | 32.5 | 25000 | 22669.648 |  | 1
75 | 80 | 67 | 51.5724 | 604000 | 493000 | 31.8 | 25000 | 22669.648 |  | 1
75 | 80 | 62 | 36.2232 | 575000 | 575000 | 31 | 25000 | 22669.648 |  | 1
75 | 80 | 57 | 22.3618 | 574000 | 574000 | 31 | 25000 | 22669.648 |  | 1
85 | 80 | 75 | 79.7527 | 613000 | 428000 | 35.7 | 20000 | 22669.648 |  | 1
85 | 80 | 72 | 68.6171 | 586000 | 422000 | 35.2 | 20000 | 22669.648 |  | 1
85 | 80 | 67 | 51.5724 | 527000 | 409000 | 34.1 | 20000 | 22669.648 |  | 1
85 | 80 | 62 | 36.2232 | 523000 | 407000 | 33.9 | 20000 | 22669.648 |  | 1
85 | 80 | 57 | 22.3618 | 517000 | 406000 | 33.8 | 20000 | 22669.648 |  | 1
85 | 80 | 75 | 79.7527 | 641000 | 437000 | 36.4 | 22500 | 22669.648 |  | 1
85 | 80 | 72 | 68.6171 | 614000 | 430000 | 35.8 | 22500 | 22669.648 |  | 1
85 | 80 | 67 | 51.5724 | 573000 | 418000 | 34.8 | 22500 | 22669.648 |  | 1
85 | 80 | 62 | 36.2232 | 536000 | 409000 | 34.1 | 22500 | 22669.648 |  | 1
85 | 80 | 57 | 22.3618 | 532000 | 409000 | 34.1 | 22500 | 22669.648 |  | 1
85 | 80 | 75 | 79.7527 | 630000 | 433000 | 36.1 | 25000 | 22669.648 |  | 1
85 | 80 | 72 | 68.6171 | 620000 | 430000 | 35.8 | 25000 | 22669.648 |  | 1
85 | 80 | 67 | 51.5724 | 568000 | 416000 | 34.7 | 25000 | 22669.648 |  | 1
85 | 80 | 62 | 36.2232 | 553000 | 553000 | 34.4 | 25000 | 22669.648 |  | 1
85 | 80 | 57 | 22.3618 | 552000 | 552000 | 34.4 | 25000 | 22669.648 |  | 1
95 | 80 | 75 | 79.7527 | 608000 | 224000 | 39.9 | 20000 | 22669.648 |  | 1
95 | 80 | 72 | 68.6171 | 579000 | 289000 | 39.3 | 20000 | 22669.648 |  | 1
95 | 80 | 67 | 51.5724 | 534000 | 397000 | 38.5 | 20000 | 22669.648 |  | 1
95 | 80 | 62 | 36.2232 | 499000 | 486000 | 37.8 | 20000 | 22398.7542 |  | 1
95 | 80 | 57 | 22.3618 | 494000 | 494000 | 37.7 | 20000 | 22398.7542 |  | 1
95 | 80 | 75 | 79.7527 | 615000 | 236000 | 40 | 22500 | 22669.648 |  | 1
95 | 80 | 72 | 68.6171 | 588000 | 309000 | 39.5 | 22500 | 22669.648 |  | 1
95 | 80 | 67 | 51.5724 | 535000 | 419000 | 38.5 | 22500 | 22669.648 |  | 1
95 | 80 | 62 | 36.2232 | 508000 | 505000 | 38 | 22500 | 22669.648 |  | 1
95 | 80 | 57 | 22.3618 | 506000 | 506000 | 38 | 22500 | 22669.648 |  | 1
95 | 80 | 75 | 79.7527 | 599000 | 222000 | 39.9 | 25000 | 22669.648 |  | 1
95 | 80 | 72 | 68.6171 | 598000 | 329000 | 39.7 | 25000 | 22669.648 |  | 1
95 | 80 | 67 | 51.5724 | 549000 | 454000 | 38.8 | 25000 | 22669.648 |  | 1
95 | 80 | 62 | 36.2232 | 520000 | 520000 | 38.2 | 25000 | 22669.648 |  | 1
95 | 80 | 57 | 22.3618 | 524000 | 524000 | 38.2 | 25000 | 22669.648 |  | 1
105 | 80 | 75 | 79.7527 | 568000 | 194000 | 44.3 | 20000 | 22669.648 |  | 1
105 | 80 | 72 | 68.6171 | 517000 | 237000 | 43.3 | 20000 | 22669.648 |  | 1
105 | 80 | 67 | 51.5724 | 501000 | 374000 | 42.9 | 20000 | 22669.648 |  | 1
105 | 80 | 62 | 36.2232 | 473000 | 461000 | 42.4 | 20000 | 22398.7542 |  | 1
105 | 80 | 57 | 22.3618 | 462000 | 462000 | 42.2 | 20000 | 22398.7542 |  | 1
105 | 80 | 75 | 79.7527 | 579000 | 210000 | 44.5 | 22500 | 22669.648 |  | 1
105 | 80 | 72 | 68.6171 | 553000 | 284000 | 43.9 | 22500 | 22669.648 |  | 1
105 | 80 | 67 | 51.5724 | 509000 | 402000 | 43 | 22500 | 22669.648 |  | 1
105 | 80 | 62 | 36.2232 | 478000 | 478000 | 42.5 | 22500 | 22398.7542 |  | 1
105 | 80 | 57 | 22.3618 | 476000 | 476000 | 42.5 | 22500 | 22398.7542 |  | 1
105 | 80 | 75 | 79.7527 | 562000 | 198000 | 44.3 | 25000 | 22669.648 |  | 1
105 | 80 | 72 | 68.6171 | 548000 | 292000 | 43.9 | 25000 | 22669.648 |  | 1
105 | 80 | 67 | 51.5724 | 516000 | 430000 | 43.2 | 25000 | 22669.648 |  | 1
105 | 80 | 62 | 36.2232 | 494000 | 494000 | 42.7 | 25000 | 22398.7542 |  | 1
105 | 80 | 57 | 22.3618 | 494000 | 494000 | 42.7 | 25000 | 22398.7542 |  | 1
115 | 80 | 75 | 79.7527 | 496000 | 134000 | 49 | 20000 | 22398.7542 |  | 1
115 | 80 | 72 | 68.6171 | 481000 | 211000 | 48.5 | 20000 | 22398.7542 |  | 1
115 | 80 | 67 | 51.5724 | 469000 | 350000 | 48.2 | 20000 | 22398.7542 |  | 1
115 | 80 | 62 | 36.2232 | 443000 | 432000 | 47.8 | 20000 | 22398.7542 |  | 1
115 | 80 | 57 | 22.3618 | 439000 | 439000 | 47.7 | 20000 | 22398.7542 |  | 1
115 | 80 | 75 | 79.7527 | 514000 | 155000 | 49.3 | 22500 | 22669.648 |  | 1
115 | 80 | 72 | 68.6171 | 490000 | 204000 | 48.7 | 22500 | 22398.7542 |  | 1
115 | 80 | 67 | 51.5724 | 476000 | 378000 | 48.3 | 22500 | 22398.7542 |  | 1
115 | 80 | 62 | 36.2232 | 452000 | 452000 | 47.9 | 22500 | 22398.7542 |  | 1
115 | 80 | 57 | 22.3618 | 452000 | 452000 | 47.9 | 22500 | 22398.7542 |  | 1
115 | 80 | 75 | 79.7527 | 533000 | 179000 | 49.5 | 25000 | 22669.648 |  | 1
115 | 80 | 72 | 68.6171 | 506000 | 231000 | 48.9 | 25000 | 22669.648 |  | 1
115 | 80 | 67 | 51.5724 | 482000 | 404000 | 48.4 | 25000 | 22398.7542 |  | 1
115 | 80 | 62 | 36.2232 | 461000 | 461000 | 48 | 25000 | 22398.7542 |  | 1
115 | 80 | 57 | 22.3618 | 462000 | 462000 | 48.1 | 25000 | 22398.7542 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 8
Degradation Coefficient (C_d) |  | 48/50A060 (60 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 72 | 68.6171 | 671000 | 294000 | 39 | 12000 | 4953.1899 |  | 1
75 | 80 | 67 | 51.5724 | 616000 | 361000 | 38 | 12000 | 4953.1899 |  | 1
75 | 80 | 62 | 36.2232 | 563000 | 425000 | 37.1 | 12000 | 4953.1899 |  | 1
75 | 80 | 57 | 22.3618 | 513000 | 483000 | 36.2 | 12000 | 4953.1899 |  | 1
75 | 80 | 75 | 79.7527 | 742000 | 271000 | 40.4 | 15000 | 7428.743 |  | 1
75 | 80 | 72 | 68.6171 | 706000 | 320000 | 39.7 | 15000 | 7428.743 |  | 1
75 | 80 | 67 | 51.5724 | 649000 | 400000 | 38.6 | 15000 | 7428.743 |  | 1
75 | 80 | 62 | 36.2232 | 596000 | 481000 | 37.7 | 15000 | 7428.743 |  | 1
75 | 80 | 57 | 22.3618 | 549000 | 542000 | 36.9 | 15000 | 7428.743 |  | 1
75 | 80 | 75 | 79.7527 | 767000 | 288000 | 40.8 | 18000 | 10712.8101 |  | 1
75 | 80 | 72 | 68.6171 | 732000 | 346000 | 40.2 | 18000 | 10712.8101 |  | 1
75 | 80 | 67 | 51.5724 | 675000 | 441000 | 39.1 | 18000 | 10712.8101 |  | 1
75 | 80 | 62 | 36.2232 | 620000 | 531000 | 38 | 18000 | 10712.8101 |  | 1
75 | 80 | 57 | 22.3618 | 583000 | 583000 | 37.4 | 18000 | 10712.8101 |  | 1
75 | 80 | 75 | 79.7527 | 787000 | 303000 | 41.2 | 21000 | 14922.0838 |  | 1
75 | 80 | 72 | 68.6171 | 751000 | 368000 | 40.5 | 21000 | 14922.0838 |  | 1
75 | 80 | 67 | 51.5724 | 693000 | 477000 | 39.4 | 21000 | 14922.0838 |  | 1
75 | 80 | 62 | 36.2232 | 639000 | 578000 | 38.4 | 21000 | 14922.0838 |  | 1
75 | 80 | 57 | 22.3618 | 613000 | 613000 | 38 | 21000 | 14922.0838 |  | 1
85 | 80 | 75 | 79.7527 | 676000 | 229000 | 43.8 | 12000 | 4953.1899 |  | 1
85 | 80 | 72 | 68.6171 | 642000 | 272000 | 43.1 | 12000 | 4953.1899 |  | 1
85 | 80 | 67 | 51.5724 | 588000 | 340000 | 42.1 | 12000 | 4953.1899 |  | 1
85 | 80 | 62 | 36.2232 | 539000 | 406000 | 41.2 | 12000 | 4953.1899 |  | 1
85 | 80 | 57 | 22.3618 | 492000 | 466000 | 40.4 | 12000 | 4657.2905 |  | 1
85 | 80 | 75 | 79.7527 | 709000 | 247000 | 44.4 | 15000 | 7428.743 |  | 1
85 | 80 | 72 | 68.6171 | 675000 | 297000 | 43.7 | 15000 | 7428.743 |  | 1
85 | 80 | 67 | 51.5724 | 620000 | 379000 | 42.7 | 15000 | 7428.743 |  | 1
85 | 80 | 62 | 36.2232 | 568000 | 459000 | 41.7 | 15000 | 7428.743 |  | 1
85 | 80 | 57 | 22.3618 | 525000 | 519000 | 41 | 15000 | 7428.743 |  | 1
85 | 80 | 75 | 79.7527 | 730000 | 260000 | 44.9 | 18000 | 10712.8101 |  | 1
85 | 80 | 72 | 68.6171 | 697000 | 320000 | 44.2 | 18000 | 10712.8101 |  | 1
85 | 80 | 67 | 51.5724 | 643000 | 416000 | 43.1 | 18000 | 10712.8101 |  | 1
85 | 80 | 62 | 36.2232 | 590000 | 508000 | 42.1 | 18000 | 10712.8101 |  | 1
85 | 80 | 57 | 22.3618 | 556000 | 556000 | 41.5 | 18000 | 10712.8101 |  | 1
85 | 80 | 75 | 79.7527 | 748000 | 275000 | 45.2 | 21000 | 14922.0838 |  | 1
85 | 80 | 72 | 68.6171 | 714000 | 341000 | 44.5 | 21000 | 14922.0838 |  | 1
85 | 80 | 67 | 51.5724 | 660000 | 452000 | 43.5 | 21000 | 14922.0838 |  | 1
85 | 80 | 62 | 36.2232 | 607000 | 552000 | 42.4 | 21000 | 14922.0838 |  | 1
85 | 80 | 57 | 22.3618 | 585000 | 585000 | 42 | 21000 | 14922.0838 |  | 1
95 | 80 | 75 | 79.7527 | 643000 | 205000 | 48.4 | 12000 | 4953.1899 |  | 1
95 | 80 | 72 | 68.6171 | 608000 | 245000 | 47.7 | 12000 | 4953.1899 |  | 1
95 | 80 | 67 | 51.5724 | 559000 | 317000 | 46.7 | 12000 | 4953.1899 |  | 1
95 | 80 | 62 | 36.2232 | 511000 | 384000 | 45.8 | 12000 | 4953.1899 |  | 1
95 | 80 | 57 | 22.3618 | 464000 | 445000 | 45 | 12000 | 4657.2905 |  | 1
95 | 80 | 75 | 79.7527 | 674000 | 220000 | 49 | 15000 | 7428.743 |  | 1
95 | 80 | 72 | 68.6171 | 641000 | 271000 | 48.3 | 15000 | 7428.743 |  | 1
95 | 80 | 67 | 51.5724 | 589000 | 356000 | 47.3 | 15000 | 7428.743 |  | 1
95 | 80 | 62 | 36.2232 | 539000 | 437000 | 46.3 | 15000 | 7428.743 |  | 1
95 | 80 | 57 | 22.3618 | 500000 | 494000 | 45.6 | 15000 | 7099.5028 |  | 1
95 | 80 | 75 | 79.7527 | 695000 | 235000 | 49.5 | 18000 | 10712.8101 |  | 1
95 | 80 | 72 | 68.6171 | 663000 | 294000 | 48.8 | 18000 | 10712.8101 |  | 1
95 | 80 | 67 | 51.5724 | 610000 | 392000 | 47.7 | 18000 | 10712.8101 |  | 1
95 | 80 | 62 | 36.2232 | 560000 | 485000 | 46.7 | 18000 | 10712.8101 |  | 1
95 | 80 | 57 | 22.3618 | 531000 | 531000 | 46.2 | 18000 | 10712.8101 |  | 1
95 | 80 | 75 | 79.7527 | 711000 | 249000 | 49.8 | 21000 | 14922.0838 |  | 1
95 | 80 | 72 | 68.6171 | 679000 | 316000 | 49.1 | 21000 | 14922.0838 |  | 1
95 | 80 | 67 | 51.5724 | 626000 | 427000 | 48 | 21000 | 14922.0838 |  | 1
95 | 80 | 62 | 36.2232 | 576000 | 528000 | 47 | 21000 | 14922.0838 |  | 1
95 | 80 | 57 | 22.3618 | 556000 | 556000 | 46.6 | 21000 | 14922.0838 |  | 1
105 | 80 | 75 | 79.7527 | 609000 | 179000 | 53.6 | 12000 | 4953.1899 |  | 1
105 | 80 | 72 | 68.6171 | 574000 | 220000 | 52.8 | 12000 | 4953.1899 |  | 1
105 | 80 | 67 | 51.5724 | 528000 | 294000 | 51.9 | 12000 | 4953.1899 |  | 1
105 | 80 | 62 | 36.2232 | 481000 | 362000 | 51 | 12000 | 4657.2905 |  | 1
105 | 80 | 57 | 22.3618 | 439000 | 420000 | 50.2 | 12000 | 4657.2905 |  | 1
105 | 80 | 75 | 79.7527 | 636000 | 193000 | 54.2 | 15000 | 7428.743 |  | 1
105 | 80 | 72 | 68.6171 | 606000 | 245000 | 53.5 | 15000 | 7428.743 |  | 1
105 | 80 | 67 | 51.5724 | 556000 | 331000 | 52.5 | 15000 | 7428.743 |  | 1
105 | 80 | 62 | 36.2232 | 508000 | 413000 | 51.5 | 15000 | 7428.743 |  | 1
105 | 80 | 57 | 22.3618 | 473000 | 469000 | 50.8 | 15000 | 7099.5028 |  | 1
105 | 80 | 75 | 79.7527 | 654000 | 205000 | 54.6 | 18000 | 10712.8101 |  | 1
105 | 80 | 72 | 68.6171 | 625000 | 267000 | 54 | 18000 | 10712.8101 |  | 1
105 | 80 | 67 | 51.5724 | 575000 | 366000 | 52.9 | 18000 | 10712.8101 |  | 1
105 | 80 | 62 | 36.2232 | 527000 | 459000 | 51.9 | 18000 | 10712.8101 |  | 1
105 | 80 | 57 | 22.3618 | 501000 | 501000 | 51.4 | 18000 | 10712.8101 |  | 1
105 | 80 | 75 | 79.7527 | 671000 | 219000 | 55 | 21000 | 14922.0838 |  | 1
105 | 80 | 72 | 68.6171 | 640000 | 288000 | 54.3 | 21000 | 14922.0838 |  | 1
105 | 80 | 67 | 51.5724 | 590000 | 401000 | 53.2 | 21000 | 14922.0838 |  | 1
105 | 80 | 62 | 36.2232 | 543000 | 501000 | 52.2 | 21000 | 14922.0838 |  | 1
105 | 80 | 57 | 22.3618 | 526000 | 526000 | 51.9 | 21000 | 14922.0838 |  | 1
115 | 80 | 75 | 79.7527 | 571000 | 153000 | 59.4 | 12000 | 4953.1899 |  | 1
115 | 80 | 72 | 68.6171 | 538000 | 193000 | 58.7 | 12000 | 4953.1899 |  | 1
115 | 80 | 67 | 51.5724 | 494000 | 268000 | 57.8 | 12000 | 4657.2905 |  | 1
115 | 80 | 62 | 36.2232 | 450000 | 338000 | 56.9 | 12000 | 4657.2905 |  | 1
115 | 80 | 57 | 22.3618 | 413000 | 395000 | 56.1 | 12000 | 4657.2905 |  | 1
115 | 80 | 75 | 79.7527 | 594000 | 162000 | 59.9 | 15000 | 7428.743 |  | 1
115 | 80 | 72 | 68.6171 | 566000 | 217000 | 59.3 | 15000 | 7428.743 |  | 1
115 | 80 | 67 | 51.5724 | 519000 | 304000 | 58.3 | 15000 | 7428.743 |  | 1
115 | 80 | 62 | 36.2232 | 474000 | 387000 | 57.4 | 15000 | 7099.5028 |  | 1
115 | 80 | 57 | 22.3618 | 443000 | 443000 | 56.7 | 15000 | 7099.5028 |  | 1
115 | 80 | 75 | 79.7527 | 614000 | 177000 | 60.4 | 18000 | 10712.8101 |  | 1
115 | 80 | 72 | 68.6171 | 585000 | 238000 | 59.7 | 18000 | 10712.8101 |  | 1
115 | 80 | 67 | 51.5724 | 538000 | 339000 | 58.7 | 18000 | 10712.8101 |  | 1
115 | 80 | 62 | 36.2232 | 492000 | 433000 | 57.7 | 18000 | 10350.2291 |  | 1
115 | 80 | 57 | 22.3618 | 470000 | 470000 | 57.3 | 18000 | 10350.2291 |  | 1
115 | 80 | 75 | 79.7527 | 628000 | 189000 | 60.7 | 21000 | 14922.0838 |  | 1
115 | 80 | 72 | 68.6171 | 599000 | 259000 | 60 | 21000 | 14922.0838 |  | 1
115 | 80 | 67 | 51.5724 | 551000 | 373000 | 59 | 21000 | 14922.0838 |  | 1
115 | 80 | 62 | 36.2232 | 506000 | 472000 | 58 | 21000 | 14922.0838 |  | 1
115 | 80 | 57 | 22.3618 | 494000 | 494000 | 57.8 | 21000 | 14526.162 |  | 1
75 | 80 | 75 | 79.7527 | 804000 | 320000 | 41.5 | 24000 | 20125.3296 |  | 1
75 | 80 | 72 | 68.6171 | 768000 | 392000 | 40.9 | 24000 | 20125.3296 |  | 1
75 | 80 | 67 | 51.5724 | 708000 | 512000 | 39.7 | 24000 | 20125.3296 |  | 1
75 | 80 | 62 | 36.2232 | 654000 | 618000 | 38.7 | 24000 | 20125.3296 |  | 1
75 | 80 | 57 | 22.3618 | 637000 | 637000 | 38.4 | 24000 | 20125.3296 |  | 1
75 | 80 | 75 | 79.7527 | 814000 | 332000 | 41.8 | 27000 | 26420.486 |  | 1
75 | 80 | 72 | 68.6171 | 779000 | 413000 | 41.1 | 27000 | 26420.486 |  | 1
75 | 80 | 67 | 51.5724 | 720000 | 546000 | 39.9 | 27000 | 26420.486 |  | 1
75 | 80 | 62 | 36.2232 | 665000 | 652000 | 38.9 | 27000 | 26420.486 |  | 1
75 | 80 | 57 | 22.3618 | 657000 | 657000 | 38.8 | 27000 | 26420.486 |  | 1
75 | 80 | 75 | 79.7527 | 825000 | 346000 | 42 | 30000 | 26420.486 |  | 1
75 | 80 | 72 | 68.6171 | 789000 | 434000 | 41.3 | 30000 | 26420.486 |  | 1
75 | 80 | 67 | 51.5724 | 729000 | 578000 | 40.1 | 30000 | 26420.486 |  | 1
75 | 80 | 62 | 36.2232 | 678000 | 678000 | 39.2 | 30000 | 26420.486 |  | 1
75 | 80 | 57 | 22.3618 | 674000 | 674000 | 39.1 | 30000 | 26420.486 |  | 1
85 | 80 | 75 | 79.7527 | 761000 | 289000 | 45.5 | 24000 | 20125.3296 |  | 1
85 | 80 | 72 | 68.6171 | 729000 | 364000 | 44.8 | 24000 | 20125.3296 |  | 1
85 | 80 | 67 | 51.5724 | 674000 | 487000 | 43.7 | 24000 | 20125.3296 |  | 1
85 | 80 | 62 | 36.2232 | 621000 | 591000 | 42.7 | 24000 | 20125.3296 |  | 1
85 | 80 | 57 | 22.3618 | 607000 | 607000 | 42.5 | 24000 | 20125.3296 |  | 1
85 | 80 | 75 | 79.7527 | 772000 | 302000 | 45.7 | 27000 | 26420.486 |  | 1
85 | 80 | 72 | 68.6171 | 740000 | 385000 | 45.1 | 27000 | 26420.486 |  | 1
85 | 80 | 67 | 51.5724 | 684000 | 520000 | 43.9 | 27000 | 26420.486 |  | 1
85 | 80 | 62 | 36.2232 | 634000 | 621000 | 43 | 27000 | 26420.486 |  | 1
85 | 80 | 57 | 22.3618 | 627000 | 627000 | 42.8 | 27000 | 26420.486 |  | 1
85 | 80 | 75 | 79.7527 | 783000 | 317000 | 46 | 30000 | 26420.486 |  | 1
85 | 80 | 72 | 68.6171 | 749000 | 406000 | 45.3 | 30000 | 26420.486 |  | 1
85 | 80 | 67 | 51.5724 | 693000 | 552000 | 44.1 | 30000 | 26420.486 |  | 1
85 | 80 | 62 | 36.2232 | 647000 | 647000 | 43.2 | 30000 | 26420.486 |  | 1
85 | 80 | 57 | 22.3618 | 646000 | 646000 | 43.2 | 30000 | 26420.486 |  | 1
95 | 80 | 75 | 79.7527 | 722000 | 260000 | 50.1 | 24000 | 20125.3296 |  | 1
95 | 80 | 72 | 68.6171 | 691000 | 337000 | 49.4 | 24000 | 20125.3296 |  | 1
95 | 80 | 67 | 51.5724 | 639000 | 461000 | 48.3 | 24000 | 20125.3296 |  | 1
95 | 80 | 62 | 36.2232 | 589000 | 565000 | 47.3 | 24000 | 20125.3296 |  | 1
95 | 80 | 57 | 22.3618 | 578000 | 578000 | 47.1 | 24000 | 20125.3296 |  | 1
95 | 80 | 75 | 79.7527 | 734000 | 275000 | 50.3 | 27000 | 26420.486 |  | 1
95 | 80 | 72 | 68.6171 | 702000 | 358000 | 49.6 | 27000 | 26420.486 |  | 1
95 | 80 | 67 | 51.5724 | 647000 | 492000 | 48.5 | 27000 | 26420.486 |  | 1
95 | 80 | 62 | 36.2232 | 599000 | 588000 | 47.5 | 27000 | 26420.486 |  | 1
95 | 80 | 57 | 22.3618 | 597000 | 597000 | 47.4 | 27000 | 26420.486 |  | 1
95 | 80 | 75 | 79.7527 | 742000 | 287000 | 50.5 | 30000 | 26420.486 |  | 1
95 | 80 | 72 | 68.6171 | 709000 | 377000 | 49.8 | 30000 | 26420.486 |  | 1
95 | 80 | 67 | 51.5724 | 656000 | 524000 | 48.6 | 30000 | 26420.486 |  | 1
95 | 80 | 62 | 36.2232 | 612000 | 612000 | 47.7 | 30000 | 26420.486 |  | 1
95 | 80 | 57 | 22.3618 | 613000 | 613000 | 47.8 | 30000 | 26420.486 |  | 1
105 | 80 | 75 | 79.7527 | 682000 | 232000 | 55.3 | 24000 | 20125.3296 |  | 1
105 | 80 | 72 | 68.6171 | 651000 | 308000 | 54.5 | 24000 | 20125.3296 |  | 1
105 | 80 | 67 | 51.5724 | 601000 | 434000 | 53.4 | 24000 | 20125.3296 |  | 1
105 | 80 | 62 | 36.2232 | 556000 | 533000 | 52.5 | 24000 | 20125.3296 |  | 1
105 | 80 | 57 | 22.3618 | 547000 | 547000 | 52.3 | 24000 | 20125.3296 |  | 1
105 | 80 | 75 | 79.7527 | 692000 | 245000 | 55.5 | 27000 | 26420.486 |  | 1
105 | 80 | 72 | 68.6171 | 661000 | 328000 | 54.8 | 27000 | 26420.486 |  | 1
105 | 80 | 67 | 51.5724 | 608000 | 464000 | 53.6 | 27000 | 26420.486 |  | 1
105 | 80 | 62 | 36.2232 | 569000 | 559000 | 52.7 | 27000 | 26420.486 |  | 1
105 | 80 | 57 | 22.3618 | 565000 | 565000 | 52.7 | 27000 | 26420.486 |  | 1
105 | 80 | 75 | 79.7527 | 700000 | 258000 | 55.7 | 30000 | 26420.486 |  | 1
105 | 80 | 72 | 68.6171 | 669000 | 349000 | 54.9 | 30000 | 26420.486 |  | 1
105 | 80 | 67 | 51.5724 | 618000 | 496000 | 53.8 | 30000 | 26420.486 |  | 1
105 | 80 | 62 | 36.2232 | 582000 | 582000 | 53 | 30000 | 26420.486 |  | 1
105 | 80 | 57 | 22.3618 | 580000 | 580000 | 53 | 30000 | 26420.486 |  | 1
115 | 80 | 75 | 79.7527 | 639000 | 202000 | 61 | 24000 | 20125.3296 |  | 1
115 | 80 | 72 | 68.6171 | 610000 | 279000 | 60.3 | 24000 | 20125.3296 |  | 1
115 | 80 | 67 | 51.5724 | 562000 | 406000 | 59.2 | 24000 | 20125.3296 |  | 1
115 | 80 | 62 | 36.2232 | 521000 | 501000 | 58.3 | 24000 | 20125.3296 |  | 1
115 | 80 | 57 | 22.3618 | 514000 | 514000 | 58.2 | 24000 | 20125.3296 |  | 1
115 | 80 | 75 | 79.7527 | 647000 | 214000 | 61.2 | 27000 | 26420.486 |  | 1
115 | 80 | 72 | 68.6171 | 618000 | 299000 | 60.5 | 27000 | 26420.486 |  | 1
115 | 80 | 67 | 51.5724 | 570000 | 437000 | 59.4 | 27000 | 26420.486 |  | 1
115 | 80 | 62 | 36.2232 | 535000 | 527000 | 58.6 | 27000 | 26420.486 |  | 1
115 | 80 | 57 | 22.3618 | 531000 | 531000 | 58.5 | 27000 | 26420.486 |  | 1
115 | 80 | 75 | 79.7527 | 655000 | 226000 | 61.4 | 30000 | 26420.486 |  | 1
115 | 80 | 72 | 68.6171 | 625000 | 318000 | 60.7 | 30000 | 26420.486 |  | 1
115 | 80 | 67 | 51.5724 | 575000 | 464000 | 59.5 | 30000 | 26420.486 |  | 1
115 | 80 | 62 | 36.2232 | 546000 | 546000 | 58.8 | 30000 | 26420.486 |  | 1
115 | 80 | 57 | 22.3618 | 545000 | 545000 | 58.8 | 30000 | 26420.486 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 9
Degradation Coefficient (C_d) |  | 48/50 030 (30 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 341000 | 97000 | 23.7 | 6000 | 833.5196 |  | 1
75 | 80 | 72 | 68.6171 | 322000 | 118000 | 23.2 | 6000 | 833.5196 |  | 1
75 | 80 | 67 | 51.5724 | 293000 | 151000 | 22.4 | 6000 | 833.5196 |  | 1
75 | 80 | 62 | 36.2232 | 266000 | 185000 | 21.8 | 6000 | 758.5028 |  | 1
75 | 80 | 57 | 22.3618 | 243000 | 218000 | 21.3 | 6000 | 758.5028 |  | 1
75 | 80 | 75 | 79.7527 | 361000 | 104000 | 24.3 | 7500 | 1316.9609 |  | 1
75 | 80 | 72 | 68.6171 | 340000 | 128000 | 23.7 | 7500 | 1150.257 |  | 1
75 | 80 | 67 | 51.5724 | 309000 | 168000 | 22.9 | 7500 | 1150.257 |  | 1
75 | 80 | 62 | 36.2232 | 282000 | 209000 | 22.2 | 7500 | 1150.257 |  | 1
75 | 80 | 57 | 22.3618 | 260000 | 244000 | 21.6 | 7500 | 1066.905 |  | 1
75 | 80 | 75 | 79.7527 | 375000 | 112000 | 24.8 | 9000 | 1762.8939 |  | 1
75 | 80 | 72 | 68.6171 | 353000 | 138000 | 24.2 | 9000 | 1762.8939 |  | 1
75 | 80 | 67 | 51.5724 | 321000 | 184000 | 23.2 | 9000 | 1587.8547 |  | 1
75 | 80 | 62 | 36.2232 | 293000 | 231000 | 22.5 | 9000 | 1587.8547 |  | 1
75 | 80 | 57 | 22.3618 | 273000 | 266000 | 21.9 | 9000 | 1500.3352 |  | 1
75 | 80 | 75 | 79.7527 | 385000 | 118000 | 25.1 | 10500 | 2369.2793 |  | 1
75 | 80 | 72 | 68.6171 | 363000 | 149000 | 24.5 | 10500 | 2369.2793 |  | 1
75 | 80 | 67 | 51.5724 | 330000 | 200000 | 23.5 | 10500 | 2190.0726 |  | 1
75 | 80 | 62 | 36.2232 | 301000 | 252000 | 22.7 | 10500 | 2190.0726 |  | 1
75 | 80 | 57 | 22.3618 | 283000 | 283000 | 22.2 | 10500 | 2190.0726 |  | 1
85 | 80 | 75 | 79.7527 | 320000 | 78000 | 25.8 | 6000 | 833.5196 |  | 1
85 | 80 | 72 | 68.6171 | 301000 | 100000 | 25.3 | 6000 | 833.5196 |  | 1
85 | 80 | 67 | 51.5724 | 274000 | 135000 | 24.5 | 6000 | 758.5028 |  | 1
85 | 80 | 62 | 36.2232 | 249000 | 170000 | 24 | 6000 | 758.5028 |  | 1
85 | 80 | 57 | 22.3618 | 227000 | 205000 | 23.5 | 6000 | 758.5028 |  | 1
85 | 80 | 75 | 79.7527 | 335000 | 83000 | 26.4 | 7500 | 1150.257 |  | 1
85 | 80 | 72 | 68.6171 | 316000 | 108000 | 25.8 | 7500 | 1150.257 |  | 1
85 | 80 | 67 | 51.5724 | 288000 | 150000 | 25 | 7500 | 1150.257 |  | 1
85 | 80 | 62 | 36.2232 | 262000 | 192000 | 24.3 | 7500 | 1066.905 |  | 1
85 | 80 | 57 | 22.3618 | 244000 | 229000 | 23.8 | 7500 | 1066.905 |  | 1
85 | 80 | 75 | 79.7527 | 346000 | 89000 | 26.8 | 9000 | 1587.8547 |  | 1
85 | 80 | 72 | 68.6171 | 327000 | 117000 | 26.2 | 9000 | 1587.8547 |  | 1
85 | 80 | 67 | 51.5724 | 298000 | 164000 | 25.3 | 9000 | 1587.8547 |  | 1
85 | 80 | 62 | 36.2232 | 271000 | 213000 | 24.6 | 9000 | 1500.3352 |  | 1
85 | 80 | 57 | 22.3618 | 256000 | 249000 | 24.1 | 9000 | 1500.3352 |  | 1
85 | 80 | 75 | 79.7527 | 355000 | 94000 | 27.1 | 10500 | 2369.2793 |  | 1
85 | 80 | 72 | 68.6171 | 335000 | 125000 | 26.5 | 10500 | 2190.0726 |  | 1
85 | 80 | 67 | 51.5724 | 305000 | 179000 | 25.6 | 10500 | 2190.0726 |  | 1
85 | 80 | 62 | 36.2232 | 279000 | 232000 | 24.8 | 10500 | 2100.4693 |  | 1
85 | 80 | 57 | 22.3618 | 264000 | 264000 | 24.3 | 10500 | 2100.4693 |  | 1
95 | 80 | 75 | 79.7527 | 297000 | 60000 | 28.2 | 6000 | 833.5196 |  | 1
95 | 80 | 72 | 68.6171 | 280000 | 82000 | 27.7 | 6000 | 758.5028 |  | 1
95 | 80 | 67 | 51.5724 | 254000 | 119000 | 27 | 6000 | 758.5028 |  | 1
95 | 80 | 62 | 36.2232 | 231000 | 155000 | 26.5 | 6000 | 758.5028 |  | 1
95 | 80 | 57 | 22.3618 | 212000 | 193000 | 26 | 6000 | 758.5028 |  | 1
95 | 80 | 75 | 79.7527 | 310000 | 62000 | 28.7 | 7500 | 1150.257 |  | 1
95 | 80 | 72 | 68.6171 | 293000 | 88000 | 28.1 | 7500 | 1150.257 |  | 1
95 | 80 | 67 | 51.5724 | 266000 | 131000 | 27.4 | 7500 | 1066.905 |  | 1
95 | 80 | 62 | 36.2232 | 242000 | 175000 | 26.7 | 7500 | 1066.905 |  | 1
95 | 80 | 57 | 22.3618 | 227000 | 213000 | 26.3 | 7500 | 1066.905 |  | 1
95 | 80 | 75 | 79.7527 | 319000 | 66000 | 29.1 | 9000 | 1587.8547 |  | 1
95 | 80 | 72 | 68.6171 | 301000 | 95000 | 28.5 | 9000 | 1587.8547 |  | 1
95 | 80 | 67 | 51.5724 | 274000 | 144000 | 27.6 | 9000 | 1500.3352 |  | 1
95 | 80 | 62 | 36.2232 | 250000 | 195000 | 27 | 9000 | 1500.3352 |  | 1
95 | 80 | 57 | 22.3618 | 238000 | 231000 | 26.6 | 9000 | 1500.3352 |  | 1
95 | 80 | 75 | 79.7527 | 326000 | 70000 | 29.4 | 10500 | 2190.0726 |  | 1
95 | 80 | 72 | 68.6171 | 308000 | 102000 | 28.7 | 10500 | 2190.0726 |  | 1
95 | 80 | 67 | 51.5724 | 280000 | 158000 | 27.9 | 10500 | 2100.4693 |  | 1
95 | 80 | 62 | 36.2232 | 257000 | 213000 | 27.1 | 10500 | 2100.4693 |  | 1
95 | 80 | 57 | 22.3618 | 245000 | 245000 | 26.8 | 10500 | 2100.4693 |  | 1
105 | 80 | 75 | 79.7527 | 274000 | 42000 | 30.9 | 6000 | 758.5028 |  | 1
105 | 80 | 72 | 68.6171 | 258000 | 65000 | 30.4 | 6000 | 758.5028 |  | 1
105 | 80 | 67 | 51.5724 | 234000 | 102000 | 29.8 | 6000 | 758.5028 |  | 1
105 | 80 | 62 | 36.2232 | 212000 | 140000 | 29.2 | 6000 | 758.5028 |  | 1
105 | 80 | 57 | 22.3618 | 198000 | 179000 | 28.8 | 6000 | 691.8212 |  | 1
105 | 80 | 75 | 79.7527 | 284000 | 42000 | 31.3 | 7500 | 1150.257 |  | 1
105 | 80 | 72 | 68.6171 | 268000 | 68000 | 30.8 | 7500 | 1066.905 |  | 1
105 | 80 | 67 | 51.5724 | 244000 | 113000 | 30.1 | 7500 | 1066.905 |  | 1
105 | 80 | 62 | 36.2232 | 222000 | 158000 | 29.5 | 7500 | 1066.905 |  | 1
105 | 80 | 57 | 22.3618 | 211000 | 197000 | 29.1 | 7500 | 1066.905 |  | 1
105 | 80 | 75 | 79.7527 | 291000 | 43000 | 31.6 | 9000 | 1587.8547 |  | 1
105 | 80 | 72 | 68.6171 | 275000 | 73000 | 31 | 9000 | 1500.3352 |  | 1
105 | 80 | 67 | 51.5724 | 250000 | 125000 | 30.3 | 9000 | 1500.3352 |  | 1
105 | 80 | 62 | 36.2232 | 229000 | 177000 | 29.7 | 9000 | 1500.3352 |  | 1
105 | 80 | 57 | 22.3618 | 220000 | 214000 | 29.3 | 9000 | 1500.3352 |  | 1
105 | 80 | 75 | 79.7527 | 296000 | 46000 | 31.8 | 10500 | 2190.0726 |  | 1
105 | 80 | 72 | 68.6171 | 280000 | 80000 | 31.3 | 10500 | 2100.4693 |  | 1
105 | 80 | 67 | 51.5724 | 254000 | 137000 | 30.4 | 10500 | 2100.4693 |  | 1
105 | 80 | 62 | 36.2232 | 234000 | 194000 | 29.8 | 10500 | 2100.4693 |  | 1
105 | 80 | 57 | 22.3618 | 225000 | 225000 | 29.5 | 10500 | 2100.4693 |  | 1
115 | 80 | 75 | 79.7527 | 250000 | 23000 | 33.9 | 6000 | 758.5028 |  | 1
115 | 80 | 72 | 68.6171 | 236000 | 47000 | 33.4 | 6000 | 758.5028 |  | 1
115 | 80 | 67 | 51.5724 | 214000 | 86000 | 32.8 | 6000 | 758.5028 |  | 1
115 | 80 | 62 | 36.2232 | 194000 | 125000 | 32.3 | 6000 | 691.8212 |  | 1
115 | 80 | 57 | 22.3618 | 183000 | 164000 | 32.1 | 6000 | 691.8212 |  | 1
115 | 80 | 75 | 79.7527 | 257000 | 21000 | 34.2 | 7500 | 1066.905 |  | 1
115 | 80 | 72 | 68.6171 | 243000 | 49000 | 33.7 | 7500 | 1066.905 |  | 1
115 | 80 | 67 | 51.5724 | 221000 | 95000 | 33 | 7500 | 1066.905 |  | 1
115 | 80 | 62 | 36.2232 | 201000 | 142000 | 32.5 | 7500 | 996.0559 |  | 1
115 | 80 | 57 | 22.3618 | 194000 | 181000 | 32.2 | 7500 | 996.0559 |  | 1
115 | 80 | 75 | 79.7527 | 262000 | 20000 | 34.4 | 9000 | 1500.3352 |  | 1
115 | 80 | 72 | 68.6171 | 247000 | 52000 | 33.9 | 9000 | 1500.3352 |  | 1
115 | 80 | 67 | 51.5724 | 225000 | 105000 | 33.2 | 9000 | 1500.3352 |  | 1
115 | 80 | 62 | 36.2232 | 207000 | 159000 | 32.7 | 9000 | 1429.486 |  | 1
115 | 80 | 57 | 22.3618 | 201000 | 196000 | 32.4 | 9000 | 1429.486 |  | 1
115 | 80 | 75 | 79.7527 | 266000 | 21000 | 34.6 | 10500 | 2100.4693 |  | 1
115 | 80 | 72 | 68.6171 | 251000 | 56000 | 34 | 10500 | 2100.4693 |  | 1
115 | 80 | 67 | 51.5724 | 228000 | 116000 | 33.3 | 10500 | 2100.4693 |  | 1
115 | 80 | 62 | 36.2232 | 213000 | 176000 | 32.8 | 10500 | 2100.4693 |  | 1
115 | 80 | 57 | 22.3618 | 205000 | 205000 | 32.6 | 10500 | 2025.4525 |  | 1
75 | 80 | 75 | 79.7527 | 395000 | 127000 | 25.5 | 12000 | 3148.6201 |  | 1
75 | 80 | 72 | 68.6171 | 372000 | 159000 | 24.8 | 12000 | 3148.6201 |  | 1
75 | 80 | 67 | 51.5724 | 337000 | 216000 | 23.8 | 12000 | 2961.0782 |  | 1
75 | 80 | 62 | 36.2232 | 308000 | 271000 | 22.9 | 12000 | 2961.0782 |  | 1
75 | 80 | 57 | 22.3618 | 294000 | 294000 | 22.5 | 12000 | 2961.0782 |  | 1
75 | 80 | 75 | 79.7527 | 401000 | 132000 | 25.7 | 13500 | 4332.2179 |  | 1
75 | 80 | 72 | 68.6171 | 378000 | 169000 | 25 | 13500 | 4132.1732 |  | 1
75 | 80 | 67 | 51.5724 | 343000 | 231000 | 24 | 13500 | 3944.6313 |  | 1
75 | 80 | 62 | 36.2232 | 314000 | 287000 | 23.1 | 13500 | 3944.6313 |  | 1
75 | 80 | 57 | 22.3618 | 304000 | 304000 | 22.8 | 13500 | 3944.6313 |  | 1
75 | 80 | 75 | 79.7527 | 309000 | 309000 | 22.9 | 15000 | 5146.9832 |  | 1
75 | 80 | 72 | 68.6171 | 411000 | 142000 | 26.1 | 15000 | 5542.905 |  | 1
75 | 80 | 67 | 51.5724 | 385000 | 179000 | 25.2 | 15000 | 5338.6927 |  | 1
75 | 80 | 62 | 36.2232 | 348000 | 246000 | 24.1 | 15000 | 5146.9832 |  | 1
75 | 80 | 57 | 22.3618 | 319000 | 299000 | 23.2 | 15000 | 5146.9832 |  | 1
85 | 80 | 75 | 79.7527 | 363000 | 100000 | 27.4 | 12000 | 3148.6201 |  | 1
85 | 80 | 72 | 68.6171 | 342000 | 134000 | 26.7 | 12000 | 2961.0782 |  | 1
85 | 80 | 67 | 51.5724 | 311000 | 193000 | 25.8 | 12000 | 2961.0782 |  | 1
85 | 80 | 62 | 36.2232 | 274000 | 274000 | 24.6 | 12000 | 2867.3073 |  | 1
85 | 80 | 57 | 22.3618 | 285000 | 255000 | 24.9 | 12000 | 2961.0782 |  | 1
85 | 80 | 75 | 79.7527 | 368000 | 105000 | 27.6 | 13500 | 4132.1732 |  | 1
85 | 80 | 72 | 68.6171 | 348000 | 143000 | 27 | 13500 | 3944.6313 |  | 1
85 | 80 | 67 | 51.5724 | 316000 | 208000 | 26 | 13500 | 3944.6313 |  | 1
85 | 80 | 62 | 36.2232 | 290000 | 263000 | 25.1 | 13500 | 3944.6313 |  | 1
85 | 80 | 57 | 22.3618 | 282000 | 282000 | 24.9 | 13500 | 3944.6313 |  | 1
85 | 80 | 75 | 79.7527 | 374000 | 112000 | 27.9 | 15000 | 5338.6927 |  | 1
85 | 80 | 72 | 68.6171 | 352000 | 152000 | 27.1 | 15000 | 5338.6927 |  | 1
85 | 80 | 67 | 51.5724 | 321000 | 222000 | 26.1 | 15000 | 5146.9832 |  | 1
85 | 80 | 62 | 36.2232 | 296000 | 276000 | 25.3 | 15000 | 5146.9832 |  | 1
85 | 80 | 57 | 22.3618 | 290000 | 290000 | 25.1 | 15000 | 5146.9832 |  | 1
95 | 80 | 75 | 79.7527 | 331000 | 74000 | 29.6 | 12000 | 2961.0782 |  | 1
95 | 80 | 72 | 68.6171 | 313000 | 110000 | 29 | 12000 | 2961.0782 |  | 1
95 | 80 | 67 | 51.5724 | 285000 | 171000 | 28 | 12000 | 2961.0782 |  | 1
95 | 80 | 62 | 36.2232 | 262000 | 230000 | 27.3 | 12000 | 2867.3073 |  | 1
95 | 80 | 57 | 22.3618 | 253000 | 253000 | 27 | 12000 | 2867.3073 |  | 1
95 | 80 | 75 | 79.7527 | 336000 | 79000 | 29.8 | 13500 | 3944.6313 |  | 1
95 | 80 | 72 | 68.6171 | 318000 | 119000 | 29.2 | 13500 | 3944.6313 |  | 1
95 | 80 | 67 | 51.5724 | 289000 | 185000 | 28.2 | 13500 | 3944.6313 |  | 1
95 | 80 | 62 | 36.2232 | 268000 | 241000 | 27.5 | 13500 | 3850.8603 |  | 1
95 | 80 | 57 | 22.3618 | 261000 | 261000 | 27.2 | 13500 | 3850.8603 |  | 1
95 | 80 | 75 | 79.7527 | 340000 | 84000 | 30 | 15000 | 5146.9832 |  | 1
95 | 80 | 72 | 68.6171 | 321000 | 126000 | 29.3 | 15000 | 5146.9832 |  | 1
95 | 80 | 67 | 51.5724 | 292000 | 198000 | 28.3 | 15000 | 5146.9832 |  | 1
95 | 80 | 62 | 36.2232 | 272000 | 253000 | 27.6 | 15000 | 5051.1285 |  | 1
95 | 80 | 57 | 22.3618 | 267000 | 267000 | 27.5 | 15000 | 5051.1285 |  | 1
105 | 80 | 75 | 79.7527 | 301000 | 49000 | 32 | 12000 | 2961.0782 |  | 1
105 | 80 | 72 | 68.6171 | 284000 | 86000 | 31.4 | 12000 | 2961.0782 |  | 1
105 | 80 | 67 | 51.5724 | 258000 | 149000 | 30.6 | 12000 | 2867.3073 |  | 1
105 | 80 | 62 | 36.2232 | 241000 | 208000 | 30 | 12000 | 2867.3073 |  | 1
105 | 80 | 57 | 22.3618 | 233000 | 233000 | 29.7 | 12000 | 2867.3073 |  | 1
105 | 80 | 75 | 79.7527 | 304000 | 53000 | 32.2 | 13500 | 3944.6313 |  | 1
105 | 80 | 72 | 68.6171 | 287000 | 93000 | 31.6 | 13500 | 3944.6313 |  | 1
105 | 80 | 67 | 51.5724 | 261000 | 161000 | 30.7 | 13500 | 3850.8603 |  | 1
105 | 80 | 62 | 36.2232 | 245000 | 219000 | 30.1 | 13500 | 3850.8603 |  | 1
105 | 80 | 57 | 22.3618 | 239000 | 239000 | 29.9 | 13500 | 3850.8603 |  | 1
105 | 80 | 75 | 79.7527 | 307000 | 57000 | 32.4 | 15000 | 5146.9832 |  | 1
105 | 80 | 72 | 68.6171 | 289000 | 100000 | 31.7 | 15000 | 5146.9832 |  | 1
105 | 80 | 67 | 51.5724 | 263000 | 174000 | 30.8 | 15000 | 5051.1285 |  | 1
105 | 80 | 62 | 36.2232 | 249000 | 230000 | 30.2 | 15000 | 5051.1285 |  | 1
105 | 80 | 57 | 22.3618 | 244000 | 244000 | 30.1 | 15000 | 5051.1285 |  | 1
115 | 80 | 75 | 79.7527 | 268000 | 24000 | 34.7 | 12000 | 2867.3073 |  | 1
115 | 80 | 72 | 68.6171 | 253000 | 62000 | 34.1 | 12000 | 2867.3073 |  | 1
115 | 80 | 67 | 51.5724 | 231000 | 127000 | 33.4 | 12000 | 2867.3073 |  | 1
115 | 80 | 62 | 36.2232 | 218000 | 186000 | 32.9 | 12000 | 2867.3073 |  | 1
115 | 80 | 57 | 22.3618 | 211000 | 211000 | 32.7 | 12000 | 2867.3073 |  | 1
115 | 80 | 75 | 79.7527 | 271000 | 26000 | 34.8 | 13500 | 3850.8603 |  | 1
115 | 80 | 72 | 68.6171 | 255000 | 68000 | 34.3 | 13500 | 3850.8603 |  | 1
115 | 80 | 67 | 51.5724 | 233000 | 139000 | 33.5 | 13500 | 3850.8603 |  | 1
115 | 80 | 62 | 36.2232 | 222000 | 197000 | 33 | 13500 | 3850.8603 |  | 1
115 | 80 | 57 | 22.3618 | 216000 | 216000 | 32.9 | 13500 | 3850.8603 |  | 1
115 | 80 | 75 | 79.7527 | 273000 | 29000 | 34.9 | 15000 | 5051.1285 |  | 1
115 | 80 | 72 | 68.6171 | 257000 | 74000 | 34.3 | 15000 | 5051.1285 |  | 1
115 | 80 | 67 | 51.5724 | 234000 | 150000 | 33.6 | 15000 | 5051.1285 |  | 1
115 | 80 | 62 | 36.2232 | 224000 | 207000 | 33.1 | 15000 | 5051.1285 |  | 1
115 | 80 | 57 | 22.3618 | 221000 | 221000 | 33 | 15000 | 5051.1285 |  | 1
75 | 80 | 75 | 79.7527 | 353000 | 98000 | 24.1 | 6000 | 983.5531 |  | 2
75 | 80 | 72 | 68.6171 | 332000 | 119000 | 23.5 | 6000 | 833.5196 |  | 2
75 | 80 | 67 | 51.5724 | 300000 | 153000 | 22.6 | 6000 | 833.5196 |  | 2
75 | 80 | 62 | 36.2232 | 272000 | 188000 | 22 | 6000 | 758.5028 |  | 2
75 | 80 | 57 | 22.3618 | 249000 | 225000 | 21.4 | 6000 | 758.5028 |  | 2
75 | 80 | 75 | 79.7527 | 374000 | 106000 | 24.8 | 7500 | 1316.9609 |  | 2
75 | 80 | 72 | 68.6171 | 351000 | 131000 | 24.1 | 7500 | 1316.9609 |  | 2
75 | 80 | 67 | 51.5724 | 318000 | 171000 | 23.2 | 7500 | 1150.257 |  | 2
75 | 80 | 62 | 36.2232 | 288000 | 214000 | 22.4 | 7500 | 1150.257 |  | 2
75 | 80 | 57 | 22.3618 | 268000 | 252000 | 21.8 | 7500 | 1066.905 |  | 2
75 | 80 | 75 | 79.7527 | 389000 | 114000 | 25.3 | 9000 | 1762.8939 |  | 2
75 | 80 | 72 | 68.6171 | 365000 | 142000 | 24.6 | 9000 | 1762.8939 |  | 2
75 | 80 | 67 | 51.5724 | 330000 | 190000 | 23.6 | 9000 | 1587.8547 |  | 2
75 | 80 | 62 | 36.2232 | 300000 | 239000 | 22.7 | 9000 | 1587.8547 |  | 2
75 | 80 | 57 | 22.3618 | 282000 | 275000 | 22.2 | 9000 | 1587.8547 |  | 2
75 | 80 | 75 | 79.7527 | 398000 | 121000 | 25.6 | 10500 | 2369.2793 |  | 2
75 | 80 | 72 | 68.6171 | 377000 | 155000 | 25 | 10500 | 2369.2793 |  | 2
75 | 80 | 67 | 51.5724 | 340000 | 208000 | 23.9 | 10500 | 2190.0726 |  | 2
75 | 80 | 62 | 36.2232 | 309000 | 262000 | 23 | 10500 | 2190.0726 |  | 2
75 | 80 | 57 | 22.3618 | 292000 | 292000 | 22.5 | 10500 | 2190.0726 |  | 2
85 | 80 | 75 | 79.7527 | 329000 | 78000 | 26.2 | 6000 | 833.5196 |  | 2
85 | 80 | 72 | 68.6171 | 310000 | 100000 | 25.6 | 6000 | 833.5196 |  | 2
85 | 80 | 67 | 51.5724 | 280000 | 136000 | 24.8 | 6000 | 758.5028 |  | 2
85 | 80 | 62 | 36.2232 | 254000 | 172000 | 24.2 | 6000 | 758.5028 |  | 2
85 | 80 | 57 | 22.3618 | 233000 | 211000 | 23.7 | 6000 | 758.5028 |  | 2
85 | 80 | 75 | 79.7527 | 346000 | 83000 | 26.8 | 7500 | 1150.257 |  | 2
85 | 80 | 72 | 68.6171 | 326000 | 109000 | 26.2 | 7500 | 1150.257 |  | 2
85 | 80 | 67 | 51.5724 | 294000 | 151000 | 25.2 | 7500 | 1150.257 |  | 2
85 | 80 | 62 | 36.2232 | 267000 | 196000 | 24.5 | 7500 | 1066.905 |  | 2
85 | 80 | 57 | 22.3618 | 251000 | 236000 | 24 | 7500 | 1066.905 |  | 2
85 | 80 | 75 | 79.7527 | 359000 | 90000 | 27.3 | 9000 | 1762.8939 |  | 2
85 | 80 | 72 | 68.6171 | 337000 | 119000 | 26.6 | 9000 | 1587.8547 |  | 2
85 | 80 | 67 | 51.5724 | 305000 | 168000 | 25.6 | 9000 | 1587.8547 |  | 2
85 | 80 | 62 | 36.2232 | 277000 | 219000 | 24.8 | 9000 | 1500.3352 |  | 2
85 | 80 | 57 | 22.3618 | 263000 | 257000 | 24.3 | 9000 | 1500.3352 |  | 2
85 | 80 | 75 | 79.7527 | 369000 | 97000 | 27.6 | 10500 | 2369.2793 |  | 2
85 | 80 | 72 | 68.6171 | 346000 | 129000 | 26.9 | 10500 | 2190.0726 |  | 2
85 | 80 | 67 | 51.5724 | 313000 | 185000 | 25.9 | 10500 | 2190.0726 |  | 2
85 | 80 | 62 | 36.2232 | 285000 | 241000 | 25 | 10500 | 2190.0726 |  | 2
85 | 80 | 57 | 22.3618 | 272000 | 272000 | 24.6 | 10500 | 2100.4693 |  | 2
95 | 80 | 75 | 79.7527 | 306000 | 59000 | 28.6 | 6000 | 833.5196 |  | 2
95 | 80 | 72 | 68.6171 | 287000 | 81000 | 28 | 6000 | 833.5196 |  | 2
95 | 80 | 67 | 51.5724 | 259000 | 118000 | 27.3 | 6000 | 758.5028 |  | 2
95 | 80 | 62 | 36.2232 | 234000 | 155000 | 26.7 | 6000 | 758.5028 |  | 2
95 | 80 | 57 | 22.3618 | 219000 | 198000 | 26.3 | 6000 | 758.5028 |  | 2
95 | 80 | 75 | 79.7527 | 319000 | 61000 | 29.1 | 7500 | 1150.257 |  | 2
95 | 80 | 72 | 68.6171 | 300000 | 87000 | 28.5 | 7500 | 1150.257 |  | 2
95 | 80 | 67 | 51.5724 | 271000 | 131000 | 27.6 | 7500 | 1066.905 |  | 2
95 | 80 | 62 | 36.2232 | 246000 | 177000 | 27 | 7500 | 1066.905 |  | 2
95 | 80 | 57 | 22.3618 | 234000 | 219000 | 26.6 | 7500 | 1066.905 |  | 2
95 | 80 | 75 | 79.7527 | 329000 | 65000 | 29.5 | 9000 | 1587.8547 |  | 2
95 | 80 | 72 | 68.6171 | 309000 | 95000 | 28.8 | 9000 | 1587.8547 |  | 2
95 | 80 | 67 | 51.5724 | 279000 | 146000 | 27.9 | 9000 | 1500.3352 |  | 2
95 | 80 | 62 | 36.2232 | 254000 | 199000 | 27.2 | 9000 | 1500.3352 |  | 2
95 | 80 | 57 | 22.3618 | 244000 | 238000 | 26.8 | 9000 | 1500.3352 |  | 2
95 | 80 | 75 | 79.7527 | 337000 | 70000 | 29.8 | 10500 | 2190.0726 |  | 2
95 | 80 | 72 | 68.6171 | 317000 | 104000 | 29.1 | 10500 | 2190.0726 |  | 2
95 | 80 | 67 | 51.5724 | 286000 | 162000 | 28.1 | 10500 | 2190.0726 |  | 2
95 | 80 | 62 | 36.2232 | 261000 | 220000 | 27.4 | 10500 | 2100.4693 |  | 2
95 | 80 | 57 | 22.3618 | 251000 | 251000 | 27.1 | 10500 | 2100.4693 |  | 2
105 | 80 | 75 | 79.7527 | 281000 | 39000 | 31.2 | 6000 | 833.5196 |  | 2
105 | 80 | 72 | 68.6171 | 264000 | 62000 | 30.7 | 6000 | 758.5028 |  | 2
105 | 80 | 67 | 51.5724 | 238000 | 101000 | 30.1 | 6000 | 758.5028 |  | 2
105 | 80 | 62 | 36.2232 | 215000 | 140000 | 29.5 | 6000 | 758.5028 |  | 2
105 | 80 | 57 | 22.3618 | 204000 | 183000 | 29.2 | 6000 | 691.8212 |  | 2
105 | 80 | 75 | 79.7527 | 291000 | 38000 | 31.7 | 7500 | 1150.257 |  | 2
105 | 80 | 72 | 68.6171 | 273000 | 65000 | 31.1 | 7500 | 1066.905 |  | 2
105 | 80 | 67 | 51.5724 | 247000 | 112000 | 30.3 | 7500 | 1066.905 |  | 2
105 | 80 | 62 | 36.2232 | 224000 | 160000 | 29.7 | 7500 | 1066.905 |  | 2
105 | 80 | 57 | 22.3618 | 216000 | 202000 | 29.4 | 7500 | 1066.905 |  | 2
105 | 80 | 75 | 79.7527 | 299000 | 40000 | 32 | 9000 | 1587.8547 |  | 2
105 | 80 | 72 | 68.6171 | 280000 | 71000 | 31.4 | 9000 | 1500.3352 |  | 2
105 | 80 | 67 | 51.5724 | 253000 | 124000 | 30.5 | 9000 | 1500.3352 |  | 2
105 | 80 | 62 | 36.2232 | 231000 | 180000 | 29.9 | 9000 | 1500.3352 |  | 2
105 | 80 | 57 | 22.3618 | 225000 | 219000 | 29.6 | 9000 | 1500.3352 |  | 2
105 | 80 | 75 | 79.7527 | 305000 | 44000 | 32.3 | 10500 | 2190.0726 |  | 2
105 | 80 | 72 | 68.6171 | 286000 | 79000 | 31.6 | 10500 | 2190.0726 |  | 2
105 | 80 | 67 | 51.5724 | 257000 | 138000 | 30.7 | 10500 | 2100.4693 |  | 2
105 | 80 | 62 | 36.2232 | 239000 | 200000 | 30.1 | 10500 | 2100.4693 |  | 2
105 | 80 | 57 | 22.3618 | 229000 | 229000 | 29.8 | 10500 | 2100.4693 |  | 2
115 | 80 | 75 | 79.7527 | 256000 | 19000 | 34.2 | 6000 | 758.5028 |  | 2
115 | 80 | 72 | 68.6171 | 240000 | 43000 | 33.8 | 6000 | 758.5028 |  | 2
115 | 80 | 67 | 51.5724 | 216000 | 84000 | 33.2 | 6000 | 758.5028 |  | 2
115 | 80 | 62 | 36.2232 | 195000 | 124000 | 32.9 | 6000 | 691.8212 |  | 2
115 | 80 | 57 | 22.3618 | 188000 | 168000 | 32.8 | 6000 | 691.8212 |  | 2
115 | 80 | 75 | 79.7527 | 263000 | 15000 | 34.5 | 7500 | 1066.905 |  | 2
115 | 80 | 72 | 68.6171 | 246000 | 44000 | 34 | 7500 | 1066.905 |  | 2
115 | 80 | 67 | 51.5724 | 222000 | 92000 | 33.3 | 7500 | 1066.905 |  | 2
115 | 80 | 62 | 36.2232 | 202000 | 142000 | 32.9 | 7500 | 996.0559 |  | 2
115 | 80 | 57 | 22.3618 | 198000 | 185000 | 32.7 | 7500 | 996.0559 |  | 2
115 | 80 | 75 | 79.7527 | 267000 | 15000 | 34.7 | 9000 | 1500.3352 |  | 2
115 | 80 | 72 | 68.6171 | 251000 | 47000 | 34.2 | 9000 | 1500.3352 |  | 2
115 | 80 | 67 | 51.5724 | 226000 | 103000 | 33.4 | 9000 | 1500.3352 |  | 2
115 | 80 | 62 | 36.2232 | 208000 | 162000 | 32.9 | 9000 | 1429.486 |  | 2
115 | 80 | 57 | 22.3618 | 205000 | 200000 | 32.8 | 9000 | 1429.486 |  | 2
115 | 80 | 75 | 79.7527 | 271000 | 17000 | 34.9 | 10500 | 2100.4693 |  | 2
115 | 80 | 72 | 68.6171 | 254000 | 53000 | 34.3 | 10500 | 2100.4693 |  | 2
115 | 80 | 67 | 51.5724 | 229000 | 115000 | 33.6 | 10500 | 2100.4693 |  | 2
115 | 80 | 62 | 36.2232 | 216000 | 177000 | 33.1 | 10500 | 2100.4693 |  | 2
115 | 80 | 57 | 22.3618 | 207000 | 207000 | 32.9 | 10500 | 2025.4525 |  | 2
75 | 80 | 75 | 79.7527 | 396000 | 123000 | 25.5 | 12000 | 3148.6201 |  | 2
75 | 80 | 72 | 68.6171 | 386000 | 167000 | 25.3 | 12000 | 3148.6201 |  | 2
75 | 80 | 67 | 51.5724 | 348000 | 226000 | 24.2 | 12000 | 2961.0782 |  | 2
75 | 80 | 62 | 36.2232 | 316000 | 282000 | 23.2 | 12000 | 2961.0782 |  | 2
75 | 80 | 57 | 22.3618 | 305000 | 305000 | 22.9 | 12000 | 2961.0782 |  | 2
75 | 80 | 75 | 79.7527 | 405000 | 130000 | 25.6 | 13500 | 4332.2179 |  | 2
75 | 80 | 72 | 68.6171 | 388000 | 174000 | 25.4 | 13500 | 4132.1732 |  | 2
75 | 80 | 67 | 51.5724 | 355000 | 245000 | 24.4 | 13500 | 4132.1732 |  | 2
75 | 80 | 62 | 36.2232 | 324000 | 298000 | 23.4 | 13500 | 3944.6313 |  | 2
75 | 80 | 57 | 22.3618 | 316000 | 316000 | 23.2 | 13500 | 3944.6313 |  | 2
75 | 80 | 75 | 79.7527 | 409000 | 132000 | 25.8 | 15000 | 5542.905 |  | 2
75 | 80 | 72 | 68.6171 | 401000 | 192000 | 25.8 | 15000 | 5542.905 |  | 2
75 | 80 | 67 | 51.5724 | 361000 | 263000 | 24.6 | 15000 | 5338.6927 |  | 2
75 | 80 | 62 | 36.2232 | 331000 | 314000 | 23.7 | 15000 | 5146.9832 |  | 2
75 | 80 | 57 | 22.3618 | 326000 | 326000 | 23.5 | 15000 | 5146.9832 |  | 2
85 | 80 | 75 | 79.7527 | 375000 | 102000 | 27.9 | 12000 | 3148.6201 |  | 2
85 | 80 | 72 | 68.6171 | 354000 | 140000 | 27.2 | 12000 | 3148.6201 |  | 2
85 | 80 | 67 | 51.5724 | 319000 | 202000 | 26.1 | 12000 | 2961.0782 |  | 2
85 | 80 | 62 | 36.2232 | 293000 | 258000 | 25.2 | 12000 | 2961.0782 |  | 2
85 | 80 | 57 | 22.3618 | 282000 | 282000 | 24.9 | 12000 | 2961.0782 |  | 2
85 | 80 | 75 | 79.7527 | 383000 | 111000 | 28.2 | 13500 | 4132.1732 |  | 2
85 | 80 | 72 | 68.6171 | 359000 | 151000 | 27.4 | 13500 | 4132.1732 |  | 2
85 | 80 | 67 | 51.5724 | 325000 | 219000 | 26.3 | 13500 | 3944.6313 |  | 2
85 | 80 | 62 | 36.2232 | 300000 | 273000 | 25.5 | 13500 | 3944.6313 |  | 2
85 | 80 | 57 | 22.3618 | 292000 | 292000 | 25.2 | 13500 | 3944.6313 |  | 2
85 | 80 | 75 | 79.7527 | 389000 | 114000 | 28.4 | 15000 | 5338.6927 |  | 2
85 | 80 | 72 | 68.6171 | 365000 | 162000 | 27.6 | 15000 | 5338.6927 |  | 2
85 | 80 | 67 | 51.5724 | 329000 | 235000 | 26.5 | 15000 | 5146.9832 |  | 2
85 | 80 | 62 | 36.2232 | 306000 | 289000 | 25.7 | 15000 | 5146.9832 |  | 2
85 | 80 | 57 | 22.3618 | 300000 | 300000 | 25.5 | 15000 | 5146.9832 |  | 2
95 | 80 | 75 | 79.7527 | 343000 | 76000 | 30.1 | 12000 | 2961.0782 |  | 2
95 | 80 | 72 | 68.6171 | 322000 | 114000 | 29.4 | 12000 | 2961.0782 |  | 2
95 | 80 | 67 | 51.5724 | 291000 | 177000 | 28.3 | 12000 | 2961.0782 |  | 2
95 | 80 | 62 | 36.2232 | 269000 | 235000 | 27.6 | 12000 | 2867.3073 |  | 2
95 | 80 | 57 | 22.3618 | 260000 | 260000 | 27.3 | 12000 | 2867.3073 |  | 2
95 | 80 | 75 | 79.7527 | 348000 | 82000 | 30.3 | 13500 | 3944.6313 |  | 2
95 | 80 | 72 | 68.6171 | 327000 | 123000 | 29.6 | 13500 | 3944.6313 |  | 2
95 | 80 | 67 | 51.5724 | 295000 | 193000 | 28.5 | 13500 | 3944.6313 |  | 2
95 | 80 | 62 | 36.2232 | 275000 | 249000 | 27.8 | 13500 | 3850.8603 |  | 2
95 | 80 | 57 | 22.3618 | 268000 | 268000 | 27.6 | 13500 | 3850.8603 |  | 2
95 | 80 | 75 | 79.7527 | 352000 | 88000 | 30.5 | 15000 | 5338.6927 |  | 2
95 | 80 | 72 | 68.6171 | 331000 | 133000 | 29.7 | 15000 | 5146.9832 |  | 2
95 | 80 | 67 | 51.5724 | 298000 | 208000 | 28.6 | 15000 | 5146.9832 |  | 2
95 | 80 | 62 | 36.2232 | 279000 | 263000 | 27.9 | 15000 | 5051.1285 |  | 2
95 | 80 | 57 | 22.3618 | 275000 | 275000 | 27.8 | 15000 | 5051.1285 |  | 2
105 | 80 | 75 | 79.7527 | 310000 | 48000 | 32.5 | 12000 | 2961.0782 |  | 2
105 | 80 | 72 | 68.6171 | 290000 | 87000 | 31.8 | 12000 | 2961.0782 |  | 2
105 | 80 | 67 | 51.5724 | 261000 | 153000 | 30.8 | 12000 | 2867.3073 |  | 2
105 | 80 | 62 | 36.2232 | 245000 | 212000 | 30.2 | 12000 | 2867.3073 |  | 2
105 | 80 | 57 | 22.3618 | 237000 | 237000 | 30 | 12000 | 2867.3073 |  | 2
105 | 80 | 75 | 79.7527 | 313000 | 53000 | 32.7 | 13500 | 3944.6313 |  | 2
105 | 80 | 72 | 68.6171 | 293000 | 95000 | 32 | 13500 | 3944.6313 |  | 2
105 | 80 | 67 | 51.5724 | 264000 | 167000 | 31 | 13500 | 3850.8603 |  | 2
105 | 80 | 62 | 36.2232 | 250000 | 225000 | 30.4 | 13500 | 3850.8603 |  | 2
105 | 80 | 57 | 22.3618 | 243000 | 243000 | 30.2 | 13500 | 3850.8603 |  | 2
105 | 80 | 75 | 79.7527 | 317000 | 59000 | 32.8 | 15000 | 5146.9832 |  | 2
105 | 80 | 72 | 68.6171 | 297000 | 105000 | 32.1 | 15000 | 5146.9832 |  | 2
105 | 80 | 67 | 51.5724 | 267000 | 181000 | 31.1 | 15000 | 5051.1285 |  | 2
105 | 80 | 62 | 36.2232 | 253000 | 238000 | 30.5 | 15000 | 5051.1285 |  | 2
105 | 80 | 57 | 22.3618 | 249000 | 249000 | 30.4 | 15000 | 5051.1285 |  | 2
115 | 80 | 75 | 79.7527 | 275000 | 20000 | 35.1 | 12000 | 2867.3073 |  | 2
115 | 80 | 72 | 68.6171 | 257000 | 59000 | 34.5 | 12000 | 2867.3073 |  | 2
115 | 80 | 67 | 51.5724 | 231000 | 129000 | 33.7 | 12000 | 2867.3073 |  | 2
115 | 80 | 62 | 36.2232 | 221000 | 189000 | 33.2 | 12000 | 2867.3073 |  | 2
115 | 80 | 57 | 22.3618 | 213000 | 213000 | 33 | 12000 | 2867.3073 |  | 2
115 | 80 | 75 | 79.7527 | 277000 | 23000 | 35.2 | 13500 | 3850.8603 |  | 2
115 | 80 | 72 | 68.6171 | 259000 | 67000 | 34.6 | 13500 | 3850.8603 |  | 2
115 | 80 | 67 | 51.5724 | 234000 | 142000 | 33.7 | 13500 | 3850.8603 |  | 2
115 | 80 | 62 | 36.2232 | 224000 | 201000 | 33.3 | 13500 | 3850.8603 |  | 2
115 | 80 | 57 | 22.3618 | 218000 | 218000 | 33.2 | 13500 | 3850.8603 |  | 2
115 | 80 | 75 | 79.7527 | 279000 | 28000 | 35.4 | 15000 | 5051.1285 |  | 2
115 | 80 | 72 | 68.6171 | 261000 | 75000 | 34.7 | 15000 | 5051.1285 |  | 2
115 | 80 | 67 | 51.5724 | 235000 | 156000 | 33.8 | 15000 | 5051.1285 |  | 2
115 | 80 | 62 | 36.2232 | 227000 | 212000 | 33.4 | 15000 | 5051.1285 |  | 2
115 | 80 | 57 | 22.3618 | 223000 | 223000 | 33.3 | 15000 | 5051.1285 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 10
Degradation Coefficient (C_d) |  | 48/50 035 (35 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 388000 | 112000 | 26.3 | 7000 | 63710.067 |  | 1
75 | 80 | 72 | 68.6171 | 364000 | 134000 | 25.6 | 7000 | 63710.067 |  | 1
75 | 80 | 67 | 51.5724 | 328000 | 172000 | 24.5 | 7000 | 188496.2793 |  | 1
75 | 80 | 62 | 36.2232 | 297000 | 211000 | 23.7 | 7000 | 188496.2793 |  | 1
75 | 80 | 57 | 22.3618 | 270000 | 249000 | 23 | 7000 | 250889.3855 |  | 1
75 | 80 | 75 | 79.7527 | 410000 | 123000 | 27 | 8750 | 87650.8324 |  | 1
75 | 80 | 72 | 68.6171 | 385000 | 149000 | 26.2 | 8750 | 69780.1732 |  | 1
75 | 80 | 67 | 51.5724 | 346000 | 194000 | 25.1 | 8750 | 205589.6816 |  | 1
75 | 80 | 62 | 36.2232 | 313000 | 241000 | 24.2 | 8750 | 205589.6816 |  | 1
75 | 80 | 57 | 22.3618 | 290000 | 281000 | 23.5 | 8750 | 205589.6816 |  | 1
75 | 80 | 75 | 79.7527 | 413000 | 124000 | 27.2 | 9625 | 89801.3128 |  | 1
75 | 80 | 72 | 68.6171 | 393000 | 157000 | 26.5 | 9625 | 73210.1061 |  | 1
75 | 80 | 67 | 51.5724 | 354000 | 206000 | 25.3 | 9625 | 73210.1061 |  | 1
75 | 80 | 62 | 36.2232 | 319000 | 255000 | 24.3 | 9625 | 215246.0056 |  | 1
75 | 80 | 57 | 22.3618 | 297000 | 294000 | 23.7 | 9625 | 215246.0056 |  | 1
75 | 80 | 75 | 79.7527 | 419000 | 127000 | 27.3 | 10500 | 92485.2458 |  | 1
75 | 80 | 72 | 68.6171 | 401000 | 165000 | 26.8 | 10500 | 92485.2458 |  | 1
75 | 80 | 67 | 51.5724 | 360000 | 217000 | 25.6 | 10500 | 76960.9441 |  | 1
75 | 80 | 62 | 36.2232 | 325000 | 270000 | 24.5 | 10500 | 225698.3408 |  | 1
75 | 80 | 57 | 22.3618 | 304000 | 304000 | 23.9 | 10500 | 225698.3408 |  | 1
85 | 80 | 75 | 79.7527 | 360000 | 88000 | 28.4 | 7000 | 63710.067 |  | 1
85 | 80 | 72 | 68.6171 | 337000 | 112000 | 27.7 | 7000 | 188496.2793 |  | 1
85 | 80 | 67 | 51.5724 | 304000 | 151000 | 26.7 | 7000 | 188496.2793 |  | 1
85 | 80 | 62 | 36.2232 | 275000 | 192000 | 25.9 | 7000 | 250889.3855 |  | 1
85 | 80 | 57 | 22.3618 | 251000 | 233000 | 25.3 | 7000 | 250889.3855 |  | 1
85 | 80 | 75 | 79.7527 | 378000 | 97000 | 29.1 | 8750 | 69780.1732 |  | 1
85 | 80 | 72 | 68.6171 | 355000 | 125000 | 28.3 | 8750 | 69780.1732 |  | 1
85 | 80 | 67 | 51.5724 | 319000 | 171000 | 27.2 | 8750 | 205589.6816 |  | 1
85 | 80 | 62 | 36.2232 | 289000 | 220000 | 26.3 | 8750 | 205589.6816 |  | 1
85 | 80 | 57 | 22.3618 | 270000 | 261000 | 25.7 | 8750 | 273494.4358 |  | 1
85 | 80 | 75 | 79.7527 | 386000 | 102000 | 29.4 | 9625 | 73210.1061 |  | 1
85 | 80 | 72 | 68.6171 | 362000 | 131000 | 28.6 | 9625 | 73210.1061 |  | 1
85 | 80 | 67 | 51.5724 | 325000 | 181000 | 27.4 | 9625 | 215246.0056 |  | 1
85 | 80 | 62 | 36.2232 | 294000 | 234000 | 26.5 | 9625 | 215246.0056 |  | 1
85 | 80 | 57 | 22.3618 | 276000 | 273000 | 25.9 | 9625 | 286263.9553 |  | 1
85 | 80 | 75 | 79.7527 | 392000 | 106000 | 29.6 | 10500 | 76960.9441 |  | 1
85 | 80 | 72 | 68.6171 | 368000 | 138000 | 28.8 | 10500 | 76960.9441 |  | 1
85 | 80 | 67 | 51.5724 | 330000 | 192000 | 27.6 | 10500 | 225698.3408 |  | 1
85 | 80 | 62 | 36.2232 | 299000 | 247000 | 26.6 | 10500 | 225698.3408 |  | 1
85 | 80 | 57 | 22.3618 | 282000 | 282000 | 26.1 | 10500 | 225698.3408 |  | 1
95 | 80 | 75 | 79.7527 | 331000 | 65000 | 30.8 | 7000 | 188496.2793 |  | 1
95 | 80 | 72 | 68.6171 | 311000 | 89000 | 30.1 | 7000 | 188496.2793 |  | 1
95 | 80 | 67 | 51.5724 | 280000 | 130000 | 29.1 | 7000 | 250889.3855 |  | 1
95 | 80 | 62 | 36.2232 | 253000 | 173000 | 28.4 | 7000 | 250889.3855 |  | 1
95 | 80 | 57 | 22.3618 | 235000 | 218000 | 27.9 | 7000 | 250889.3855 |  | 1
95 | 80 | 75 | 79.7527 | 346000 | 71000 | 31.4 | 8750 | 205589.6816 |  | 1
95 | 80 | 72 | 68.6171 | 324000 | 99000 | 30.7 | 8750 | 205589.6816 |  | 1
95 | 80 | 67 | 51.5724 | 292000 | 148000 | 29.6 | 8750 | 205589.6816 |  | 1
95 | 80 | 62 | 36.2232 | 265000 | 199000 | 28.8 | 8750 | 273494.4358 |  | 1
95 | 80 | 57 | 22.3618 | 250000 | 242000 | 28.3 | 8750 | 273494.4358 |  | 1
95 | 80 | 75 | 79.7527 | 352000 | 74000 | 31.7 | 9625 | 73210.1061 |  | 1
95 | 80 | 72 | 68.6171 | 330000 | 105000 | 30.9 | 9625 | 215246.0056 |  | 1
95 | 80 | 67 | 51.5724 | 297000 | 157000 | 29.8 | 9625 | 215246.0056 |  | 1
95 | 80 | 62 | 36.2232 | 269000 | 212000 | 28.9 | 9625 | 286263.9553 |  | 1
95 | 80 | 57 | 22.3618 | 255000 | 253000 | 28.4 | 9625 | 286263.9553 |  | 1
95 | 80 | 75 | 79.7527 | 357000 | 78000 | 31.9 | 10500 | 76960.9441 |  | 1
95 | 80 | 72 | 68.6171 | 335000 | 111000 | 31.1 | 10500 | 225698.3408 |  | 1
95 | 80 | 67 | 51.5724 | 302000 | 167000 | 30 | 10500 | 225698.3408 |  | 1
95 | 80 | 62 | 36.2232 | 273000 | 224000 | 29.1 | 10500 | 300067.0391 |  | 1
95 | 80 | 57 | 22.3618 | 259000 | 259000 | 28.6 | 10500 | 300067.0391 |  | 1
105 | 80 | 75 | 79.7527 | 303000 | 42000 | 33.5 | 7000 | 188496.2793 |  | 1
105 | 80 | 72 | 68.6171 | 284000 | 67000 | 32.8 | 7000 | 188496.2793 |  | 1
105 | 80 | 67 | 51.5724 | 256000 | 110000 | 32 | 7000 | 250889.3855 |  | 1
105 | 80 | 62 | 36.2232 | 230000 | 154000 | 31.3 | 7000 | 250889.3855 |  | 1
105 | 80 | 57 | 22.3618 | 217000 | 200000 | 30.9 | 7000 | 250889.3855 |  | 1
105 | 80 | 75 | 79.7527 | 314000 | 44000 | 34 | 8750 | 205589.6816 |  | 1
105 | 80 | 72 | 68.6171 | 294000 | 74000 | 33.3 | 8750 | 205589.6816 |  | 1
105 | 80 | 67 | 51.5724 | 265000 | 125000 | 32.3 | 8750 | 273494.4358 |  | 1
105 | 80 | 62 | 36.2232 | 240000 | 178000 | 31.6 | 8750 | 273494.4358 |  | 1
105 | 80 | 57 | 22.3618 | 229000 | 222000 | 31.2 | 8750 | 273494.4358 |  | 1
105 | 80 | 75 | 79.7527 | 318000 | 47000 | 34.2 | 9625 | 215246.0056 |  | 1
105 | 80 | 72 | 68.6171 | 298000 | 78000 | 33.5 | 9625 | 215246.0056 |  | 1
105 | 80 | 67 | 51.5724 | 269000 | 133000 | 32.5 | 9625 | 286263.9553 |  | 1
105 | 80 | 62 | 36.2232 | 244000 | 190000 | 31.7 | 9625 | 286263.9553 |  | 1
105 | 80 | 57 | 22.3618 | 225000 | 223000 | 31.2 | 9625 | 286263.9553 |  | 1
105 | 80 | 75 | 79.7527 | 322000 | 49000 | 34.4 | 10500 | 225698.3408 |  | 1
105 | 80 | 72 | 68.6171 | 301000 | 83000 | 33.7 | 10500 | 225698.3408 |  | 1
105 | 80 | 67 | 51.5724 | 272000 | 142000 | 32.6 | 10500 | 300067.0391 |  | 1
105 | 80 | 62 | 36.2232 | 247000 | 202000 | 31.8 | 10500 | 300067.0391 |  | 1
105 | 80 | 57 | 22.3618 | 236000 | 236000 | 31.5 | 10500 | 300067.0391 |  | 1
115 | 80 | 75 | 79.7527 | 274000 | 18000 | 36.5 | 7000 | 250889.3855 |  | 1
115 | 80 | 72 | 68.6171 | 256000 | 45000 | 35.9 | 7000 | 250889.3855 |  | 1
115 | 80 | 67 | 51.5724 | 230000 | 90000 | 35.2 | 7000 | 250889.3855 |  | 1
115 | 80 | 62 | 36.2232 | 207000 | 135000 | 34.6 | 7000 | 239428.4916 |  | 1
115 | 80 | 57 | 22.3618 | 188000 | 172000 | 34 | 7000 | 239428.4916 |  | 1
115 | 80 | 75 | 79.7527 | 281000 | 18000 | 36.9 | 8750 | 205589.6816 |  | 1
115 | 80 | 72 | 68.6171 | 263000 | 49000 | 36.3 | 8750 | 273494.4358 |  | 1
115 | 80 | 67 | 51.5724 | 237000 | 103000 | 35.4 | 8750 | 273494.4358 |  | 1
115 | 80 | 62 | 36.2232 | 216000 | 153000 | 34.8 | 8750 | 273494.4358 |  | 1
115 | 80 | 57 | 22.3618 | 198000 | 192000 | 34.3 | 8750 | 263988.1453 |  | 1
115 | 80 | 75 | 79.7527 | 284000 | 19000 | 37.1 | 9625 | 215246.0056 |  | 1
115 | 80 | 72 | 68.6171 | 266000 | 52000 | 36.4 | 9625 | 286263.9553 |  | 1
115 | 80 | 67 | 51.5724 | 239000 | 110000 | 35.5 | 9625 | 286263.9553 |  | 1
115 | 80 | 62 | 36.2232 | 207000 | 160000 | 34.7 | 9625 | 277576.5978 |  | 1
115 | 80 | 57 | 22.3618 | 199000 | 199000 | 34.4 | 9625 | 277576.5978 |  | 1
115 | 80 | 75 | 79.7527 | 287000 | 20000 | 37.2 | 10500 | 225698.3408 |  | 1
115 | 80 | 72 | 68.6171 | 269000 | 56000 | 36.5 | 10500 | 300067.0391 |  | 1
115 | 80 | 67 | 51.5724 | 237000 | 112000 | 35.5 | 10500 | 300067.0391 |  | 1
115 | 80 | 62 | 36.2232 | 210000 | 169000 | 34.8 | 10500 | 292096.5084 |  | 1
115 | 80 | 57 | 22.3618 | 200000 | 200000 | 34.5 | 10500 | 292096.5084 |  | 1
75 | 80 | 75 | 79.7527 | 435000 | 142000 | 27.9 | 12225 | 98707.4693 |  | 1
75 | 80 | 72 | 68.6171 | 407000 | 175000 | 27 | 12225 | 98707.4693 |  | 1
75 | 80 | 67 | 51.5724 | 372000 | 239000 | 25.9 | 12225 | 84979.4022 |  | 1
75 | 80 | 62 | 36.2232 | 335000 | 297000 | 24.8 | 12225 | 247853.2905 |  | 1
75 | 80 | 57 | 22.3618 | 320000 | 320000 | 24.4 | 12225 | 247853.2905 |  | 1
75 | 80 | 75 | 79.7527 | 451000 | 159000 | 28.4 | 14000 | 106123.7095 |  | 1
75 | 80 | 72 | 68.6171 | 413000 | 186000 | 27.2 | 14000 | 106123.7095 |  | 1
75 | 80 | 67 | 51.5724 | 377000 | 258000 | 26.1 | 14000 | 94246.0559 |  | 1
75 | 80 | 62 | 36.2232 | 343000 | 322000 | 25.1 | 14000 | 273136.0223 |  | 1
75 | 80 | 57 | 22.3618 | 334000 | 334000 | 24.8 | 14000 | 273136.0223 |  | 1
75 | 80 | 75 | 79.7527 | 441000 | 150000 | 28 | 15000 | 110733.0726 |  | 1
75 | 80 | 72 | 68.6171 | 427000 | 204000 | 27.6 | 15000 | 110733.0726 |  | 1
75 | 80 | 67 | 51.5724 | 381000 | 269000 | 26.2 | 15000 | 99688.9385 |  | 1
75 | 80 | 62 | 36.2232 | 349000 | 331000 | 25.3 | 15000 | 287730.9497 |  | 1
75 | 80 | 57 | 22.3618 | 342000 | 342000 | 25.1 | 15000 | 287730.9497 |  | 1
85 | 80 | 75 | 79.7527 | 402000 | 114000 | 30 | 12225 | 98707.4693 |  | 1
85 | 80 | 72 | 68.6171 | 378000 | 152000 | 29.2 | 12225 | 84979.4022 |  | 1
85 | 80 | 67 | 51.5724 | 340000 | 213000 | 27.9 | 12225 | 247853.2905 |  | 1
85 | 80 | 62 | 36.2232 | 307000 | 272000 | 26.9 | 12225 | 247853.2905 |  | 1
85 | 80 | 57 | 22.3618 | 296000 | 296000 | 26.5 | 12225 | 247853.2905 |  | 1
85 | 80 | 75 | 79.7527 | 404000 | 118000 | 30 | 14000 | 106123.7095 |  | 1
85 | 80 | 72 | 68.6171 | 386000 | 165000 | 29.5 | 14000 | 94246.0559 |  | 1
85 | 80 | 67 | 51.5724 | 347000 | 233000 | 28.2 | 14000 | 273136.0223 |  | 1
85 | 80 | 62 | 36.2232 | 315000 | 291000 | 27.2 | 14000 | 273136.0223 |  | 1
85 | 80 | 57 | 22.3618 | 307000 | 307000 | 26.9 | 14000 | 273136.0223 |  | 1
85 | 80 | 75 | 79.7527 | 420000 | 134000 | 30.6 | 15000 | 110733.0726 |  | 1
85 | 80 | 72 | 68.6171 | 391000 | 174000 | 29.7 | 15000 | 99688.9385 |  | 1
85 | 80 | 67 | 51.5724 | 350000 | 244000 | 28.3 | 15000 | 287730.9497 |  | 1
85 | 80 | 62 | 36.2232 | 320000 | 302000 | 27.3 | 15000 | 287730.9497 |  | 1
85 | 80 | 57 | 22.3618 | 314000 | 314000 | 27.1 | 15000 | 287730.9497 |  | 1
95 | 80 | 75 | 79.7527 | 366000 | 85000 | 32.3 | 12225 | 84979.4022 |  | 1
95 | 80 | 72 | 68.6171 | 343000 | 122000 | 31.4 | 12225 | 247853.2905 |  | 1
95 | 80 | 67 | 51.5724 | 308000 | 186000 | 30.2 | 12225 | 247853.2905 |  | 1
95 | 80 | 62 | 36.2232 | 277000 | 247000 | 29.2 | 12225 | 329290.2346 |  | 1
95 | 80 | 57 | 22.3618 | 271000 | 271000 | 29 | 12225 | 329290.2346 |  | 1
95 | 80 | 75 | 79.7527 | 373000 | 93000 | 32.5 | 14000 | 94246.0559 |  | 1
95 | 80 | 72 | 68.6171 | 349000 | 135000 | 31.7 | 14000 | 273136.0223 |  | 1
95 | 80 | 67 | 51.5724 | 313000 | 205000 | 30.5 | 14000 | 273136.0223 |  | 1
95 | 80 | 62 | 36.2232 | 288000 | 265000 | 29.5 | 14000 | 273136.0223 |  | 1
95 | 80 | 57 | 22.3618 | 281000 | 281000 | 29.3 | 14000 | 273136.0223 |  | 1
95 | 80 | 75 | 79.7527 | 376000 | 97000 | 32.7 | 15000 | 99688.9385 |  | 1
95 | 80 | 72 | 68.6171 | 353000 | 142000 | 31.9 | 15000 | 99688.9385 |  | 1
95 | 80 | 67 | 51.5724 | 316000 | 216000 | 30.6 | 15000 | 287730.9497 |  | 1
95 | 80 | 62 | 36.2232 | 292000 | 275000 | 29.7 | 15000 | 287730.9497 |  | 1
95 | 80 | 57 | 22.3618 | 287000 | 287000 | 29.5 | 15000 | 287730.9497 |  | 1
105 | 80 | 75 | 79.7527 | 328000 | 55000 | 34.7 | 12225 | 247853.2905 |  | 1
105 | 80 | 72 | 68.6171 | 307000 | 93000 | 33.9 | 12225 | 247853.2905 |  | 1
105 | 80 | 67 | 51.5724 | 277000 | 159000 | 32.8 | 12225 | 329290.2346 |  | 1
105 | 80 | 62 | 36.2232 | 255000 | 223000 | 32 | 12225 | 329290.2346 |  | 1
105 | 80 | 57 | 22.3618 | 246000 | 246000 | 31.8 | 12225 | 329290.2346 |  | 1
105 | 80 | 75 | 79.7527 | 334000 | 62000 | 35 | 14000 | 273136.0223 |  | 1
105 | 80 | 72 | 68.6171 | 312000 | 104000 | 34.2 | 14000 | 273136.0223 |  | 1
105 | 80 | 67 | 51.5724 | 281000 | 177000 | 33 | 14000 | 273136.0223 |  | 1
105 | 80 | 62 | 36.2232 | 261000 | 239000 | 32.3 | 14000 | 362581.0056 |  | 1
105 | 80 | 57 | 22.3618 | 255000 | 255000 | 32.1 | 14000 | 362581.0056 |  | 1
105 | 80 | 75 | 79.7527 | 337000 | 66000 | 35.1 | 15000 | 287730.9497 |  | 1
105 | 80 | 72 | 68.6171 | 314000 | 110000 | 34.3 | 15000 | 287730.9497 |  | 1
105 | 80 | 67 | 51.5724 | 283000 | 187000 | 33.1 | 15000 | 287730.9497 |  | 1
105 | 80 | 62 | 36.2232 | 264000 | 248000 | 32.4 | 15000 | 381751.9553 |  | 1
105 | 80 | 57 | 22.3618 | 259000 | 259000 | 32.2 | 15000 | 381751.9553 |  | 1
115 | 80 | 75 | 79.7527 | 291000 | 24000 | 37.5 | 12225 | 247853.2905 |  | 1
115 | 80 | 72 | 68.6171 | 272000 | 64000 | 36.7 | 12225 | 329290.2346 |  | 1
115 | 80 | 67 | 51.5724 | 240000 | 128000 | 35.6 | 12225 | 329290.2346 |  | 1
115 | 80 | 62 | 36.2232 | 219000 | 187000 | 35 | 12225 | 329290.2346 |  | 1
115 | 80 | 57 | 22.3618 | 208000 | 208000 | 34.8 | 12225 | 322507.4693 |  | 1
115 | 80 | 75 | 79.7527 | 295000 | 29000 | 37.7 | 14000 | 273136.0223 |  | 1
115 | 80 | 72 | 68.6171 | 275000 | 74000 | 36.9 | 14000 | 362581.0056 |  | 1
115 | 80 | 67 | 51.5724 | 243000 | 145000 | 35.8 | 14000 | 362581.0056 |  | 1
115 | 80 | 62 | 36.2232 | 223000 | 202000 | 35.2 | 14000 | 362581.0056 |  | 1
115 | 80 | 57 | 22.3618 | 215000 | 215000 | 35.1 | 14000 | 362581.0056 |  | 1
115 | 80 | 75 | 79.7527 | 296000 | 33000 | 37.8 | 15000 | 287730.9497 |  | 1
115 | 80 | 72 | 68.6171 | 276000 | 78000 | 37 | 15000 | 381751.9553 |  | 1
115 | 80 | 67 | 51.5724 | 245000 | 155000 | 35.9 | 15000 | 381751.9553 |  | 1
115 | 80 | 62 | 36.2232 | 224000 | 209000 | 35.3 | 15000 | 381751.9553 |  | 1
115 | 80 | 57 | 22.3618 | 219000 | 219000 | 35.2 | 15000 | 381751.9553 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 11
Degradation Coefficient (C_d) |  | 48/50 040 (40 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 453000 | 162000 | 24.6 | 8000 | 1521.1732 |  | 1
75 | 80 | 72 | 68.6171 | 431000 | 177000 | 24.2 | 8000 | 1521.1732 |  | 1
75 | 80 | 67 | 51.5724 | 395000 | 207000 | 23.5 | 8000 | 1352.3855 |  | 1
75 | 80 | 62 | 36.2232 | 358000 | 247000 | 22.9 | 8000 | 1352.3855 |  | 1
75 | 80 | 57 | 22.3618 | 329000 | 288000 | 23.5 | 8000 | 1189.8492 |  | 1
75 | 80 | 75 | 79.7527 | 479000 | 175000 | 25.1 | 10000 | 2221.3296 |  | 1
75 | 80 | 72 | 68.6171 | 450000 | 185000 | 24.5 | 10000 | 2221.3296 |  | 1
75 | 80 | 67 | 51.5724 | 418000 | 233000 | 23.9 | 10000 | 2221.3296 |  | 1
75 | 80 | 62 | 36.2232 | 379000 | 275000 | 23.3 | 10000 | 2033.7877 |  | 1
75 | 80 | 57 | 22.3618 | 340000 | 313000 | 22.7 | 10000 | 1850.4134 |  | 1
75 | 80 | 75 | 79.7527 | 498000 | 178000 | 25.5 | 12000 | 3194.4637 |  | 1
75 | 80 | 72 | 68.6171 | 473000 | 201000 | 25 | 12000 | 3194.4637 |  | 1
75 | 80 | 67 | 51.5724 | 433000 | 252000 | 24.2 | 12000 | 3194.4637 |  | 1
75 | 80 | 62 | 36.2232 | 393000 | 300000 | 23.5 | 12000 | 2975.6648 |  | 1
75 | 80 | 57 | 22.3618 | 363000 | 342000 | 23.1 | 12000 | 2975.6648 |  | 1
75 | 80 | 75 | 79.7527 | 513000 | 183000 | 25.8 | 14000 | 4732.3073 |  | 1
75 | 80 | 72 | 68.6171 | 486000 | 212000 | 25.3 | 14000 | 4478.0838 |  | 1
75 | 80 | 67 | 51.5724 | 455000 | 281000 | 25.6 | 14000 | 4478.0838 |  | 1
75 | 80 | 62 | 36.2232 | 406000 | 326000 | 23.8 | 14000 | 4478.0838 |  | 1
75 | 80 | 57 | 22.3618 | 377000 | 362000 | 23.3 | 14000 | 4223.8603 |  | 1
85 | 80 | 75 | 79.7527 | 434000 | 148000 | 27.1 | 8000 | 1521.1732 |  | 1
85 | 80 | 72 | 68.6171 | 413000 | 161000 | 26.7 | 8000 | 1521.1732 |  | 1
85 | 80 | 67 | 51.5724 | 379000 | 193000 | 26.1 | 8000 | 1352.3855 |  | 1
85 | 80 | 62 | 36.2232 | 344000 | 235000 | 25.5 | 8000 | 1189.8492 |  | 1
85 | 80 | 57 | 22.3618 | 308000 | 269000 | 25.1 | 8000 | 1189.8492 |  | 1
85 | 80 | 75 | 79.7527 | 460000 | 156000 | 27.6 | 10000 | 2221.3296 |  | 1
85 | 80 | 72 | 68.6171 | 437000 | 177000 | 27.1 | 10000 | 2221.3296 |  | 1
85 | 80 | 67 | 51.5724 | 401000 | 220000 | 26.5 | 10000 | 2221.3296 |  | 1
85 | 80 | 62 | 36.2232 | 363000 | 263000 | 25.8 | 10000 | 2033.7877 |  | 1
85 | 80 | 57 | 22.3618 | 329000 | 302000 | 25.4 | 10000 | 1850.4134 |  | 1
85 | 80 | 75 | 79.7527 | 478000 | 157000 | 28 | 12000 | 3194.4637 |  | 1
85 | 80 | 72 | 68.6171 | 453000 | 186000 | 27.5 | 12000 | 3194.4637 |  | 1
85 | 80 | 67 | 51.5724 | 416000 | 239000 | 26.7 | 12000 | 3194.4637 |  | 1
85 | 80 | 62 | 36.2232 | 377000 | 288000 | 26.1 | 12000 | 2975.6648 |  | 1
85 | 80 | 57 | 22.3618 | 349000 | 329000 | 25.6 | 12000 | 2758.9497 |  | 1
85 | 80 | 75 | 79.7527 | 490000 | 167000 | 28.2 | 14000 | 4478.0838 |  | 1
85 | 80 | 72 | 68.6171 | 465000 | 197000 | 27.7 | 14000 | 4478.0838 |  | 1
85 | 80 | 67 | 51.5724 | 426000 | 255000 | 26.9 | 14000 | 4478.0838 |  | 1
85 | 80 | 62 | 36.2232 | 388000 | 311000 | 26.3 | 14000 | 4223.8603 |  | 1
85 | 80 | 57 | 22.3618 | 361000 | 347000 | 25.8 | 14000 | 4223.8603 |  | 1
95 | 80 | 75 | 79.7527 | 416000 | 134000 | 29.9 | 8000 | 1521.1732 |  | 1
95 | 80 | 72 | 68.6171 | 396000 | 146000 | 29.6 | 8000 | 1352.3855 |  | 1
95 | 80 | 67 | 51.5724 | 362000 | 180000 | 29 | 8000 | 1352.3855 |  | 1
95 | 80 | 62 | 36.2232 | 325000 | 220000 | 28.4 | 8000 | 1189.8492 |  | 1
95 | 80 | 57 | 22.3618 | 294000 | 257000 | 28.1 | 8000 | 1189.8492 |  | 1
95 | 80 | 75 | 79.7527 | 439000 | 141000 | 30.4 | 10000 | 2221.3296 |  | 1
95 | 80 | 72 | 68.6171 | 418000 | 163000 | 30 | 10000 | 2221.3296 |  | 1
95 | 80 | 67 | 51.5724 | 384000 | 206000 | 29.4 | 10000 | 2033.7877 |  | 1
95 | 80 | 62 | 36.2232 | 357000 | 261000 | 29.9 | 10000 | 2033.7877 |  | 1
95 | 80 | 57 | 22.3618 | 316000 | 290000 | 28.4 | 10000 | 1850.4134 |  | 1
95 | 80 | 75 | 79.7527 | 456000 | 142000 | 30.8 | 12000 | 3194.4637 |  | 1
95 | 80 | 72 | 68.6171 | 445000 | 177000 | 30.9 | 12000 | 3194.4637 |  | 1
95 | 80 | 67 | 51.5724 | 397000 | 224000 | 29.6 | 12000 | 2975.6648 |  | 1
95 | 80 | 62 | 36.2232 | 373000 | 289000 | 30 | 12000 | 2975.6648 |  | 1
95 | 80 | 57 | 22.3618 | 332000 | 312000 | 28.6 | 12000 | 2758.9497 |  | 1
95 | 80 | 75 | 79.7527 | 467000 | 151000 | 31 | 14000 | 4478.0838 |  | 1
95 | 80 | 72 | 68.6171 | 459000 | 197000 | 31.5 | 14000 | 4478.0838 |  | 1
95 | 80 | 67 | 51.5724 | 406000 | 241000 | 29.8 | 14000 | 4478.0838 |  | 1
95 | 80 | 62 | 36.2232 | 360000 | 287000 | 29 | 14000 | 4223.8603 |  | 1
95 | 80 | 57 | 22.3618 | 345000 | 330000 | 28.8 | 14000 | 3969.6369 |  | 1
105 | 80 | 75 | 79.7527 | 391000 | 114000 | 33.3 | 8000 | 1352.3855 |  | 1
105 | 80 | 72 | 68.6171 | 377000 | 133000 | 32.9 | 8000 | 1352.3855 |  | 1
105 | 80 | 67 | 51.5724 | 346000 | 164000 | 32.4 | 8000 | 1189.8492 |  | 1
105 | 80 | 62 | 36.2232 | 322000 | 221000 | 33 | 8000 | 1189.8492 |  | 1
105 | 80 | 57 | 22.3618 | 287000 | 254000 | 32.7 | 8000 | 1189.8492 |  | 1
105 | 80 | 75 | 79.7527 | 418000 | 126000 | 33.7 | 10000 | 2221.3296 |  | 1
105 | 80 | 72 | 68.6171 | 397000 | 148000 | 33.3 | 10000 | 2033.7877 |  | 1
105 | 80 | 67 | 51.5724 | 364000 | 192000 | 32.7 | 10000 | 2033.7877 |  | 1
105 | 80 | 62 | 36.2232 | 340000 | 249000 | 33.6 | 10000 | 1850.4134 |  | 1
105 | 80 | 57 | 22.3618 | 300000 | 275000 | 31.8 | 10000 | 1850.4134 |  | 1
105 | 80 | 75 | 79.7527 | 434000 | 126000 | 34 | 12000 | 3194.4637 |  | 1
105 | 80 | 72 | 68.6171 | 414000 | 153000 | 33.6 | 12000 | 3194.4637 |  | 1
105 | 80 | 67 | 51.5724 | 376000 | 209000 | 33 | 12000 | 2975.6648 |  | 1
105 | 80 | 62 | 36.2232 | 353000 | 273000 | 34 | 12000 | 2975.6648 |  | 1
105 | 80 | 57 | 22.3618 | 316000 | 296000 | 32 | 12000 | 2758.9497 |  | 1
105 | 80 | 75 | 79.7527 | 444000 | 134000 | 34.3 | 14000 | 4478.0838 |  | 1
105 | 80 | 72 | 68.6171 | 422000 | 166000 | 33.8 | 14000 | 4478.0838 |  | 1
105 | 80 | 67 | 51.5724 | 385000 | 225000 | 33.1 | 14000 | 4223.8603 |  | 1
105 | 80 | 62 | 36.2232 | 345000 | 277000 | 33.1 | 14000 | 3969.6369 |  | 1
105 | 80 | 57 | 22.3618 | 328000 | 314000 | 32.2 | 14000 | 3969.6369 |  | 1
115 | 80 | 75 | 79.7527 | 374000 | 103000 | 37 | 8000 | 1352.3855 |  | 1
115 | 80 | 72 | 68.6171 | 360000 | 123000 | 36.8 | 8000 | 1352.3855 |  | 1
115 | 80 | 67 | 51.5724 | 325000 | 154000 | 36.2 | 8000 | 1189.8492 |  | 1
115 | 80 | 62 | 36.2232 | 305000 | 209000 | 37 | 8000 | 1189.8492 |  | 1
115 | 80 | 57 | 22.3618 | 261000 | 226000 | 35.2 | 8000 | 1108.581 |  | 1
115 | 80 | 75 | 79.7527 | 395000 | 108000 | 37.4 | 10000 | 2033.7877 |  | 1
115 | 80 | 72 | 68.6171 | 374000 | 132000 | 37 | 10000 | 2033.7877 |  | 1
115 | 80 | 67 | 51.5724 | 342000 | 176000 | 36.5 | 10000 | 1850.4134 |  | 1
115 | 80 | 62 | 36.2232 | 309000 | 222000 | 36 | 10000 | 1850.4134 |  | 1
115 | 80 | 57 | 22.3618 | 283000 | 259000 | 35.6 | 10000 | 1850.4134 |  | 1
115 | 80 | 75 | 79.7527 | 409000 | 110000 | 37.7 | 12000 | 3194.4637 |  | 1
115 | 80 | 72 | 68.6171 | 389000 | 136000 | 37.3 | 12000 | 2975.6648 |  | 1
115 | 80 | 67 | 51.5724 | 354000 | 194000 | 36.8 | 12000 | 2975.6648 |  | 1
115 | 80 | 62 | 36.2232 | 320000 | 245000 | 36.2 | 12000 | 2758.9497 |  | 1
115 | 80 | 57 | 22.3618 | 299000 | 280000 | 35.9 | 12000 | 2758.9497 |  | 1
115 | 80 | 75 | 79.7527 | 418000 | 117000 | 37.9 | 14000 | 4478.0838 |  | 1
115 | 80 | 72 | 68.6171 | 398000 | 149000 | 37.5 | 14000 | 4223.8603 |  | 1
115 | 80 | 67 | 51.5724 | 362000 | 209000 | 36.9 | 14000 | 4223.8603 |  | 1
115 | 80 | 62 | 36.2232 | 329000 | 266000 | 36.4 | 14000 | 3969.6369 |  | 1
115 | 80 | 57 | 22.3618 | 309000 | 296000 | 36.1 | 14000 | 3969.6369 |  | 1
75 | 80 | 75 | 79.7527 | 523000 | 192000 | 26 | 16000 | 6397.2626 |  | 1
75 | 80 | 72 | 68.6171 | 496000 | 225000 | 25.5 | 16000 | 6105.5307 |  | 1
75 | 80 | 67 | 51.5724 | 452000 | 285000 | 24.6 | 16000 | 6105.5307 |  | 1
75 | 80 | 62 | 36.2232 | 414000 | 346000 | 23.9 | 16000 | 6105.5307 |  | 1
75 | 80 | 57 | 22.3618 | 393000 | 380000 | 24.6 | 16000 | 5811.7151 |  | 1
75 | 80 | 75 | 79.7527 | 532000 | 196000 | 26.2 | 18000 | 8453.9721 |  | 1
75 | 80 | 72 | 68.6171 | 504000 | 236000 | 25.6 | 18000 | 8453.9721 |  | 1
75 | 80 | 67 | 51.5724 | 460000 | 301000 | 24.8 | 18000 | 8124.7318 |  | 1
75 | 80 | 62 | 36.2232 | 420000 | 364000 | 24 | 18000 | 8124.7318 |  | 1
75 | 80 | 57 | 22.3618 | 405000 | 405000 | 24.9 | 18000 | 8124.7318 |  | 1
75 | 80 | 75 | 79.7527 | 540000 | 199000 | 26.4 | 20000 | 10948.2793 |  | 1
75 | 80 | 72 | 68.6171 | 511000 | 246000 | 25.8 | 20000 | 10948.2793 |  | 1
75 | 80 | 67 | 51.5724 | 466000 | 316000 | 24.9 | 20000 | 10573.1955 |  | 1
75 | 80 | 62 | 36.2232 | 427000 | 376000 | 24.2 | 20000 | 10573.1955 |  | 1
75 | 80 | 57 | 22.3618 | 404000 | 385000 | 23.8 | 20000 | 10573.1955 |  | 1
85 | 80 | 75 | 79.7527 | 500000 | 175000 | 28.4 | 16000 | 6105.5307 |  | 1
85 | 80 | 72 | 68.6171 | 474000 | 209000 | 27.9 | 16000 | 6105.5307 |  | 1
85 | 80 | 67 | 51.5724 | 434000 | 271000 | 27.1 | 16000 | 6105.5307 |  | 1
85 | 80 | 62 | 36.2232 | 397000 | 332000 | 26.4 | 16000 | 5811.7151 |  | 1
85 | 80 | 57 | 22.3618 | 368000 | 368000 | 25.9 | 16000 | 5811.7151 |  | 1
85 | 80 | 75 | 79.7527 | 508000 | 179000 | 28.6 | 18000 | 8453.9721 |  | 1
85 | 80 | 72 | 68.6171 | 482000 | 220000 | 28.1 | 18000 | 8124.7318 |  | 1
85 | 80 | 67 | 51.5724 | 442000 | 278000 | 27.3 | 18000 | 8124.7318 |  | 1
85 | 80 | 62 | 36.2232 | 416000 | 356000 | 27.8 | 18000 | 8124.7318 |  | 1
85 | 80 | 57 | 22.3618 | 378000 | 378000 | 26.1 | 18000 | 7787.1564 |  | 1
85 | 80 | 75 | 79.7527 | 515000 | 182000 | 28.8 | 20000 | 10948.2793 |  | 1
85 | 80 | 72 | 68.6171 | 489000 | 230000 | 28.2 | 20000 | 10573.1955 |  | 1
85 | 80 | 67 | 51.5724 | 434000 | 288000 | 27.2 | 20000 | 10573.1955 |  | 1
85 | 80 | 62 | 36.2232 | 419000 | 377000 | 27.4 | 20000 | 10573.1955 |  | 1
85 | 80 | 57 | 22.3618 | 388000 | 388000 | 26.3 | 20000 | 10187.6927 |  | 1
95 | 80 | 75 | 79.7527 | 476000 | 158000 | 31.2 | 16000 | 6105.5307 |  | 1
95 | 80 | 72 | 68.6171 | 453000 | 193000 | 30.7 | 16000 | 6105.5307 |  | 1
95 | 80 | 67 | 51.5724 | 414000 | 256000 | 30 | 16000 | 6105.5307 |  | 1
95 | 80 | 62 | 36.2232 | 377000 | 316000 | 29.3 | 16000 | 5811.7151 |  | 1
95 | 80 | 57 | 22.3618 | 351000 | 351000 | 28.9 | 16000 | 5811.7151 |  | 1
95 | 80 | 75 | 79.7527 | 484000 | 161000 | 31.4 | 18000 | 8124.7318 |  | 1
95 | 80 | 72 | 68.6171 | 476000 | 219000 | 31.9 | 18000 | 8124.7318 |  | 1
95 | 80 | 67 | 51.5724 | 421000 | 271000 | 30.1 | 18000 | 8124.7318 |  | 1
95 | 80 | 62 | 36.2232 | 381000 | 333000 | 29.4 | 18000 | 7787.1564 |  | 1
95 | 80 | 57 | 22.3618 | 363000 | 363000 | 29.1 | 18000 | 7787.1564 |  | 1
95 | 80 | 75 | 79.7527 | 491000 | 165000 | 31.6 | 20000 | 10573.1955 |  | 1
95 | 80 | 72 | 68.6171 | 466000 | 214000 | 31 | 20000 | 10573.1955 |  | 1
95 | 80 | 67 | 51.5724 | 441000 | 300000 | 31.6 | 20000 | 10573.1955 |  | 1
95 | 80 | 62 | 36.2232 | 390000 | 348000 | 29.6 | 20000 | 10187.6927 |  | 1
95 | 80 | 57 | 22.3618 | 373000 | 373000 | 29.3 | 20000 | 10187.6927 |  | 1
105 | 80 | 75 | 79.7527 | 452000 | 141000 | 34.5 | 16000 | 6105.5307 |  | 1
105 | 80 | 72 | 68.6171 | 430000 | 177000 | 34 | 16000 | 6105.5307 |  | 1
105 | 80 | 67 | 51.5724 | 392000 | 240000 | 33.3 | 16000 | 5811.7151 |  | 1
105 | 80 | 62 | 36.2232 | 358000 | 301000 | 32.7 | 16000 | 5811.7151 |  | 1
105 | 80 | 57 | 22.3618 | 335000 | 335000 | 32.3 | 16000 | 5515.8156 |  | 1
105 | 80 | 75 | 79.7527 | 459000 | 144000 | 34.6 | 18000 | 8124.7318 |  | 1
105 | 80 | 72 | 68.6171 | 437000 | 187000 | 34.1 | 18000 | 8124.7318 |  | 1
105 | 80 | 67 | 51.5724 | 389000 | 245000 | 33.2 | 18000 | 7787.1564 |  | 1
105 | 80 | 62 | 36.2232 | 362000 | 315000 | 32.8 | 18000 | 7787.1564 |  | 1
105 | 80 | 57 | 22.3618 | 346000 | 346000 | 32.5 | 18000 | 7441.2458 |  | 1
105 | 80 | 75 | 79.7527 | 466000 | 148000 | 34.8 | 20000 | 10573.1955 |  | 1
105 | 80 | 72 | 68.6171 | 459000 | 213000 | 35.3 | 20000 | 10573.1955 |  | 1
105 | 80 | 67 | 51.5724 | 395000 | 260000 | 33.4 | 20000 | 10187.6927 |  | 1
105 | 80 | 62 | 36.2232 | 369000 | 323000 | 32.9 | 20000 | 10187.6927 |  | 1
105 | 80 | 57 | 22.3618 | 356000 | 356000 | 32.7 | 20000 | 10187.6927 |  | 1
115 | 80 | 75 | 79.7527 | 427000 | 119000 | 38.1 | 16000 | 6105.5307 |  | 1
115 | 80 | 72 | 68.6171 | 405000 | 159000 | 37.7 | 16000 | 6105.5307 |  | 1
115 | 80 | 67 | 51.5724 | 369000 | 224000 | 37.1 | 16000 | 5811.7151 |  | 1
115 | 80 | 62 | 36.2232 | 335000 | 284000 | 36.5 | 16000 | 5515.8156 |  | 1
115 | 80 | 57 | 22.3618 | 316000 | 316000 | 36.2 | 16000 | 5515.8156 |  | 1
115 | 80 | 75 | 79.7527 | 450000 | 143000 | 39.2 | 18000 | 8124.7318 |  | 1
115 | 80 | 72 | 68.6171 | 411000 | 169000 | 37.8 | 18000 | 8124.7318 |  | 1
115 | 80 | 67 | 51.5724 | 375000 | 239000 | 37.2 | 18000 | 7787.1564 |  | 1
115 | 80 | 62 | 36.2232 | 344000 | 298000 | 36.7 | 18000 | 7441.2458 |  | 1
115 | 80 | 57 | 22.3618 | 327000 | 327000 | 36.4 | 18000 | 7441.2458 |  | 1
115 | 80 | 75 | 79.7527 | 441000 | 132000 | 38.5 | 20000 | 10573.1955 |  | 1
115 | 80 | 72 | 68.6171 | 416000 | 178000 | 38 | 20000 | 10573.1955 |  | 1
115 | 80 | 67 | 51.5724 | 380000 | 252000 | 37.3 | 20000 | 10187.6927 |  | 1
115 | 80 | 62 | 36.2232 | 351000 | 310000 | 36.8 | 20000 | 10187.6927 |  | 1
115 | 80 | 57 | 22.3618 | 336000 | 336000 | 36.5 | 20000 | 9791.7709 |  | 1
75 | 80 | 75 | 79.7527 | 445000 | 133000 | 24.9 | 8000 | 1521.1732 |  | 2
75 | 80 | 72 | 68.6171 | 418000 | 154000 | 24.4 | 8000 | 1521.1732 |  | 2
75 | 80 | 67 | 51.5724 | 373000 | 191000 | 23.5 | 8000 | 1352.3855 |  | 2
75 | 80 | 62 | 36.2232 | 335000 | 234000 | 22.8 | 8000 | 1189.8492 |  | 2
75 | 80 | 57 | 22.3618 | 300000 | 273000 | 22.3 | 8000 | 1189.8492 |  | 2
75 | 80 | 75 | 79.7527 | 479000 | 148000 | 25.6 | 10000 | 2221.3296 |  | 2
75 | 80 | 72 | 68.6171 | 451000 | 174000 | 25 | 10000 | 2221.3296 |  | 2
75 | 80 | 67 | 51.5724 | 403000 | 224000 | 24 | 10000 | 2221.3296 |  | 2
75 | 80 | 62 | 36.2232 | 363000 | 275000 | 23.3 | 10000 | 2033.7877 |  | 2
75 | 80 | 57 | 22.3618 | 337000 | 322000 | 22.8 | 10000 | 1850.4134 |  | 2
75 | 80 | 75 | 79.7527 | 495000 | 152000 | 25.8 | 12000 | 3194.4637 |  | 2
75 | 80 | 72 | 68.6171 | 467000 | 190000 | 25.3 | 12000 | 3194.4637 |  | 2
75 | 80 | 67 | 51.5724 | 424000 | 252000 | 24.4 | 12000 | 3194.4637 |  | 2
75 | 80 | 62 | 36.2232 | 385000 | 314000 | 23.7 | 12000 | 2975.6648 |  | 2
75 | 80 | 57 | 22.3618 | 358000 | 352000 | 23.2 | 12000 | 2975.6648 |  | 2
75 | 80 | 75 | 79.7527 | 518000 | 170000 | 26.4 | 14000 | 4732.3073 |  | 2
75 | 80 | 72 | 68.6171 | 486000 | 211000 | 25.7 | 14000 | 4478.0838 |  | 2
75 | 80 | 67 | 51.5724 | 440000 | 279000 | 24.7 | 14000 | 4478.0838 |  | 2
75 | 80 | 62 | 36.2232 | 401000 | 348000 | 23.9 | 14000 | 4478.0838 |  | 2
75 | 80 | 57 | 22.3618 | 382000 | 381000 | 23.6 | 14000 | 4223.8603 |  | 2
85 | 80 | 75 | 79.7527 | 414000 | 106000 | 27.2 | 8000 | 1521.1732 |  | 2
85 | 80 | 72 | 68.6171 | 389000 | 129000 | 26.6 | 8000 | 1352.3855 |  | 2
85 | 80 | 67 | 51.5724 | 347000 | 167000 | 25.8 | 8000 | 1189.8492 |  | 2
85 | 80 | 62 | 36.2232 | 313000 | 213000 | 25.2 | 8000 | 1189.8492 |  | 2
85 | 80 | 57 | 22.3618 | 279000 | 254000 | 24.7 | 8000 | 1108.581 |  | 2
85 | 80 | 75 | 79.7527 | 443000 | 117000 | 27.7 | 10000 | 2221.3296 |  | 2
85 | 80 | 72 | 68.6171 | 416000 | 143000 | 27.2 | 10000 | 2221.3296 |  | 2
85 | 80 | 67 | 51.5724 | 377000 | 200000 | 26.4 | 10000 | 2033.7877 |  | 2
85 | 80 | 62 | 36.2232 | 340000 | 254000 | 25.7 | 10000 | 1850.4134 |  | 2
85 | 80 | 57 | 22.3618 | 318000 | 304000 | 25.2 | 10000 | 1850.4134 |  | 2
85 | 80 | 75 | 79.7527 | 466000 | 128000 | 28.2 | 12000 | 3194.4637 |  | 2
85 | 80 | 72 | 68.6171 | 437000 | 165000 | 27.6 | 12000 | 3194.4637 |  | 2
85 | 80 | 67 | 51.5724 | 398000 | 229000 | 26.7 | 12000 | 2975.6648 |  | 2
85 | 80 | 62 | 36.2232 | 362000 | 293000 | 26 | 12000 | 2975.6648 |  | 2
85 | 80 | 57 | 22.3618 | 339000 | 332000 | 25.6 | 12000 | 2758.9497 |  | 2
85 | 80 | 75 | 79.7527 | 482000 | 139000 | 28.5 | 14000 | 4478.0838 |  | 2
85 | 80 | 72 | 68.6171 | 453000 | 183000 | 27.9 | 14000 | 4478.0838 |  | 2
85 | 80 | 67 | 51.5724 | 414000 | 256000 | 27 | 14000 | 4478.0838 |  | 2
85 | 80 | 62 | 36.2232 | 378000 | 328000 | 26.3 | 14000 | 4223.8603 |  | 2
85 | 80 | 57 | 22.3618 | 362000 | 361000 | 26 | 14000 | 4223.8603 |  | 2
95 | 80 | 75 | 79.7527 | 384000 | 80000 | 29.7 | 8000 | 1352.3855 |  | 2
95 | 80 | 72 | 68.6171 | 361000 | 104000 | 29.2 | 8000 | 1352.3855 |  | 2
95 | 80 | 67 | 51.5724 | 322000 | 144000 | 28.5 | 8000 | 1189.8492 |  | 2
95 | 80 | 62 | 36.2232 | 290000 | 193000 | 28 | 8000 | 1189.8492 |  | 2
95 | 80 | 57 | 22.3618 | 261000 | 236000 | 27.5 | 8000 | 1108.581 |  | 2
95 | 80 | 75 | 79.7527 | 412000 | 90000 | 30.3 | 10000 | 2221.3296 |  | 2
95 | 80 | 72 | 68.6171 | 387000 | 118000 | 29.8 | 10000 | 2033.7877 |  | 2
95 | 80 | 67 | 51.5724 | 351000 | 177000 | 29.1 | 10000 | 2033.7877 |  | 2
95 | 80 | 62 | 36.2232 | 317000 | 234000 | 28.5 | 10000 | 1850.4134 |  | 2
95 | 80 | 57 | 22.3618 | 299000 | 285000 | 28.2 | 10000 | 1850.4134 |  | 2
95 | 80 | 75 | 79.7527 | 433000 | 99000 | 30.8 | 12000 | 3194.4637 |  | 2
95 | 80 | 72 | 68.6171 | 407000 | 138000 | 30.2 | 12000 | 3194.4637 |  | 2
95 | 80 | 67 | 51.5724 | 372000 | 206000 | 29.5 | 12000 | 2975.6648 |  | 2
95 | 80 | 62 | 36.2232 | 338000 | 273000 | 28.9 | 12000 | 2758.9497 |  | 2
95 | 80 | 57 | 22.3618 | 318000 | 311000 | 28.5 | 12000 | 2758.9497 |  | 2
95 | 80 | 75 | 79.7527 | 449000 | 111000 | 31.1 | 14000 | 4478.0838 |  | 2
95 | 80 | 72 | 68.6171 | 424000 | 158000 | 30.5 | 14000 | 4478.0838 |  | 2
95 | 80 | 67 | 51.5724 | 388000 | 234000 | 29.8 | 14000 | 4223.8603 |  | 2
95 | 80 | 62 | 36.2232 | 354000 | 307000 | 29.1 | 14000 | 4223.8603 |  | 2
95 | 80 | 57 | 22.3618 | 339000 | 339000 | 28.8 | 14000 | 3969.6369 |  | 2
105 | 80 | 75 | 79.7527 | 355000 | 53000 | 32.7 | 8000 | 1352.3855 |  | 2
105 | 80 | 72 | 68.6171 | 333000 | 80000 | 32.3 | 8000 | 1189.8492 |  | 2
105 | 80 | 67 | 51.5724 | 295000 | 121000 | 31.7 | 8000 | 1189.8492 |  | 2
105 | 80 | 62 | 36.2232 | 265000 | 172000 | 31.3 | 8000 | 1108.581 |  | 2
105 | 80 | 57 | 22.3618 | 239000 | 217000 | 31 | 8000 | 1108.581 |  | 2
105 | 80 | 75 | 79.7527 | 380000 | 63000 | 33.3 | 10000 | 2033.7877 |  | 2
105 | 80 | 72 | 68.6171 | 356000 | 92000 | 32.8 | 10000 | 2033.7877 |  | 2
105 | 80 | 67 | 51.5724 | 323000 | 154000 | 32.3 | 10000 | 1850.4134 |  | 2
105 | 80 | 62 | 36.2232 | 292000 | 213000 | 31.8 | 10000 | 1850.4134 |  | 2
105 | 80 | 57 | 22.3618 | 279000 | 266000 | 31.6 | 10000 | 1758.7263 |  | 2
105 | 80 | 75 | 79.7527 | 401000 | 72000 | 33.8 | 12000 | 3194.4637 |  | 2
105 | 80 | 72 | 68.6171 | 376000 | 112000 | 33.3 | 12000 | 2975.6648 |  | 2
105 | 80 | 67 | 51.5724 | 343000 | 183000 | 32.7 | 12000 | 2758.9497 |  | 2
105 | 80 | 62 | 36.2232 | 312000 | 251000 | 32.2 | 12000 | 2758.9497 |  | 2
105 | 80 | 57 | 22.3618 | 300000 | 293000 | 31.9 | 12000 | 2758.9497 |  | 2
105 | 80 | 75 | 79.7527 | 416000 | 84000 | 34.1 | 14000 | 4478.0838 |  | 2
105 | 80 | 72 | 68.6171 | 393000 | 132000 | 33.6 | 14000 | 4223.8603 |  | 2
105 | 80 | 67 | 51.5724 | 358000 | 210000 | 33 | 14000 | 4223.8603 |  | 2
105 | 80 | 62 | 36.2232 | 331000 | 284000 | 32.4 | 14000 | 3969.6369 |  | 2
105 | 80 | 57 | 22.3618 | 318000 | 317000 | 32.2 | 14000 | 3969.6369 |  | 2
115 | 80 | 75 | 79.7527 | 324000 | 27000 | 36.2 | 8000 | 1189.8492 |  | 2
115 | 80 | 72 | 68.6171 | 303000 | 56000 | 35.9 | 8000 | 1189.8492 |  | 2
115 | 80 | 67 | 51.5724 | 266000 | 99000 | 35.4 | 8000 | 1108.581 |  | 2
115 | 80 | 62 | 36.2232 | 239000 | 151000 | 35.4 | 8000 | 1108.581 |  | 2
115 | 80 | 57 | 22.3618 | 220000 | 199000 | 35.5 | 8000 | 1108.581 |  | 2
115 | 80 | 75 | 79.7527 | 346000 | 35000 | 36.8 | 10000 | 1850.4134 |  | 2
115 | 80 | 72 | 68.6171 | 323000 | 65000 | 36.4 | 10000 | 1850.4134 |  | 2
115 | 80 | 67 | 51.5724 | 294000 | 131000 | 36 | 10000 | 1850.4134 |  | 2
115 | 80 | 62 | 36.2232 | 264000 | 192000 | 36 | 10000 | 1758.7263 |  | 2
115 | 80 | 57 | 22.3618 | 259000 | 248000 | 35.9 | 10000 | 1758.7263 |  | 2
115 | 80 | 75 | 79.7527 | 365000 | 44000 | 37.3 | 12000 | 2975.6648 |  | 2
115 | 80 | 72 | 68.6171 | 343000 | 85000 | 36.9 | 12000 | 2758.9497 |  | 2
115 | 80 | 67 | 51.5724 | 313000 | 159000 | 36.5 | 12000 | 2758.9497 |  | 2
115 | 80 | 62 | 36.2232 | 284000 | 229000 | 36.3 | 12000 | 2758.9497 |  | 2
115 | 80 | 57 | 22.3618 | 276000 | 269000 | 36.1 | 12000 | 2650.5922 |  | 2
115 | 80 | 75 | 79.7527 | 381000 | 56000 | 37.7 | 14000 | 4223.8603 |  | 2
115 | 80 | 72 | 68.6171 | 358000 | 105000 | 37.3 | 14000 | 4223.8603 |  | 2
115 | 80 | 67 | 51.5724 | 329000 | 187000 | 36.8 | 14000 | 3969.6369 |  | 2
115 | 80 | 62 | 36.2232 | 300000 | 255000 | 36.4 | 14000 | 3969.6369 |  | 2
115 | 80 | 57 | 22.3618 | 295000 | 295000 | 36.3 | 14000 | 3969.6369 |  | 2
75 | 80 | 75 | 79.7527 | 523000 | 176000 | 26.4 | 16000 | 6397.2626 |  | 2
75 | 80 | 72 | 68.6171 | 498000 | 227000 | 25.9 | 16000 | 6105.5307 |  | 2
75 | 80 | 67 | 51.5724 | 452000 | 304000 | 24.9 | 16000 | 6105.5307 |  | 2
75 | 80 | 62 | 36.2232 | 414000 | 377000 | 24.2 | 16000 | 6105.5307 |  | 2
75 | 80 | 57 | 22.3618 | 399000 | 399000 | 23.9 | 16000 | 5811.7151 |  | 2
75 | 80 | 75 | 79.7527 | 540000 | 194000 | 26.8 | 18000 | 8453.9721 |  | 2
75 | 80 | 72 | 68.6171 | 508000 | 243000 | 26.1 | 18000 | 8453.9721 |  | 2
75 | 80 | 67 | 51.5724 | 462000 | 327000 | 25.1 | 18000 | 8124.7318 |  | 2
75 | 80 | 62 | 36.2232 | 426000 | 394000 | 24.4 | 18000 | 8124.7318 |  | 2
75 | 80 | 57 | 22.3618 | 413000 | 413000 | 24.2 | 18000 | 8124.7318 |  | 2
75 | 80 | 75 | 79.7527 | 549000 | 205000 | 27 | 20000 | 10948.2793 |  | 2
75 | 80 | 72 | 68.6171 | 516000 | 257000 | 26.3 | 20000 | 10948.2793 |  | 2
75 | 80 | 67 | 51.5724 | 471000 | 350000 | 25.3 | 20000 | 10573.1955 |  | 2
75 | 80 | 62 | 36.2232 | 428000 | 406000 | 24.5 | 20000 | 10573.1955 |  | 2
75 | 80 | 57 | 22.3618 | 419000 | 419000 | 24.3 | 20000 | 10573.1955 |  | 2
85 | 80 | 75 | 79.7527 | 493000 | 152000 | 28.7 | 16000 | 6105.5307 |  | 2
85 | 80 | 72 | 68.6171 | 466000 | 200000 | 28.1 | 16000 | 6105.5307 |  | 2
85 | 80 | 67 | 51.5724 | 426000 | 281000 | 27.3 | 16000 | 6105.5307 |  | 2
85 | 80 | 62 | 36.2232 | 393000 | 356000 | 26.6 | 16000 | 5811.7151 |  | 2
85 | 80 | 57 | 22.3618 | 378000 | 378000 | 26.3 | 16000 | 5811.7151 |  | 2
85 | 80 | 75 | 79.7527 | 504000 | 164000 | 29 | 18000 | 8453.9721 |  | 2
85 | 80 | 72 | 68.6171 | 477000 | 217000 | 28.3 | 18000 | 8124.7318 |  | 2
85 | 80 | 67 | 51.5724 | 435000 | 304000 | 27.5 | 18000 | 8124.7318 |  | 2
85 | 80 | 62 | 36.2232 | 407000 | 379000 | 26.8 | 18000 | 8124.7318 |  | 2
85 | 80 | 57 | 22.3618 | 396000 | 396000 | 26.6 | 18000 | 7787.1564 |  | 2
85 | 80 | 75 | 79.7527 | 513000 | 174000 | 29.1 | 20000 | 10948.2793 |  | 2
85 | 80 | 72 | 68.6171 | 485000 | 232000 | 28.5 | 20000 | 10573.1955 |  | 2
85 | 80 | 67 | 51.5724 | 444000 | 327000 | 27.6 | 20000 | 10573.1955 |  | 2
85 | 80 | 62 | 36.2232 | 419000 | 400000 | 27.1 | 20000 | 10573.1955 |  | 2
85 | 80 | 57 | 22.3618 | 405000 | 405000 | 26.8 | 20000 | 10573.1955 |  | 2
95 | 80 | 75 | 79.7527 | 462000 | 125000 | 31.4 | 16000 | 6105.5307 |  | 2
95 | 80 | 72 | 68.6171 | 439000 | 177000 | 30.8 | 16000 | 6105.5307 |  | 2
95 | 80 | 67 | 51.5724 | 400000 | 259000 | 30 | 16000 | 5811.7151 |  | 2
95 | 80 | 62 | 36.2232 | 370000 | 333000 | 29.4 | 16000 | 5811.7151 |  | 2
95 | 80 | 57 | 22.3618 | 357000 | 357000 | 29.1 | 16000 | 5811.7151 |  | 2
95 | 80 | 75 | 79.7527 | 473000 | 138000 | 31.6 | 18000 | 8124.7318 |  | 2
95 | 80 | 72 | 68.6171 | 449000 | 192000 | 31 | 18000 | 8124.7318 |  | 2
95 | 80 | 67 | 51.5724 | 409000 | 282000 | 30.2 | 18000 | 8124.7318 |  | 2
95 | 80 | 62 | 36.2232 | 384000 | 357000 | 29.7 | 18000 | 7787.1564 |  | 2
95 | 80 | 57 | 22.3618 | 370000 | 370000 | 29.4 | 18000 | 7787.1564 |  | 2
95 | 80 | 75 | 79.7527 | 480000 | 146000 | 31.7 | 20000 | 10573.1955 |  | 2
95 | 80 | 72 | 68.6171 | 454000 | 205000 | 31.2 | 20000 | 10573.1955 |  | 2
95 | 80 | 67 | 51.5724 | 417000 | 305000 | 30.4 | 20000 | 10573.1955 |  | 2
95 | 80 | 62 | 36.2232 | 398000 | 380000 | 29.9 | 20000 | 10187.6927 |  | 2
95 | 80 | 57 | 22.3618 | 382000 | 382000 | 29.6 | 20000 | 10187.6927 |  | 2
105 | 80 | 75 | 79.7527 | 428000 | 97000 | 34.4 | 16000 | 6105.5307 |  | 2
105 | 80 | 72 | 68.6171 | 408000 | 151000 | 34 | 16000 | 6105.5307 |  | 2
105 | 80 | 67 | 51.5724 | 371000 | 235000 | 33.3 | 16000 | 5811.7151 |  | 2
105 | 80 | 62 | 36.2232 | 346000 | 311000 | 32.7 | 16000 | 5515.8156 |  | 2
105 | 80 | 57 | 22.3618 | 335000 | 335000 | 32.5 | 16000 | 5515.8156 |  | 2
105 | 80 | 75 | 79.7527 | 439000 | 110000 | 34.7 | 18000 | 8124.7318 |  | 2
105 | 80 | 72 | 68.6171 | 417000 | 167000 | 34.2 | 18000 | 8124.7318 |  | 2
105 | 80 | 67 | 51.5724 | 380000 | 259000 | 33.5 | 18000 | 7787.1564 |  | 2
105 | 80 | 62 | 36.2232 | 361000 | 335000 | 33 | 18000 | 7787.1564 |  | 2
105 | 80 | 57 | 22.3618 | 348000 | 348000 | 32.8 | 18000 | 7441.2458 |  | 2
105 | 80 | 75 | 79.7527 | 449000 | 122000 | 34.9 | 20000 | 10573.1955 |  | 2
105 | 80 | 72 | 68.6171 | 422000 | 179000 | 34.3 | 20000 | 10573.1955 |  | 2
105 | 80 | 67 | 51.5724 | 388000 | 281000 | 33.6 | 20000 | 10187.6927 |  | 2
105 | 80 | 62 | 36.2232 | 377000 | 360000 | 33.4 | 20000 | 10187.6927 |  | 2
105 | 80 | 57 | 22.3618 | 361000 | 361000 | 33 | 20000 | 10187.6927 |  | 2
115 | 80 | 75 | 79.7527 | 393000 | 70000 | 38.1 | 16000 | 5811.7151 |  | 2
115 | 80 | 72 | 68.6171 | 374000 | 126000 | 37.6 | 16000 | 5811.7151 |  | 2
115 | 80 | 67 | 51.5724 | 338000 | 210000 | 37 | 16000 | 5515.8156 |  | 2
115 | 80 | 62 | 36.2232 | 322000 | 288000 | 36.7 | 16000 | 5515.8156 |  | 2
115 | 80 | 57 | 22.3618 | 310000 | 310000 | 36.5 | 16000 | 5515.8156 |  | 2
115 | 80 | 75 | 79.7527 | 403000 | 82000 | 38.4 | 18000 | 8124.7318 |  | 2
115 | 80 | 72 | 68.6171 | 385000 | 142000 | 37.9 | 18000 | 7787.1564 |  | 2
115 | 80 | 67 | 51.5724 | 347000 | 233000 | 37.3 | 18000 | 7441.2458 |  | 2
115 | 80 | 62 | 36.2232 | 335000 | 310000 | 36.9 | 18000 | 7441.2458 |  | 2
115 | 80 | 57 | 22.3618 | 324000 | 324000 | 36.7 | 18000 | 7441.2458 |  | 2
115 | 80 | 75 | 79.7527 | 412000 | 93000 | 38.6 | 20000 | 10573.1955 |  | 2
115 | 80 | 72 | 68.6171 | 390000 | 155000 | 38.1 | 20000 | 10187.6927 |  | 2
115 | 80 | 67 | 51.5724 | 354000 | 255000 | 37.5 | 20000 | 10187.6927 |  | 2
115 | 80 | 62 | 36.2232 | 347000 | 327000 | 37.2 | 20000 | 9791.7709 |  | 2
115 | 80 | 57 | 22.3618 | 334000 | 334000 | 36.9 | 20000 | 9791.7709 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 12
Degradation Coefficient (C_d) |  | 48/50 050 (50 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 590000 | 206000 | 33.2 | 10000 | 2477.6369 |  | 1
75 | 80 | 72 | 68.6171 | 563000 | 233000 | 32.7 | 10000 | 2477.6369 |  | 1
75 | 80 | 67 | 51.5724 | 519000 | 275000 | 32.1 | 10000 | 2477.6369 |  | 1
75 | 80 | 62 | 36.2232 | 472000 | 329000 | 31.5 | 10000 | 2281.7598 |  | 1
75 | 80 | 57 | 22.3618 | 450000 | 413000 | 31.8 | 10000 | 2281.7598 |  | 1
75 | 80 | 75 | 79.7527 | 625000 | 219000 | 33.8 | 12500 | 3852.9441 |  | 1
75 | 80 | 72 | 68.6171 | 598000 | 248000 | 33.3 | 12500 | 3852.9441 |  | 1
75 | 80 | 67 | 51.5724 | 549000 | 308000 | 32.5 | 12500 | 3852.9441 |  | 1
75 | 80 | 62 | 36.2232 | 502000 | 370000 | 31.9 | 12500 | 3852.9441 |  | 1
75 | 80 | 57 | 22.3618 | 465000 | 450000 | 31.4 | 12500 | 3623.7263 |  | 1
75 | 80 | 75 | 79.7527 | 652000 | 228000 | 34.2 | 15000 | 5749.2011 |  | 1
75 | 80 | 72 | 68.6171 | 619000 | 256000 | 33.7 | 15000 | 5749.2011 |  | 1
75 | 80 | 67 | 51.5724 | 571000 | 336000 | 32.9 | 15000 | 5749.2011 |  | 1
75 | 80 | 62 | 36.2232 | 524000 | 406000 | 32.3 | 15000 | 5749.2011 |  | 1
75 | 80 | 57 | 22.3618 | 491000 | 480000 | 31.6 | 15000 | 5478.3073 |  | 1
75 | 80 | 75 | 79.7527 | 671000 | 235000 | 34.5 | 17500 | 8233.0894 |  | 1
75 | 80 | 72 | 68.6171 | 638000 | 281000 | 34 | 17500 | 8233.0894 |  | 1
75 | 80 | 67 | 51.5724 | 588000 | 362000 | 33.2 | 17500 | 8233.0894 |  | 1
75 | 80 | 62 | 36.2232 | 551000 | 473000 | 32.5 | 17500 | 8233.0894 |  | 1
75 | 80 | 57 | 22.3618 | 513000 | 513000 | 32 | 17500 | 8233.0894 |  | 1
85 | 80 | 75 | 79.7527 | 565000 | 184000 | 36.7 | 10000 | 2477.6369 |  | 1
85 | 80 | 72 | 68.6171 | 538000 | 213000 | 36.2 | 10000 | 2477.6369 |  | 1
85 | 80 | 67 | 51.5724 | 493000 | 256000 | 35.6 | 10000 | 2281.7598 |  | 1
85 | 80 | 62 | 36.2232 | 450000 | 312000 | 35.2 | 10000 | 2281.7598 |  | 1
85 | 80 | 57 | 22.3618 | 429000 | 397000 | 35.5 | 10000 | 2281.7598 |  | 1
85 | 80 | 75 | 79.7527 | 598000 | 194000 | 37.3 | 12500 | 3852.9441 |  | 1
85 | 80 | 72 | 68.6171 | 572000 | 228000 | 36.8 | 12500 | 3852.9441 |  | 1
85 | 80 | 67 | 51.5724 | 525000 | 290000 | 36.1 | 12500 | 3852.9441 |  | 1
85 | 80 | 62 | 36.2232 | 479000 | 353000 | 35.6 | 12500 | 3623.7263 |  | 1
85 | 80 | 57 | 22.3618 | 445000 | 431000 | 35 | 12500 | 3623.7263 |  | 1
85 | 80 | 75 | 79.7527 | 620000 | 206000 | 37.7 | 15000 | 5749.2011 |  | 1
85 | 80 | 72 | 68.6171 | 590000 | 234000 | 37.2 | 15000 | 5749.2011 |  | 1
85 | 80 | 67 | 51.5724 | 545000 | 317000 | 36.5 | 15000 | 5749.2011 |  | 1
85 | 80 | 62 | 36.2232 | 500000 | 388000 | 35.9 | 15000 | 5478.3073 |  | 1
85 | 80 | 57 | 22.3618 | 467000 | 467000 | 35.4 | 15000 | 5478.3073 |  | 1
85 | 80 | 75 | 79.7527 | 638000 | 212000 | 38 | 17500 | 8233.0894 |  | 1
85 | 80 | 72 | 68.6171 | 610000 | 260000 | 37.5 | 17500 | 8233.0894 |  | 1
85 | 80 | 67 | 51.5724 | 562000 | 343000 | 36.8 | 17500 | 8233.0894 |  | 1
85 | 80 | 62 | 36.2232 | 513000 | 420000 | 36.2 | 17500 | 8233.0894 |  | 1
85 | 80 | 57 | 22.3618 | 492000 | 492000 | 35.8 | 17500 | 7912.1844 |  | 1
95 | 80 | 75 | 79.7527 | 538000 | 163000 | 40.8 | 10000 | 2477.6369 |  | 1
95 | 80 | 72 | 68.6171 | 513000 | 195000 | 40.4 | 10000 | 2477.6369 |  | 1
95 | 80 | 67 | 51.5724 | 466000 | 236000 | 39.9 | 10000 | 2281.7598 |  | 1
95 | 80 | 62 | 36.2232 | 424000 | 293000 | 39.5 | 10000 | 2281.7598 |  | 1
95 | 80 | 57 | 22.3618 | 407000 | 380000 | 40.4 | 10000 | 2281.7598 |  | 1
95 | 80 | 75 | 79.7527 | 568000 | 172000 | 41.4 | 12500 | 3852.9441 |  | 1
95 | 80 | 72 | 68.6171 | 544000 | 208000 | 41 | 12500 | 3852.9441 |  | 1
95 | 80 | 67 | 51.5724 | 498000 | 270000 | 40.4 | 12500 | 3623.7263 |  | 1
95 | 80 | 62 | 36.2232 | 451000 | 332000 | 39.9 | 12500 | 3623.7263 |  | 1
95 | 80 | 57 | 22.3618 | 436000 | 424000 | 40.6 | 12500 | 3623.7263 |  | 1
95 | 80 | 75 | 79.7527 | 593000 | 177000 | 41.9 | 15000 | 5749.2011 |  | 1
95 | 80 | 72 | 68.6171 | 563000 | 215000 | 41.4 | 15000 | 5749.2011 |  | 1
95 | 80 | 67 | 51.5724 | 517000 | 296000 | 40.8 | 15000 | 5749.2011 |  | 1
95 | 80 | 62 | 36.2232 | 473000 | 369000 | 40.3 | 15000 | 5478.3073 |  | 1
95 | 80 | 57 | 22.3618 | 444000 | 444000 | 39.9 | 15000 | 5478.3073 |  | 1
95 | 80 | 75 | 79.7527 | 607000 | 189000 | 42.2 | 17500 | 8233.0894 |  | 1
95 | 80 | 72 | 68.6171 | 581000 | 238000 | 41.7 | 17500 | 8233.0894 |  | 1
95 | 80 | 67 | 51.5724 | 533000 | 322000 | 41.1 | 17500 | 8233.0894 |  | 1
95 | 80 | 62 | 36.2232 | 487000 | 402000 | 40.5 | 17500 | 7912.1844 |  | 1
95 | 80 | 57 | 22.3618 | 467000 | 467000 | 40.1 | 17500 | 7912.1844 |  | 1
105 | 80 | 75 | 79.7527 | 507000 | 140000 | 45.6 | 10000 | 2477.6369 |  | 1
105 | 80 | 72 | 68.6171 | 483000 | 174000 | 45.3 | 10000 | 2281.7598 |  | 1
105 | 80 | 67 | 51.5724 | 439000 | 216000 | 44.9 | 10000 | 2281.7598 |  | 1
105 | 80 | 62 | 36.2232 | 398000 | 274000 | 45 | 10000 | 2090.0503 |  | 1
105 | 80 | 57 | 22.3618 | 383000 | 360000 | 46.4 | 10000 | 2090.0503 |  | 1
105 | 80 | 75 | 79.7527 | 537000 | 148000 | 46.2 | 12500 | 3852.9441 |  | 1
105 | 80 | 72 | 68.6171 | 511000 | 177000 | 45.9 | 12500 | 3852.9441 |  | 1
105 | 80 | 67 | 51.5724 | 469000 | 250000 | 45.4 | 12500 | 3623.7263 |  | 1
105 | 80 | 62 | 36.2232 | 423000 | 311000 | 45.3 | 12500 | 3623.7263 |  | 1
105 | 80 | 57 | 22.3618 | 398000 | 388000 | 45.3 | 12500 | 3396.5922 |  | 1
105 | 80 | 75 | 79.7527 | 559000 | 154000 | 46.7 | 15000 | 5749.2011 |  | 1
105 | 80 | 72 | 68.6171 | 533000 | 196000 | 46.3 | 15000 | 5749.2011 |  | 1
105 | 80 | 67 | 51.5724 | 486000 | 275000 | 45.8 | 15000 | 5478.3073 |  | 1
105 | 80 | 62 | 36.2232 | 445000 | 350000 | 45.5 | 15000 | 5478.3073 |  | 1
105 | 80 | 57 | 22.3618 | 420000 | 420000 | 45.5 | 15000 | 5478.3073 |  | 1
105 | 80 | 75 | 79.7527 | 572000 | 164000 | 46.9 | 17500 | 8233.0894 |  | 1
105 | 80 | 72 | 68.6171 | 547000 | 215000 | 46.6 | 17500 | 8233.0894 |  | 1
105 | 80 | 67 | 51.5724 | 502000 | 301000 | 46.1 | 17500 | 8233.0894 |  | 1
105 | 80 | 62 | 36.2232 | 458000 | 382000 | 45.8 | 17500 | 7912.1844 |  | 1
105 | 80 | 57 | 22.3618 | 442000 | 442000 | 45.6 | 17500 | 7912.1844 |  | 1
115 | 80 | 75 | 79.7527 | 474000 | 116000 | 51.1 | 10000 | 2281.7598 |  | 1
115 | 80 | 72 | 68.6171 | 454000 | 145000 | 51 | 10000 | 2281.7598 |  | 1
115 | 80 | 67 | 51.5724 | 429000 | 224000 | 51.3 | 10000 | 2281.7598 |  | 1
115 | 80 | 62 | 36.2232 | 399000 | 294000 | 52.7 | 10000 | 2090.0503 |  | 1
115 | 80 | 57 | 22.3618 | 343000 | 321000 | 52.2 | 10000 | 1902.5084 |  | 1
115 | 80 | 75 | 79.7527 | 501000 | 124000 | 51.7 | 12500 | 3852.9441 |  | 1
115 | 80 | 72 | 68.6171 | 477000 | 155000 | 51.5 | 12500 | 3623.7263 |  | 1
115 | 80 | 67 | 51.5724 | 454000 | 253000 | 51.6 | 12500 | 3623.7263 |  | 1
115 | 80 | 62 | 36.2232 | 408000 | 320000 | 52.1 | 12500 | 3623.7263 |  | 1
115 | 80 | 57 | 22.3618 | 375000 | 366000 | 52.3 | 12500 | 3396.5922 |  | 1
115 | 80 | 75 | 79.7527 | 521000 | 129000 | 52.1 | 15000 | 5749.2011 |  | 1
115 | 80 | 72 | 68.6171 | 497000 | 173000 | 51.9 | 15000 | 5478.3073 |  | 1
115 | 80 | 67 | 51.5724 | 470000 | 280000 | 51.9 | 15000 | 5478.3073 |  | 1
115 | 80 | 62 | 36.2232 | 424000 | 357000 | 52.1 | 15000 | 5478.3073 |  | 1
115 | 80 | 57 | 22.3618 | 394000 | 394000 | 52.3 | 15000 | 5205.3296 |  | 1
115 | 80 | 75 | 79.7527 | 534000 | 138000 | 52.4 | 17500 | 8233.0894 |  | 1
115 | 80 | 72 | 68.6171 | 510000 | 191000 | 52.2 | 17500 | 8233.0894 |  | 1
115 | 80 | 67 | 51.5724 | 483000 | 305000 | 52 | 17500 | 7912.1844 |  | 1
115 | 80 | 62 | 36.2232 | 434000 | 388000 | 52.1 | 17500 | 7912.1844 |  | 1
115 | 80 | 57 | 22.3618 | 415000 | 415000 | 52.2 | 17500 | 7912.1844 |  | 1
75 | 80 | 75 | 79.7527 | 684000 | 241000 | 34.8 | 20000 | 11383.7933 |  | 1
75 | 80 | 72 | 68.6171 | 650000 | 296000 | 34.2 | 20000 | 11383.7933 |  | 1
75 | 80 | 67 | 51.5724 | 599000 | 383000 | 33.4 | 20000 | 11383.7933 |  | 1
75 | 80 | 62 | 36.2232 | 562000 | 503000 | 32.7 | 20000 | 11383.7933 |  | 1
75 | 80 | 57 | 22.3618 | 531000 | 531000 | 32.3 | 20000 | 11383.7933 |  | 1
85 | 80 | 75 | 79.7527 | 650000 | 217000 | 38.3 | 20000 | 11383.7933 |  | 1
85 | 80 | 72 | 68.6171 | 621000 | 274000 | 37.7 | 20000 | 11383.7933 |  | 1
85 | 80 | 67 | 51.5724 | 573000 | 363000 | 36.9 | 20000 | 11383.7933 |  | 1
85 | 80 | 62 | 36.2232 | 536000 | 483000 | 36.3 | 20000 | 11383.7933 |  | 1
85 | 80 | 57 | 22.3618 | 508000 | 508000 | 36 | 20000 | 11383.7933 |  | 1
95 | 80 | 75 | 79.7527 | 618000 | 194000 | 42.4 | 20000 | 11383.7933 |  | 1
95 | 80 | 72 | 68.6171 | 591000 | 251000 | 41.9 | 20000 | 11383.7933 |  | 1
95 | 80 | 67 | 51.5724 | 543000 | 342000 | 41.3 | 20000 | 11383.7933 |  | 1
95 | 80 | 62 | 36.2232 | 497000 | 427000 | 40.7 | 20000 | 11012.8771 |  | 1
95 | 80 | 57 | 22.3618 | 484000 | 484000 | 40.4 | 20000 | 11012.8771 |  | 1
105 | 80 | 75 | 79.7527 | 583000 | 169000 | 47.2 | 20000 | 11383.7933 |  | 1
105 | 80 | 72 | 68.6171 | 557000 | 228000 | 46.8 | 20000 | 11383.7933 |  | 1
105 | 80 | 67 | 51.5724 | 511000 | 320000 | 46.2 | 20000 | 11383.7933 |  | 1
105 | 80 | 62 | 36.2232 | 492000 | 447000 | 46.2 | 20000 | 11012.8771 |  | 1
105 | 80 | 57 | 22.3618 | 458000 | 458000 | 45.6 | 20000 | 11012.8771 |  | 1
115 | 80 | 75 | 79.7527 | 544000 | 142000 | 52.6 | 20000 | 11383.7933 |  | 1
115 | 80 | 72 | 68.6171 | 519000 | 203000 | 52.3 | 20000 | 11383.7933 |  | 1
115 | 80 | 67 | 51.5724 | 492000 | 326000 | 52.1 | 20000 | 11012.8771 |  | 1
115 | 80 | 62 | 36.2232 | 448000 | 406000 | 51.9 | 20000 | 11012.8771 |  | 1
115 | 80 | 57 | 22.3618 | 430000 | 430000 | 52.1 | 20000 | 11012.8771 |  | 1
75 | 80 | 75 | 79.7527 | 589000 | 191000 | 33.4 | 10000 | 2477.6369 |  | 2
75 | 80 | 72 | 68.6171 | 555000 | 216000 | 32.8 | 10000 | 2477.6369 |  | 2
75 | 80 | 67 | 51.5724 | 500000 | 261000 | 32 | 10000 | 2281.7598 |  | 2
75 | 80 | 62 | 36.2232 | 454000 | 316000 | 31.2 | 10000 | 2281.7598 |  | 2
75 | 80 | 57 | 22.3618 | 407000 | 365000 | 30.5 | 10000 | 2281.7598 |  | 2
75 | 80 | 75 | 79.7527 | 633000 | 209000 | 34.2 | 12500 | 3852.9441 |  | 2
75 | 80 | 72 | 68.6171 | 597000 | 238000 | 33.6 | 12500 | 3852.9441 |  | 2
75 | 80 | 67 | 51.5724 | 538000 | 301000 | 32.5 | 12500 | 3852.9441 |  | 2
75 | 80 | 62 | 36.2232 | 489000 | 366000 | 31.7 | 12500 | 3623.7263 |  | 2
75 | 80 | 57 | 22.3618 | 452000 | 427000 | 31.1 | 12500 | 3623.7263 |  | 2
75 | 80 | 75 | 79.7527 | 673000 | 241000 | 35.1 | 15000 | 5749.2011 |  | 2
75 | 80 | 72 | 68.6171 | 619000 | 260000 | 33.9 | 15000 | 5749.2011 |  | 2
75 | 80 | 67 | 51.5724 | 563000 | 335000 | 33 | 15000 | 5749.2011 |  | 2
75 | 80 | 62 | 36.2232 | 515000 | 411000 | 32.1 | 15000 | 5749.2011 |  | 2
75 | 80 | 57 | 22.3618 | 482000 | 468000 | 31.5 | 15000 | 5478.3073 |  | 2
75 | 80 | 75 | 79.7527 | 697000 | 251000 | 35.4 | 17500 | 8233.0894 |  | 2
75 | 80 | 72 | 68.6171 | 653000 | 297000 | 34.6 | 17500 | 8233.0894 |  | 2
75 | 80 | 67 | 51.5724 | 583000 | 367000 | 33.3 | 17500 | 8233.0894 |  | 2
75 | 80 | 62 | 36.2232 | 534000 | 452000 | 32.4 | 17500 | 8233.0894 |  | 2
75 | 80 | 57 | 22.3618 | 509000 | 509000 | 32 | 17500 | 8233.0894 |  | 2
85 | 80 | 75 | 79.7527 | 552000 | 160000 | 36.7 | 10000 | 2477.6369 |  | 2
85 | 80 | 72 | 68.6171 | 523000 | 190000 | 36.1 | 10000 | 2477.6369 |  | 2
85 | 80 | 67 | 51.5724 | 468000 | 233000 | 35.2 | 10000 | 2281.7598 |  | 2
85 | 80 | 62 | 36.2232 | 445000 | 300000 | 34.7 | 10000 | 2281.7598 |  | 2
85 | 80 | 57 | 22.3618 | 408000 | 371000 | 34.3 | 10000 | 2281.7598 |  | 2
85 | 80 | 75 | 79.7527 | 592000 | 175000 | 37.4 | 12500 | 3852.9441 |  | 2
85 | 80 | 72 | 68.6171 | 557000 | 205000 | 36.8 | 12500 | 3852.9441 |  | 2
85 | 80 | 67 | 51.5724 | 506000 | 275000 | 35.8 | 12500 | 3852.9441 |  | 2
85 | 80 | 62 | 36.2232 | 470000 | 345000 | 35.1 | 12500 | 3623.7263 |  | 2
85 | 80 | 57 | 22.3618 | 436000 | 424000 | 34.6 | 12500 | 3623.7263 |  | 2
85 | 80 | 75 | 79.7527 | 618000 | 192000 | 37.9 | 15000 | 5749.2011 |  | 2
85 | 80 | 72 | 68.6171 | 581000 | 228000 | 37.2 | 15000 | 5749.2011 |  | 2
85 | 80 | 67 | 51.5724 | 531000 | 309000 | 36.3 | 15000 | 5749.2011 |  | 2
85 | 80 | 62 | 36.2232 | 488000 | 390000 | 35.5 | 15000 | 5478.3073 |  | 2
85 | 80 | 57 | 22.3618 | 460000 | 460000 | 35 | 15000 | 5478.3073 |  | 2
85 | 80 | 75 | 79.7527 | 640000 | 201000 | 38.3 | 17500 | 8233.0894 |  | 2
85 | 80 | 72 | 68.6171 | 601000 | 252000 | 37.6 | 17500 | 8233.0894 |  | 2
85 | 80 | 67 | 51.5724 | 550000 | 340000 | 36.6 | 17500 | 8233.0894 |  | 2
85 | 80 | 62 | 36.2232 | 502000 | 432000 | 35.8 | 17500 | 8233.0894 |  | 2
85 | 80 | 57 | 22.3618 | 483000 | 483000 | 35.4 | 17500 | 7912.1844 |  | 2
95 | 80 | 75 | 79.7527 | 514000 | 128000 | 40.5 | 10000 | 2477.6369 |  | 2
95 | 80 | 72 | 68.6171 | 485000 | 159000 | 39.9 | 10000 | 2281.7598 |  | 2
95 | 80 | 67 | 51.5724 | 436000 | 206000 | 39.1 | 10000 | 2281.7598 |  | 2
95 | 80 | 62 | 36.2232 | 418000 | 279000 | 38.9 | 10000 | 2281.7598 |  | 2
95 | 80 | 57 | 22.3618 | 382000 | 350000 | 38.5 | 10000 | 2090.0503 |  | 2
95 | 80 | 75 | 79.7527 | 551000 | 142000 | 41.2 | 12500 | 3852.9441 |  | 2
95 | 80 | 72 | 68.6171 | 510000 | 162000 | 40.5 | 12500 | 3852.9441 |  | 2
95 | 80 | 67 | 51.5724 | 475000 | 249000 | 39.8 | 12500 | 3623.7263 |  | 2
95 | 80 | 62 | 36.2232 | 441000 | 323000 | 39.3 | 12500 | 3623.7263 |  | 2
95 | 80 | 57 | 22.3618 | 417000 | 406000 | 38.9 | 12500 | 3623.7263 |  | 2
95 | 80 | 75 | 79.7527 | 575000 | 158000 | 41.7 | 15000 | 5749.2011 |  | 2
95 | 80 | 72 | 68.6171 | 543000 | 198000 | 41.1 | 15000 | 5749.2011 |  | 2
95 | 80 | 67 | 51.5724 | 499000 | 282000 | 40.3 | 15000 | 5478.3073 |  | 2
95 | 80 | 62 | 36.2232 | 457000 | 365000 | 39.7 | 15000 | 5478.3073 |  | 2
95 | 80 | 57 | 22.3618 | 435000 | 435000 | 39.2 | 15000 | 5478.3073 |  | 2
95 | 80 | 75 | 79.7527 | 597000 | 166000 | 42.2 | 17500 | 8233.0894 |  | 2
95 | 80 | 72 | 68.6171 | 564000 | 221000 | 41.5 | 17500 | 8233.0894 |  | 2
95 | 80 | 67 | 51.5724 | 518000 | 314000 | 40.7 | 17500 | 8233.0894 |  | 2
95 | 80 | 62 | 36.2232 | 470000 | 405000 | 39.9 | 17500 | 7912.1844 |  | 2
95 | 80 | 57 | 22.3618 | 453000 | 453000 | 39.5 | 17500 | 7912.1844 |  | 2
105 | 80 | 75 | 79.7527 | 477000 | 97000 | 44.9 | 10000 | 2281.7598 |  | 2
105 | 80 | 72 | 68.6171 | 450000 | 130000 | 44.5 | 10000 | 2281.7598 |  | 2
105 | 80 | 67 | 51.5724 | 402000 | 179000 | 43.9 | 10000 | 2281.7598 |  | 2
105 | 80 | 62 | 36.2232 | 387000 | 255000 | 43.9 | 10000 | 2090.0503 |  | 2
105 | 80 | 57 | 22.3618 | 365000 | 334000 | 43.6 | 10000 | 2090.0503 |  | 2
105 | 80 | 75 | 79.7527 | 511000 | 110000 | 45.7 | 12500 | 3852.9441 |  | 2
105 | 80 | 72 | 68.6171 | 473000 | 131000 | 45.1 | 12500 | 3623.7263 |  | 2
105 | 80 | 67 | 51.5724 | 440000 | 222000 | 44.6 | 12500 | 3623.7263 |  | 2
105 | 80 | 62 | 36.2232 | 408000 | 298000 | 44.3 | 12500 | 3623.7263 |  | 2
105 | 80 | 57 | 22.3618 | 363000 | 354000 | 43.8 | 12500 | 3396.5922 |  | 2
105 | 80 | 75 | 79.7527 | 537000 | 121000 | 46.3 | 15000 | 5749.2011 |  | 2
105 | 80 | 72 | 68.6171 | 504000 | 166000 | 45.7 | 15000 | 5749.2011 |  | 2
105 | 80 | 67 | 51.5724 | 464000 | 255000 | 45.1 | 15000 | 5478.3073 |  | 2
105 | 80 | 62 | 36.2232 | 423000 | 339000 | 44.7 | 15000 | 5478.3073 |  | 2
105 | 80 | 57 | 22.3618 | 405000 | 405000 | 44.2 | 15000 | 5478.3073 |  | 2
105 | 80 | 75 | 79.7527 | 555000 | 133000 | 46.7 | 17500 | 8233.0894 |  | 2
105 | 80 | 72 | 68.6171 | 525000 | 191000 | 46.2 | 17500 | 8233.0894 |  | 2
105 | 80 | 67 | 51.5724 | 482000 | 286000 | 45.5 | 17500 | 7912.1844 |  | 2
105 | 80 | 62 | 36.2232 | 436000 | 378000 | 44.8 | 17500 | 7912.1844 |  | 2
105 | 80 | 57 | 22.3618 | 425000 | 425000 | 44.5 | 17500 | 7912.1844 |  | 2
115 | 80 | 75 | 79.7527 | 438000 | 64000 | 50.1 | 10000 | 2281.7598 |  | 2
115 | 80 | 72 | 68.6171 | 412000 | 100000 | 49.9 | 10000 | 2281.7598 |  | 2
115 | 80 | 67 | 51.5724 | 365000 | 151000 | 49.6 | 10000 | 2090.0503 |  | 2
115 | 80 | 62 | 36.2232 | 353000 | 230000 | 50.5 | 10000 | 2090.0503 |  | 2
115 | 80 | 57 | 22.3618 | 340000 | 314000 | 51.4 | 10000 | 1902.5084 |  | 2
115 | 80 | 75 | 79.7527 | 469000 | 77000 | 50.9 | 12500 | 3623.7263 |  | 2
115 | 80 | 72 | 68.6171 | 430000 | 99000 | 50.4 | 12500 | 3623.7263 |  | 2
115 | 80 | 67 | 51.5724 | 402000 | 194000 | 50.3 | 12500 | 3623.7263 |  | 2
115 | 80 | 62 | 36.2232 | 372000 | 271000 | 50.9 | 12500 | 3396.5922 |  | 2
115 | 80 | 57 | 22.3618 | 333000 | 326000 | 50.6 | 12500 | 3171.5419 |  | 2
115 | 80 | 75 | 79.7527 | 493000 | 87000 | 51.5 | 15000 | 5478.3073 |  | 2
115 | 80 | 72 | 68.6171 | 461000 | 134000 | 51.1 | 15000 | 5478.3073 |  | 2
115 | 80 | 67 | 51.5724 | 424000 | 226000 | 50.8 | 15000 | 5478.3073 |  | 2
115 | 80 | 62 | 36.2232 | 387000 | 312000 | 51 | 15000 | 5205.3296 |  | 2
115 | 80 | 57 | 22.3618 | 381000 | 381000 | 50.7 | 15000 | 5205.3296 |  | 2
115 | 80 | 75 | 79.7527 | 511000 | 99000 | 52 | 17500 | 8233.0894 |  | 2
115 | 80 | 72 | 68.6171 | 482000 | 159000 | 51.5 | 17500 | 7912.1844 |  | 2
115 | 80 | 67 | 51.5724 | 441000 | 256000 | 51.1 | 17500 | 7912.1844 |  | 2
115 | 80 | 62 | 36.2232 | 400000 | 345000 | 50.2 | 17500 | 7589.1955 |  | 2
115 | 80 | 57 | 22.3618 | 398000 | 398000 | 50.7 | 17500 | 7589.1955 |  | 2
75 | 80 | 75 | 79.7527 | 707000 | 262000 | 35.6 | 20000 | 11383.7933 |  | 2
75 | 80 | 72 | 68.6171 | 650000 | 298000 | 34.3 | 20000 | 11383.7933 |  | 2
75 | 80 | 67 | 51.5724 | 597000 | 395000 | 33.5 | 20000 | 11383.7933 |  | 2
75 | 80 | 62 | 36.2232 | 548000 | 487000 | 32.7 | 20000 | 11383.7933 |  | 2
75 | 80 | 57 | 22.3618 | 527000 | 527000 | 32.3 | 20000 | 11383.7933 |  | 2
85 | 80 | 75 | 79.7527 | 650000 | 211000 | 38.5 | 20000 | 11383.7933 |  | 2
85 | 80 | 72 | 68.6171 | 616000 | 271000 | 37.9 | 20000 | 11383.7933 |  | 2
85 | 80 | 67 | 51.5724 | 564000 | 369000 | 36.9 | 20000 | 11383.7933 |  | 2
85 | 80 | 62 | 36.2232 | 517000 | 473000 | 36.1 | 20000 | 11383.7933 |  | 2
85 | 80 | 57 | 22.3618 | 506000 | 506000 | 35.8 | 20000 | 11383.7933 |  | 2
95 | 80 | 75 | 79.7527 | 611000 | 181000 | 42.5 | 20000 | 11383.7933 |  | 2
95 | 80 | 72 | 68.6171 | 579000 | 242000 | 41.8 | 20000 | 11383.7933 |  | 2
95 | 80 | 67 | 51.5724 | 532000 | 342000 | 40.9 | 20000 | 11383.7933 |  | 2
95 | 80 | 62 | 36.2232 | 500000 | 458000 | 40.2 | 20000 | 11012.8771 |  | 2
95 | 80 | 57 | 22.3618 | 471000 | 471000 | 39.8 | 20000 | 11012.8771 |  | 2
105 | 80 | 75 | 79.7527 | 570000 | 148000 | 47.1 | 20000 | 11383.7933 |  | 2
105 | 80 | 72 | 68.6171 | 539000 | 211000 | 46.5 | 20000 | 11383.7933 |  | 2
105 | 80 | 67 | 51.5724 | 496000 | 315000 | 45.8 | 20000 | 11012.8771 |  | 2
105 | 80 | 62 | 36.2232 | 446000 | 411000 | 44.9 | 20000 | 11012.8771 |  | 2
105 | 80 | 57 | 22.3618 | 442000 | 442000 | 44.8 | 20000 | 11012.8771 |  | 2
115 | 80 | 75 | 79.7527 | 524000 | 115000 | 52.4 | 20000 | 11383.7933 |  | 2
115 | 80 | 72 | 68.6171 | 495000 | 178000 | 51.8 | 20000 | 11012.8771 |  | 2
115 | 80 | 67 | 51.5724 | 454000 | 285000 | 51.4 | 20000 | 11012.8771 |  | 2
115 | 80 | 62 | 36.2232 | 411000 | 378000 | 50.6 | 20000 | 11012.8771 |  | 2
115 | 80 | 57 | 22.3618 | 403000 | 403000 | 50.6 | 20000 | 11012.8771 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 13
Degradation Coefficient (C_d) |  | 48/50 055 (55 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 648000 | 206000 | 41.9 | 11000 | 2335.9385 |  | 1
75 | 80 | 72 | 68.6171 | 613000 | 244000 | 41.3 | 11000 | 2335.9385 |  | 1
75 | 80 | 67 | 51.5724 | 562000 | 311000 | 40.5 | 11000 | 2335.9385 |  | 1
75 | 80 | 62 | 36.2232 | 501000 | 364000 | 39.7 | 11000 | 2335.9385 |  | 1
75 | 80 | 57 | 22.3618 | 464000 | 434000 | 39.2 | 11000 | 2073.3799 |  | 1
75 | 80 | 75 | 79.7527 | 681000 | 221000 | 42.5 | 13750 | 3165.2905 |  | 1
75 | 80 | 72 | 68.6171 | 647000 | 269000 | 41.9 | 13750 | 3165.2905 |  | 1
75 | 80 | 67 | 51.5724 | 598000 | 354000 | 41.2 | 13750 | 3165.2905 |  | 1
75 | 80 | 62 | 36.2232 | 541000 | 424000 | 40.2 | 13750 | 3165.2905 |  | 1
75 | 80 | 57 | 22.3618 | 494000 | 487000 | 39.6 | 13750 | 2894.3966 |  | 1
75 | 80 | 75 | 79.7527 | 704000 | 236000 | 43 | 16500 | 4344.7207 |  | 1
75 | 80 | 72 | 68.6171 | 668000 | 290000 | 42.3 | 16500 | 4344.7207 |  | 1
75 | 80 | 67 | 51.5724 | 615000 | 383000 | 41.4 | 16500 | 4344.7207 |  | 1
75 | 80 | 62 | 36.2232 | 561000 | 471000 | 40.5 | 16500 | 4344.7207 |  | 1
75 | 80 | 57 | 22.3618 | 523000 | 523000 | 40 | 16500 | 4344.7207 |  | 1
75 | 80 | 75 | 79.7527 | 719000 | 248000 | 43.3 | 19250 | 5872.1453 |  | 1
75 | 80 | 72 | 68.6171 | 684000 | 310000 | 42.6 | 19250 | 5872.1453 |  | 1
75 | 80 | 67 | 51.5724 | 630000 | 415000 | 41.6 | 19250 | 5872.1453 |  | 1
75 | 80 | 62 | 36.2232 | 578000 | 515000 | 40.8 | 19250 | 5872.1453 |  | 1
75 | 80 | 57 | 22.3618 | 549000 | 549000 | 40.3 | 19250 | 5872.1453 |  | 1
85 | 80 | 75 | 79.7527 | 573000 | 139000 | 44.8 | 11000 | 2335.9385 |  | 1
85 | 80 | 72 | 68.6171 | 588000 | 226000 | 45.1 | 11000 | 2335.9385 |  | 1
85 | 80 | 67 | 51.5724 | 536000 | 292000 | 44.3 | 11000 | 2335.9385 |  | 1
85 | 80 | 62 | 36.2232 | 488000 | 357000 | 43.7 | 11000 | 2073.3799 |  | 1
85 | 80 | 57 | 22.3618 | 443000 | 416000 | 43 | 11000 | 2073.3799 |  | 1
85 | 80 | 75 | 79.7527 | 652000 | 200000 | 46.2 | 13750 | 3165.2905 |  | 1
85 | 80 | 72 | 68.6171 | 619000 | 249000 | 45.6 | 13750 | 3165.2905 |  | 1
85 | 80 | 67 | 51.5724 | 567000 | 329000 | 44.8 | 13750 | 3165.2905 |  | 1
85 | 80 | 62 | 36.2232 | 516000 | 407000 | 44.1 | 13750 | 3165.2905 |  | 1
85 | 80 | 57 | 22.3618 | 472000 | 466000 | 43.4 | 13750 | 2894.3966 |  | 1
85 | 80 | 75 | 79.7527 | 672000 | 213000 | 46.6 | 16500 | 4344.7207 |  | 1
85 | 80 | 72 | 68.6171 | 639000 | 269000 | 46 | 16500 | 4344.7207 |  | 1
85 | 80 | 67 | 51.5724 | 586000 | 361000 | 45.1 | 16500 | 4344.7207 |  | 1
85 | 80 | 62 | 36.2232 | 537000 | 453000 | 44.3 | 16500 | 4344.7207 |  | 1
85 | 80 | 57 | 22.3618 | 500000 | 500000 | 43.8 | 16500 | 4048.8212 |  | 1
85 | 80 | 75 | 79.7527 | 687000 | 225000 | 46.9 | 19250 | 5872.1453 |  | 1
85 | 80 | 72 | 68.6171 | 654000 | 289000 | 46.3 | 19250 | 5872.1453 |  | 1
85 | 80 | 67 | 51.5724 | 602000 | 394000 | 45.3 | 19250 | 5872.1453 |  | 1
85 | 80 | 62 | 36.2232 | 551000 | 495000 | 44.5 | 19250 | 5872.1453 |  | 1
85 | 80 | 57 | 22.3618 | 525000 | 525000 | 44.2 | 19250 | 5872.1453 |  | 1
95 | 80 | 75 | 79.7527 | 591000 | 165000 | 50 | 11000 | 2335.9385 |  | 1
95 | 80 | 72 | 68.6171 | 560000 | 206000 | 49.5 | 11000 | 2335.9385 |  | 1
95 | 80 | 67 | 51.5724 | 510000 | 273000 | 48.8 | 11000 | 2335.9385 |  | 1
95 | 80 | 62 | 36.2232 | 463000 | 338000 | 48.1 | 11000 | 2073.3799 |  | 1
95 | 80 | 57 | 22.3618 | 422000 | 403000 | 47.7 | 11000 | 2073.3799 |  | 1
95 | 80 | 75 | 79.7527 | 621000 | 178000 | 50.5 | 13750 | 3165.2905 |  | 1
95 | 80 | 72 | 68.6171 | 515000 | 154000 | 48.6 | 13750 | 3165.2905 |  | 1
95 | 80 | 67 | 51.5724 | 538000 | 309000 | 49.2 | 13750 | 3165.2905 |  | 1
95 | 80 | 62 | 36.2232 | 490000 | 388000 | 48.5 | 13750 | 2894.3966 |  | 1
95 | 80 | 57 | 22.3618 | 455000 | 455000 | 48.4 | 13750 | 2894.3966 |  | 1
95 | 80 | 75 | 79.7527 | 640000 | 191000 | 50.9 | 16500 | 4344.7207 |  | 1
95 | 80 | 72 | 68.6171 | 533000 | 172000 | 48.9 | 16500 | 4344.7207 |  | 1
95 | 80 | 67 | 51.5724 | 558000 | 342000 | 49.4 | 16500 | 4344.7207 |  | 1
95 | 80 | 62 | 36.2232 | 509000 | 433000 | 48.7 | 16500 | 4344.7207 |  | 1
95 | 80 | 57 | 22.3618 | 476000 | 476000 | 48.2 | 16500 | 4048.8212 |  | 1
95 | 80 | 75 | 79.7527 | 652000 | 200000 | 51.1 | 19250 | 5872.1453 |  | 1
95 | 80 | 72 | 68.6171 | 623000 | 267000 | 50.6 | 19250 | 5872.1453 |  | 1
95 | 80 | 67 | 51.5724 | 572000 | 373000 | 49.7 | 19250 | 5872.1453 |  | 1
95 | 80 | 62 | 36.2232 | 522000 | 473000 | 48.9 | 19250 | 5872.1453 |  | 1
95 | 80 | 57 | 22.3618 | 500000 | 500000 | 48.6 | 19250 | 5547.0726 |  | 1
105 | 80 | 75 | 79.7527 | 560000 | 143000 | 55 | 11000 | 2335.9385 |  | 1
105 | 80 | 72 | 68.6171 | 529000 | 185000 | 54.5 | 11000 | 2335.9385 |  | 1
105 | 80 | 67 | 51.5724 | 481000 | 253000 | 53.8 | 11000 | 2073.3799 |  | 1
105 | 80 | 62 | 36.2232 | 436000 | 319000 | 53.6 | 11000 | 2073.3799 |  | 1
105 | 80 | 57 | 22.3618 | 395000 | 374000 | 53.3 | 11000 | 1829.5754 |  | 1
105 | 80 | 75 | 79.7527 | 588000 | 156000 | 55.5 | 13750 | 3165.2905 |  | 1
105 | 80 | 72 | 68.6171 | 557000 | 205000 | 54.9 | 13750 | 3165.2905 |  | 1
105 | 80 | 67 | 51.5724 | 508000 | 288000 | 54.1 | 13750 | 3165.2905 |  | 1
105 | 80 | 62 | 36.2232 | 462000 | 368000 | 53.6 | 13750 | 2894.3966 |  | 1
105 | 80 | 57 | 22.3618 | 424000 | 424000 | 53.3 | 13750 | 2894.3966 |  | 1
105 | 80 | 75 | 79.7527 | 606000 | 167000 | 55.8 | 16500 | 4344.7207 |  | 1
105 | 80 | 72 | 68.6171 | 576000 | 225000 | 55.2 | 16500 | 4344.7207 |  | 1
105 | 80 | 67 | 51.5724 | 526000 | 320000 | 54.4 | 16500 | 4344.7207 |  | 1
105 | 80 | 62 | 36.2232 | 479000 | 411000 | 53.7 | 16500 | 4048.8212 |  | 1
105 | 80 | 57 | 22.3618 | 451000 | 451000 | 53.5 | 16500 | 4048.8212 |  | 1
105 | 80 | 75 | 79.7527 | 623000 | 183000 | 56.2 | 19250 | 5872.1453 |  | 1
105 | 80 | 72 | 68.6171 | 589000 | 243000 | 55.5 | 19250 | 5872.1453 |  | 1
105 | 80 | 67 | 51.5724 | 539000 | 351000 | 54.6 | 19250 | 5872.1453 |  | 1
105 | 80 | 62 | 36.2232 | 491000 | 450000 | 53.8 | 19250 | 5547.0726 |  | 1
105 | 80 | 57 | 22.3618 | 474000 | 474000 | 53.6 | 19250 | 5547.0726 |  | 1
115 | 80 | 75 | 79.7527 | 526000 | 121000 | 60.7 | 11000 | 2335.9385 |  | 1
115 | 80 | 72 | 68.6171 | 497000 | 163000 | 60.3 | 11000 | 2073.3799 |  | 1
115 | 80 | 67 | 51.5724 | 451000 | 232000 | 60 | 11000 | 2073.3799 |  | 1
115 | 80 | 62 | 36.2232 | 408000 | 299000 | 60.1 | 11000 | 2073.3799 |  | 1
115 | 80 | 57 | 22.3618 | 371000 | 352000 | 60 | 11000 | 1829.5754 |  | 1
115 | 80 | 75 | 79.7527 | 552000 | 132000 | 61 | 13750 | 3165.2905 |  | 1
115 | 80 | 72 | 68.6171 | 523000 | 183000 | 60.5 | 13750 | 3165.2905 |  | 1
115 | 80 | 67 | 51.5724 | 476000 | 266000 | 60 | 13750 | 2894.3966 |  | 1
115 | 80 | 62 | 36.2232 | 432000 | 347000 | 59.8 | 13750 | 2894.3966 |  | 1
115 | 80 | 57 | 22.3618 | 398000 | 398000 | 59.8 | 13750 | 2638.0894 |  | 1
115 | 80 | 75 | 79.7527 | 569000 | 143000 | 61.4 | 16500 | 4344.7207 |  | 1
115 | 80 | 72 | 68.6171 | 540000 | 201000 | 60.8 | 16500 | 4344.7207 |  | 1
115 | 80 | 67 | 51.5724 | 493000 | 298000 | 60.1 | 16500 | 4048.8212 |  | 1
115 | 80 | 62 | 36.2232 | 448000 | 389000 | 59.8 | 16500 | 4048.8212 |  | 1
115 | 80 | 57 | 22.3618 | 424000 | 424000 | 59.7 | 16500 | 4048.8212 |  | 1
115 | 80 | 75 | 79.7527 | 584000 | 157000 | 61.7 | 19250 | 5872.1453 |  | 1
115 | 80 | 72 | 68.6171 | 552000 | 219000 | 61 | 19250 | 5872.1453 |  | 1
115 | 80 | 67 | 51.5724 | 505000 | 328000 | 60.2 | 19250 | 5872.1453 |  | 1
115 | 80 | 62 | 36.2232 | 460000 | 422000 | 59.7 | 19250 | 5547.0726 |  | 1
115 | 80 | 57 | 22.3618 | 457000 | 457000 | 60.4 | 19250 | 5547.0726 |  | 1
75 | 80 | 75 | 79.7527 | 732000 | 260000 | 43.5 | 22000 | 7782.9888 |  | 1
75 | 80 | 72 | 68.6171 | 699000 | 332000 | 43 | 22000 | 7782.9888 |  | 1
75 | 80 | 67 | 51.5724 | 641000 | 445000 | 41.9 | 22000 | 7782.9888 |  | 1
75 | 80 | 62 | 36.2232 | 589000 | 553000 | 41 | 22000 | 7782.9888 |  | 1
75 | 80 | 57 | 22.3618 | 571000 | 571000 | 40.7 | 22000 | 7782.9888 |  | 1
75 | 80 | 75 | 79.7527 | 742000 | 272000 | 43.8 | 24750 | 10108.5084 |  | 1
75 | 80 | 72 | 68.6171 | 709000 | 350000 | 43.2 | 24750 | 10108.5084 |  | 1
75 | 80 | 67 | 51.5724 | 651000 | 474000 | 42.1 | 24750 | 10108.5084 |  | 1
75 | 80 | 62 | 36.2232 | 598000 | 584000 | 41.1 | 24750 | 10108.5084 |  | 1
75 | 80 | 57 | 22.3618 | 597000 | 597000 | 41.3 | 24750 | 10108.5084 |  | 1
85 | 80 | 75 | 79.7527 | 698000 | 237000 | 47.2 | 22000 | 7782.9888 |  | 1
85 | 80 | 72 | 68.6171 | 666000 | 307000 | 46.5 | 22000 | 7782.9888 |  | 1
85 | 80 | 67 | 51.5724 | 554000 | 366000 | 44.5 | 22000 | 7782.9888 |  | 1
85 | 80 | 62 | 36.2232 | 561000 | 531000 | 44.7 | 22000 | 7782.9888 |  | 1
85 | 80 | 57 | 22.3618 | 555000 | 555000 | 44.9 | 22000 | 7782.9888 |  | 1
85 | 80 | 75 | 79.7527 | 707000 | 248000 | 47.4 | 24750 | 10108.5084 |  | 1
85 | 80 | 72 | 68.6171 | 677000 | 327000 | 46.8 | 24750 | 10108.5084 |  | 1
85 | 80 | 67 | 51.5724 | 621000 | 453000 | 45.7 | 24750 | 10108.5084 |  | 1
85 | 80 | 62 | 36.2232 | 571000 | 560000 | 44.8 | 24750 | 10108.5084 |  | 1
85 | 80 | 57 | 22.3618 | 564000 | 564000 | 44.8 | 24750 | 10108.5084 |  | 1
95 | 80 | 75 | 79.7527 | 665000 | 214000 | 51.4 | 22000 | 7782.9888 |  | 1
95 | 80 | 72 | 68.6171 | 634000 | 285000 | 50.8 | 22000 | 7782.9888 |  | 1
95 | 80 | 67 | 51.5724 | 582000 | 403000 | 49.8 | 22000 | 7782.9888 |  | 1
95 | 80 | 62 | 36.2232 | 532000 | 508000 | 49 | 22000 | 7782.9888 |  | 1
95 | 80 | 57 | 22.3618 | 530000 | 530000 | 49.4 | 22000 | 7782.9888 |  | 1
95 | 80 | 75 | 79.7527 | 674000 | 224000 | 51.6 | 24750 | 10108.5084 |  | 1
95 | 80 | 72 | 68.6171 | 642000 | 302000 | 51 | 24750 | 10108.5084 |  | 1
95 | 80 | 67 | 51.5724 | 591000 | 431000 | 50 | 24750 | 10108.5084 |  | 1
95 | 80 | 62 | 36.2232 | 543000 | 531000 | 49.2 | 24750 | 10108.5084 |  | 1
95 | 80 | 57 | 22.3618 | 545000 | 545000 | 49.5 | 24750 | 10108.5084 |  | 1
105 | 80 | 75 | 79.7527 | 633000 | 193000 | 56.4 | 22000 | 7782.9888 |  | 1
105 | 80 | 72 | 68.6171 | 599000 | 261000 | 55.7 | 22000 | 7782.9888 |  | 1
105 | 80 | 67 | 51.5724 | 549000 | 380000 | 54.8 | 22000 | 7782.9888 |  | 1
105 | 80 | 62 | 36.2232 | 503000 | 476000 | 54 | 22000 | 7782.9888 |  | 1
105 | 80 | 57 | 22.3618 | 502000 | 502000 | 54.4 | 22000 | 7782.9888 |  | 1
105 | 80 | 75 | 79.7527 | 638000 | 200000 | 56.4 | 24750 | 10108.5084 |  | 1
105 | 80 | 72 | 68.6171 | 607000 | 278000 | 55.8 | 24750 | 10108.5084 |  | 1
105 | 80 | 67 | 51.5724 | 557000 | 408000 | 54.9 | 24750 | 10108.5084 |  | 1
105 | 80 | 62 | 36.2232 | 514000 | 504000 | 54.1 | 24750 | 10108.5084 |  | 1
105 | 80 | 57 | 22.3618 | 518000 | 518000 | 54.6 | 24750 | 10108.5084 |  | 1
115 | 80 | 75 | 79.7527 | 591000 | 164000 | 61.8 | 22000 | 7782.9888 |  | 1
115 | 80 | 72 | 68.6171 | 562000 | 237000 | 61.2 | 22000 | 7782.9888 |  | 1
115 | 80 | 67 | 51.5724 | 514000 | 357000 | 60.3 | 22000 | 7782.9888 |  | 1
115 | 80 | 62 | 36.2232 | 473000 | 449000 | 59.7 | 22000 | 7412.0726 |  | 1
115 | 80 | 57 | 22.3618 | 463000 | 463000 | 59.7 | 22000 | 7412.0726 |  | 1
115 | 80 | 75 | 79.7527 | 599000 | 174000 | 62 | 24750 | 10108.5084 |  | 1
115 | 80 | 72 | 68.6171 | 569000 | 253000 | 61.3 | 24750 | 10108.5084 |  | 1
115 | 80 | 67 | 51.5724 | 522000 | 384000 | 60.4 | 24750 | 10108.5084 |  | 1
115 | 80 | 62 | 36.2232 | 482000 | 475000 | 59.8 | 24750 | 9687.581 |  | 1
115 | 80 | 57 | 22.3618 | 488000 | 488000 | 60.3 | 24750 | 9687.581 |  | 1
75 | 80 | 75 | 79.7527 | 639000 | 174000 | 42 | 11000 | 2335.9385 |  | 2
75 | 80 | 72 | 68.6171 | 598000 | 211000 | 41.3 | 11000 | 2335.9385 |  | 2
75 | 80 | 67 | 51.5724 | 533000 | 270000 | 40.2 | 11000 | 2335.9385 |  | 2
75 | 80 | 62 | 36.2232 | 481000 | 338000 | 39.3 | 11000 | 2073.3799 |  | 2
75 | 80 | 57 | 22.3618 | 441000 | 411000 | 38.7 | 11000 | 2073.3799 |  | 2
75 | 80 | 75 | 79.7527 | 678000 | 194000 | 42.8 | 13750 | 3165.2905 |  | 2
75 | 80 | 72 | 68.6171 | 632000 | 237000 | 42 | 13750 | 3165.2905 |  | 2
75 | 80 | 67 | 51.5724 | 569000 | 316000 | 40.9 | 13750 | 3165.2905 |  | 2
75 | 80 | 62 | 36.2232 | 510000 | 392000 | 39.9 | 13750 | 3165.2905 |  | 2
75 | 80 | 57 | 22.3618 | 476000 | 467000 | 39.2 | 13750 | 2894.3966 |  | 2
75 | 80 | 75 | 79.7527 | 704000 | 213000 | 43.3 | 16500 | 4344.7207 |  | 2
75 | 80 | 72 | 68.6171 | 658000 | 263000 | 42.5 | 16500 | 4344.7207 |  | 2
75 | 80 | 67 | 51.5724 | 588000 | 350000 | 41.2 | 16500 | 4344.7207 |  | 2
75 | 80 | 62 | 36.2232 | 535000 | 448000 | 40.3 | 16500 | 4344.7207 |  | 2
75 | 80 | 57 | 22.3618 | 500000 | 500000 | 39.7 | 16500 | 4048.8212 |  | 2
75 | 80 | 75 | 79.7527 | 721000 | 227000 | 43.6 | 19250 | 5872.1453 |  | 2
75 | 80 | 72 | 68.6171 | 671000 | 282000 | 42.7 | 19250 | 5872.1453 |  | 2
75 | 80 | 67 | 51.5724 | 618000 | 403000 | 41.7 | 19250 | 5872.1453 |  | 2
75 | 80 | 62 | 36.2232 | 550000 | 496000 | 40.6 | 19250 | 5872.1453 |  | 2
75 | 80 | 57 | 22.3618 | 524000 | 524000 | 40.2 | 19250 | 5872.1453 |  | 2
85 | 80 | 75 | 79.7527 | 591000 | 133000 | 45.4 | 11000 | 2335.9385 |  | 2
85 | 80 | 72 | 68.6171 | 553000 | 172000 | 44.7 | 11000 | 2335.9385 |  | 2
85 | 80 | 67 | 51.5724 | 497000 | 241000 | 43.7 | 11000 | 2073.3799 |  | 2
85 | 80 | 62 | 36.2232 | 449000 | 311000 | 43 | 11000 | 2073.3799 |  | 2
85 | 80 | 57 | 22.3618 | 415000 | 387000 | 42.5 | 11000 | 2073.3799 |  | 2
85 | 80 | 75 | 79.7527 | 618000 | 143000 | 46 | 13750 | 3165.2905 |  | 2
85 | 80 | 72 | 68.6171 | 577000 | 189000 | 45.2 | 13750 | 3165.2905 |  | 2
85 | 80 | 67 | 51.5724 | 534000 | 286000 | 44.3 | 13750 | 3165.2905 |  | 2
85 | 80 | 62 | 36.2232 | 473000 | 360000 | 43.3 | 13750 | 2894.3966 |  | 2
85 | 80 | 57 | 22.3618 | 446000 | 438000 | 42.8 | 13750 | 2894.3966 |  | 2
85 | 80 | 75 | 79.7527 | 663000 | 182000 | 46.7 | 16500 | 4344.7207 |  | 2
85 | 80 | 72 | 68.6171 | 616000 | 231000 | 45.9 | 16500 | 4344.7207 |  | 2
85 | 80 | 67 | 51.5724 | 552000 | 322000 | 44.7 | 16500 | 4344.7207 |  | 2
85 | 80 | 62 | 36.2232 | 491000 | 410000 | 43.7 | 16500 | 4048.8212 |  | 2
85 | 80 | 57 | 22.3618 | 467000 | 467000 | 43.2 | 16500 | 4048.8212 |  | 2
85 | 80 | 75 | 79.7527 | 676000 | 192000 | 47 | 19250 | 5872.1453 |  | 2
85 | 80 | 72 | 68.6171 | 629000 | 251000 | 46.2 | 19250 | 5872.1453 |  | 2
85 | 80 | 67 | 51.5724 | 566000 | 358000 | 45 | 19250 | 5872.1453 |  | 2
85 | 80 | 62 | 36.2232 | 502000 | 453000 | 43.9 | 19250 | 5872.1453 |  | 2
85 | 80 | 57 | 22.3618 | 490000 | 490000 | 43.6 | 19250 | 5547.0726 |  | 2
95 | 80 | 75 | 79.7527 | 563000 | 113000 | 49.6 | 11000 | 2335.9385 |  | 2
95 | 80 | 72 | 68.6171 | 525000 | 151000 | 48.9 | 11000 | 2335.9385 |  | 2
95 | 80 | 67 | 51.5724 | 469000 | 219000 | 47.9 | 11000 | 2073.3799 |  | 2
95 | 80 | 62 | 36.2232 | 415000 | 283000 | 47.3 | 11000 | 2073.3799 |  | 2
95 | 80 | 57 | 22.3618 | 395000 | 371000 | 46.9 | 11000 | 1829.5754 |  | 2
95 | 80 | 75 | 79.7527 | 595000 | 128000 | 50.2 | 13750 | 3165.2905 |  | 2
95 | 80 | 72 | 68.6171 | 552000 | 172000 | 49.4 | 13750 | 3165.2905 |  | 2
95 | 80 | 67 | 51.5724 | 493000 | 253000 | 48.3 | 13750 | 2894.3966 |  | 2
95 | 80 | 62 | 36.2232 | 436000 | 330000 | 47.5 | 13750 | 2894.3966 |  | 2
95 | 80 | 57 | 22.3618 | 416000 | 410000 | 47.2 | 13750 | 2894.3966 |  | 2
95 | 80 | 75 | 79.7527 | 618000 | 144000 | 50.7 | 16500 | 4344.7207 |  | 2
95 | 80 | 72 | 68.6171 | 573000 | 195000 | 49.8 | 16500 | 4344.7207 |  | 2
95 | 80 | 67 | 51.5724 | 510000 | 288000 | 48.6 | 16500 | 4344.7207 |  | 2
95 | 80 | 62 | 36.2232 | 452000 | 378000 | 47.7 | 16500 | 4048.8212 |  | 2
95 | 80 | 57 | 22.3618 | 433000 | 433000 | 47.4 | 16500 | 4048.8212 |  | 2
95 | 80 | 75 | 79.7527 | 621000 | 144000 | 50.9 | 19250 | 5872.1453 |  | 2
95 | 80 | 72 | 68.6171 | 568000 | 197000 | 49.9 | 19250 | 5872.1453 |  | 2
95 | 80 | 67 | 51.5724 | 523000 | 323000 | 48.9 | 19250 | 5872.1453 |  | 2
95 | 80 | 62 | 36.2232 | 467000 | 424000 | 47.9 | 19250 | 5547.0726 |  | 2
95 | 80 | 57 | 22.3618 | 455000 | 455000 | 47.7 | 19250 | 5547.0726 |  | 2
105 | 80 | 75 | 79.7527 | 511000 | 70000 | 54.3 | 11000 | 2335.9385 |  | 2
105 | 80 | 72 | 68.6171 | 476000 | 111000 | 53.6 | 11000 | 2073.3799 |  | 2
105 | 80 | 67 | 51.5724 | 423000 | 181000 | 52.7 | 11000 | 2073.3799 |  | 2
105 | 80 | 62 | 36.2232 | 380000 | 256000 | 52.5 | 11000 | 1829.5754 |  | 2
105 | 80 | 57 | 22.3618 | 364000 | 339000 | 52.6 | 11000 | 1829.5754 |  | 2
105 | 80 | 75 | 79.7527 | 554000 | 97000 | 55 | 13750 | 3165.2905 |  | 2
105 | 80 | 72 | 68.6171 | 512000 | 141000 | 54.1 | 13750 | 3165.2905 |  | 2
105 | 80 | 67 | 51.5724 | 454000 | 222000 | 53.1 | 13750 | 2894.3966 |  | 2
105 | 80 | 62 | 36.2232 | 407000 | 310000 | 52.4 | 13750 | 2894.3966 |  | 2
105 | 80 | 57 | 22.3618 | 389000 | 384000 | 52.3 | 13750 | 2638.0894 |  | 2
105 | 80 | 75 | 79.7527 | 577000 | 114000 | 55.5 | 16500 | 4344.7207 |  | 2
105 | 80 | 72 | 68.6171 | 514000 | 145000 | 54.3 | 16500 | 4344.7207 |  | 2
105 | 80 | 67 | 51.5724 | 457000 | 243000 | 53.2 | 16500 | 4048.8212 |  | 2
105 | 80 | 62 | 36.2232 | 413000 | 346000 | 52.5 | 16500 | 4048.8212 |  | 2
105 | 80 | 57 | 22.3618 | 399000 | 399000 | 52.3 | 16500 | 3759.1732 |  | 2
105 | 80 | 75 | 79.7527 | 572000 | 106000 | 55.6 | 19250 | 5872.1453 |  | 2
105 | 80 | 72 | 68.6171 | 529000 | 167000 | 54.6 | 19250 | 5872.1453 |  | 2
105 | 80 | 67 | 51.5724 | 468000 | 276000 | 53.4 | 19250 | 5547.0726 |  | 2
105 | 80 | 62 | 36.2232 | 433000 | 388000 | 52.7 | 19250 | 5547.0726 |  | 2
105 | 80 | 57 | 22.3618 | 417000 | 417000 | 52.5 | 19250 | 5547.0726 |  | 2
115 | 80 | 75 | 79.7527 | 469000 | 39000 | 60 | 11000 | 2073.3799 |  | 2
115 | 80 | 72 | 68.6171 | 434000 | 80000 | 59.3 | 11000 | 2073.3799 |  | 2
115 | 80 | 67 | 51.5724 | 383000 | 151000 | 58.9 | 11000 | 1829.5754 |  | 2
115 | 80 | 62 | 36.2232 | 343000 | 228000 | 59.4 | 11000 | 1604.5251 |  | 2
115 | 80 | 57 | 22.3618 | 334000 | 311000 | 59.9 | 11000 | 1604.5251 |  | 2
115 | 80 | 75 | 79.7527 | 490000 | 44000 | 60.4 | 13750 | 2894.3966 |  | 2
115 | 80 | 72 | 68.6171 | 453000 | 93000 | 59.5 | 13750 | 2894.3966 |  | 2
115 | 80 | 67 | 51.5724 | 399000 | 178000 | 58.7 | 13750 | 2638.0894 |  | 2
115 | 80 | 62 | 36.2232 | 358000 | 270000 | 58.7 | 13750 | 2638.0894 |  | 2
115 | 80 | 57 | 22.3618 | 350000 | 347000 | 59 | 13750 | 2396.3687 |  | 2
115 | 80 | 75 | 79.7527 | 507000 | 56000 | 60.8 | 16500 | 4344.7207 |  | 2
115 | 80 | 72 | 68.6171 | 467000 | 110000 | 59.7 | 16500 | 4048.8212 |  | 2
115 | 80 | 67 | 51.5724 | 411000 | 208000 | 58.7 | 16500 | 4048.8212 |  | 2
115 | 80 | 62 | 36.2232 | 374000 | 316000 | 58.4 | 16500 | 3759.1732 |  | 2
115 | 80 | 57 | 22.3618 | 363000 | 363000 | 58.5 | 16500 | 3759.1732 |  | 2
115 | 80 | 75 | 79.7527 | 520000 | 68000 | 61.2 | 19250 | 5872.1453 |  | 2
115 | 80 | 72 | 68.6171 | 477000 | 128000 | 59.9 | 19250 | 5547.0726 |  | 2
115 | 80 | 67 | 51.5724 | 420000 | 240000 | 58.7 | 19250 | 5547.0726 |  | 2
115 | 80 | 62 | 36.2232 | 393000 | 351000 | 58.3 | 19250 | 5217.8324 |  | 2
115 | 80 | 57 | 22.3618 | 378000 | 378000 | 58.3 | 19250 | 5217.8324 |  | 2
75 | 80 | 75 | 79.7527 | 739000 | 246000 | 43.9 | 22000 | 7782.9888 |  | 2
75 | 80 | 72 | 68.6171 | 686000 | 307000 | 43 | 22000 | 7782.9888 |  | 2
75 | 80 | 67 | 51.5724 | 746000 | 653000 | 44.1 | 22000 | 7782.9888 |  | 2
75 | 80 | 62 | 36.2232 | 568000 | 537000 | 40.9 | 22000 | 7782.9888 |  | 2
75 | 80 | 57 | 22.3618 | 555000 | 555000 | 40.7 | 22000 | 7782.9888 |  | 2
75 | 80 | 75 | 79.7527 | 752000 | 263000 | 44.1 | 24750 | 10108.5084 |  | 2
75 | 80 | 72 | 68.6171 | 697000 | 329000 | 43.2 | 24750 | 10108.5084 |  | 2
75 | 80 | 67 | 51.5724 | 750000 | 668000 | 44.2 | 24750 | 10108.5084 |  | 2
75 | 80 | 62 | 36.2232 | 582000 | 569000 | 41.2 | 24750 | 10108.5084 |  | 2
75 | 80 | 57 | 22.3618 | 576000 | 576000 | 41.1 | 24750 | 10108.5084 |  | 2
85 | 80 | 75 | 79.7527 | 692000 | 210000 | 47.3 | 22000 | 7782.9888 |  | 2
85 | 80 | 72 | 68.6171 | 643000 | 274000 | 46.5 | 22000 | 7782.9888 |  | 2
85 | 80 | 67 | 51.5724 | 573000 | 389000 | 45.2 | 22000 | 7782.9888 |  | 2
85 | 80 | 62 | 36.2232 | 521000 | 491000 | 44.2 | 22000 | 7782.9888 |  | 2
85 | 80 | 57 | 22.3618 | 518000 | 518000 | 44.1 | 22000 | 7782.9888 |  | 2
85 | 80 | 75 | 79.7527 | 704000 | 226000 | 47.6 | 24750 | 10108.5084 |  | 2
85 | 80 | 72 | 68.6171 | 653000 | 297000 | 46.7 | 24750 | 10108.5084 |  | 2
85 | 80 | 67 | 51.5724 | 584000 | 426000 | 45.4 | 24750 | 10108.5084 |  | 2
85 | 80 | 62 | 36.2232 | 531000 | 520000 | 44.5 | 24750 | 10108.5084 |  | 2
85 | 80 | 57 | 22.3618 | 537000 | 537000 | 44.5 | 24750 | 10108.5084 |  | 2
95 | 80 | 75 | 79.7527 | 636000 | 161000 | 51.3 | 22000 | 7782.9888 |  | 2
95 | 80 | 72 | 68.6171 | 579000 | 218000 | 50.1 | 22000 | 7782.9888 |  | 2
95 | 80 | 67 | 51.5724 | 535000 | 359000 | 49.1 | 22000 | 7782.9888 |  | 2
95 | 80 | 62 | 36.2232 | 484000 | 456000 | 48.2 | 22000 | 7412.0726 |  | 2
95 | 80 | 57 | 22.3618 | 473000 | 473000 | 48.1 | 22000 | 7412.0726 |  | 2
95 | 80 | 75 | 79.7527 | 666000 | 197000 | 51.7 | 24750 | 10108.5084 |  | 2
95 | 80 | 72 | 68.6171 | 612000 | 264000 | 50.6 | 24750 | 10108.5084 |  | 2
95 | 80 | 67 | 51.5724 | 543000 | 393000 | 49.3 | 24750 | 10108.5084 |  | 2
95 | 80 | 62 | 36.2232 | 495000 | 486000 | 48.4 | 24750 | 9687.581 |  | 2
95 | 80 | 57 | 22.3618 | 489000 | 489000 | 48.4 | 24750 | 9687.581 |  | 2
105 | 80 | 75 | 79.7527 | 586000 | 122000 | 56 | 22000 | 7782.9888 |  | 2
105 | 80 | 72 | 68.6171 | 539000 | 188000 | 54.8 | 22000 | 7782.9888 |  | 2
105 | 80 | 67 | 51.5724 | 475000 | 308000 | 53.5 | 22000 | 7412.0726 |  | 2
105 | 80 | 62 | 36.2232 | 445000 | 419000 | 52.9 | 22000 | 7412.0726 |  | 2
105 | 80 | 57 | 22.3618 | 434000 | 434000 | 52.8 | 22000 | 7412.0726 |  | 2
105 | 80 | 75 | 79.7527 | 593000 | 134000 | 56.2 | 24750 | 10108.5084 |  | 2
105 | 80 | 72 | 68.6171 | 545000 | 207000 | 55 | 24750 | 10108.5084 |  | 2
105 | 80 | 67 | 51.5724 | 484000 | 343000 | 53.7 | 24750 | 9687.581 |  | 2
105 | 80 | 62 | 36.2232 | 454000 | 446000 | 53.1 | 24750 | 9687.581 |  | 2
105 | 80 | 57 | 22.3618 | 448000 | 448000 | 53 | 24750 | 9687.581 |  | 2
115 | 80 | 75 | 79.7527 | 532000 | 82000 | 61.6 | 22000 | 7782.9888 |  | 2
115 | 80 | 72 | 68.6171 | 486000 | 148000 | 60.1 | 22000 | 7412.0726 |  | 2
115 | 80 | 67 | 51.5724 | 427000 | 272000 | 58.8 | 22000 | 7412.0726 |  | 2
115 | 80 | 62 | 36.2232 | 404000 | 380000 | 58.4 | 22000 | 7412.0726 |  | 2
115 | 80 | 57 | 22.3618 | 393000 | 393000 | 58.3 | 22000 | 7036.9888 |  | 2
115 | 80 | 75 | 79.7527 | 543000 | 98000 | 62 | 24750 | 10108.5084 |  | 2
115 | 80 | 72 | 68.6171 | 494000 | 169000 | 60.3 | 24750 | 9687.581 |  | 2
115 | 80 | 67 | 51.5724 | 434000 | 304000 | 58.9 | 24750 | 9687.581 |  | 2
115 | 80 | 62 | 36.2232 | 410000 | 405000 | 58.4 | 24750 | 9687.581 |  | 2
115 | 80 | 57 | 22.3618 | 405000 | 405000 | 58.4 | 24750 | 9687.581 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 14
Degradation Coefficient (C_d) |  | 48/50 060 (60 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 711000 | 224000 | 48.5 | 12000 | 2535.9832 |  | 1
75 | 80 | 72 | 68.6171 | 674000 | 268000 | 47.7 | 12000 | 2535.9832 |  | 1
75 | 80 | 67 | 51.5724 | 615000 | 339000 | 46.6 | 12000 | 2535.9832 |  | 1
75 | 80 | 62 | 36.2232 | 560000 | 408000 | 45.7 | 12000 | 2535.9832 |  | 1
75 | 80 | 57 | 22.3618 | 508000 | 473000 | 44.8 | 12000 | 2535.9832 |  | 1
75 | 80 | 75 | 79.7527 | 754000 | 247000 | 49.5 | 15000 | 3640.3966 |  | 1
75 | 80 | 72 | 68.6171 | 710000 | 293000 | 48.5 | 15000 | 3640.3966 |  | 1
75 | 80 | 67 | 51.5724 | 650000 | 379000 | 47.2 | 15000 | 3640.3966 |  | 1
75 | 80 | 62 | 36.2232 | 600000 | 469000 | 46.5 | 15000 | 3640.3966 |  | 1
75 | 80 | 57 | 22.3618 | 539000 | 530000 | 45.2 | 15000 | 3640.3966 |  | 1
75 | 80 | 75 | 79.7527 | 771000 | 255000 | 49.9 | 18000 | 5232.419 |  | 1
75 | 80 | 72 | 68.6171 | 734000 | 315000 | 49 | 18000 | 5232.419 |  | 1
75 | 80 | 67 | 51.5724 | 674000 | 415000 | 47.7 | 18000 | 5232.419 |  | 1
75 | 80 | 62 | 36.2232 | 626000 | 522000 | 47.1 | 18000 | 5232.419 |  | 1
75 | 80 | 57 | 22.3618 | 570000 | 570000 | 45.8 | 18000 | 5232.419 |  | 1
75 | 80 | 75 | 79.7527 | 789000 | 269000 | 50.3 | 21000 | 7355.8101 |  | 1
75 | 80 | 72 | 68.6171 | 758000 | 344000 | 49.7 | 21000 | 7355.8101 |  | 1
75 | 80 | 67 | 51.5724 | 692000 | 450000 | 48.1 | 21000 | 7355.8101 |  | 1
75 | 80 | 62 | 36.2232 | 634000 | 559000 | 47 | 21000 | 7355.8101 |  | 1
75 | 80 | 57 | 22.3618 | 599000 | 599000 | 46.3 | 21000 | 7355.8101 |  | 1
85 | 80 | 75 | 79.7527 | 681000 | 202000 | 52.8 | 12000 | 2535.9832 |  | 1
85 | 80 | 72 | 68.6171 | 646000 | 246000 | 52 | 12000 | 2535.9832 |  | 1
85 | 80 | 67 | 51.5724 | 589000 | 318000 | 51 | 12000 | 2535.9832 |  | 1
85 | 80 | 62 | 36.2232 | 536000 | 389000 | 50 | 12000 | 2535.9832 |  | 1
85 | 80 | 57 | 22.3618 | 482000 | 446000 | 49.2 | 12000 | 2273.4246 |  | 1
85 | 80 | 75 | 79.7527 | 723000 | 226000 | 53.8 | 15000 | 3640.3966 |  | 1
85 | 80 | 72 | 68.6171 | 688000 | 279000 | 53.1 | 15000 | 3640.3966 |  | 1
85 | 80 | 67 | 51.5724 | 622000 | 357000 | 51.6 | 15000 | 3640.3966 |  | 1
85 | 80 | 62 | 36.2232 | 567000 | 442000 | 50.6 | 15000 | 3640.3966 |  | 1
85 | 80 | 57 | 22.3618 | 518000 | 508000 | 49.6 | 15000 | 3640.3966 |  | 1
85 | 80 | 75 | 79.7527 | 746000 | 239000 | 54.3 | 18000 | 5232.419 |  | 1
85 | 80 | 72 | 68.6171 | 702000 | 292000 | 53.2 | 18000 | 5232.419 |  | 1
85 | 80 | 67 | 51.5724 | 645000 | 393000 | 52 | 18000 | 5232.419 |  | 1
85 | 80 | 62 | 36.2232 | 589000 | 492000 | 51 | 18000 | 5232.419 |  | 1
85 | 80 | 57 | 22.3618 | 546000 | 546000 | 50.2 | 18000 | 5232.419 |  | 1
85 | 80 | 75 | 79.7527 | 755000 | 244000 | 54.4 | 21000 | 7355.8101 |  | 1
85 | 80 | 72 | 68.6171 | 717000 | 311000 | 53.5 | 21000 | 7355.8101 |  | 1
85 | 80 | 67 | 51.5724 | 661000 | 427000 | 52.4 | 21000 | 7355.8101 |  | 1
85 | 80 | 62 | 36.2232 | 605000 | 537000 | 51.3 | 21000 | 7355.8101 |  | 1
85 | 80 | 57 | 22.3618 | 586000 | 586000 | 51.6 | 21000 | 7355.8101 |  | 1
95 | 80 | 75 | 79.7527 | 649000 | 179000 | 57.7 | 12000 | 2535.9832 |  | 1
95 | 80 | 72 | 68.6171 | 615000 | 224000 | 57 | 12000 | 2535.9832 |  | 1
95 | 80 | 67 | 51.5724 | 561000 | 298000 | 55.9 | 12000 | 2535.9832 |  | 1
95 | 80 | 62 | 36.2232 | 510000 | 370000 | 55.2 | 12000 | 2535.9832 |  | 1
95 | 80 | 57 | 22.3618 | 462000 | 435000 | 54.8 | 12000 | 2273.4246 |  | 1
95 | 80 | 75 | 79.7527 | 681000 | 193000 | 58.4 | 15000 | 3640.3966 |  | 1
95 | 80 | 72 | 68.6171 | 647000 | 247000 | 57.6 | 15000 | 3640.3966 |  | 1
95 | 80 | 67 | 51.5724 | 592000 | 335000 | 56.5 | 15000 | 3640.3966 |  | 1
95 | 80 | 62 | 36.2232 | 539000 | 422000 | 55.5 | 15000 | 3640.3966 |  | 1
95 | 80 | 57 | 22.3618 | 494000 | 485000 | 54.8 | 15000 | 3369.5028 |  | 1
95 | 80 | 75 | 79.7527 | 703000 | 206000 | 58.9 | 18000 | 5232.419 |  | 1
95 | 80 | 72 | 68.6171 | 668000 | 268000 | 58.1 | 18000 | 5232.419 |  | 1
95 | 80 | 67 | 51.5724 | 613000 | 370000 | 56.9 | 18000 | 5232.419 |  | 1
95 | 80 | 62 | 36.2232 | 560000 | 470000 | 55.9 | 18000 | 5232.419 |  | 1
95 | 80 | 57 | 22.3618 | 521000 | 521000 | 55.2 | 18000 | 5232.419 |  | 1
95 | 80 | 75 | 79.7527 | 727000 | 227000 | 59.6 | 21000 | 7355.8101 |  | 1
95 | 80 | 72 | 68.6171 | 684000 | 288000 | 58.4 | 21000 | 7355.8101 |  | 1
95 | 80 | 67 | 51.5724 | 629000 | 404000 | 57.3 | 21000 | 7355.8101 |  | 1
95 | 80 | 62 | 36.2232 | 575000 | 513000 | 56.2 | 21000 | 7355.8101 |  | 1
95 | 80 | 57 | 22.3618 | 548000 | 548000 | 55.7 | 21000 | 7355.8101 |  | 1
105 | 80 | 75 | 79.7527 | 614000 | 155000 | 63.3 | 12000 | 2535.9832 |  | 1
105 | 80 | 72 | 68.6171 | 582000 | 201000 | 62.6 | 12000 | 2535.9832 |  | 1
105 | 80 | 67 | 51.5724 | 531000 | 276000 | 61.8 | 12000 | 2535.9832 |  | 1
105 | 80 | 62 | 36.2232 | 482000 | 349000 | 61.4 | 12000 | 2273.4246 |  | 1
105 | 80 | 57 | 22.3618 | 433000 | 408000 | 61.3 | 12000 | 2273.4246 |  | 1
105 | 80 | 75 | 79.7527 | 644000 | 168000 | 63.9 | 15000 | 3640.3966 |  | 1
105 | 80 | 72 | 68.6171 | 611000 | 222000 | 63.2 | 15000 | 3640.3966 |  | 1
105 | 80 | 67 | 51.5724 | 559000 | 312000 | 62.1 | 15000 | 3640.3966 |  | 1
105 | 80 | 62 | 36.2232 | 509000 | 400000 | 61.5 | 15000 | 3640.3966 |  | 1
105 | 80 | 57 | 22.3618 | 468000 | 461000 | 61 | 15000 | 3369.5028 |  | 1
105 | 80 | 75 | 79.7527 | 664000 | 180000 | 64.4 | 18000 | 5232.419 |  | 1
105 | 80 | 72 | 68.6171 | 631000 | 243000 | 63.6 | 18000 | 5232.419 |  | 1
105 | 80 | 67 | 51.5724 | 579000 | 346000 | 62.5 | 18000 | 5232.419 |  | 1
105 | 80 | 62 | 36.2232 | 528000 | 447000 | 61.7 | 18000 | 5232.419 |  | 1
105 | 80 | 57 | 22.3618 | 495000 | 495000 | 61.3 | 18000 | 4928.1844 |  | 1
105 | 80 | 75 | 79.7527 | 679000 | 192000 | 64.7 | 21000 | 7355.8101 |  | 1
105 | 80 | 72 | 68.6171 | 646000 | 262000 | 64 | 21000 | 7355.8101 |  | 1
105 | 80 | 67 | 51.5724 | 593000 | 379000 | 62.8 | 21000 | 7355.8101 |  | 1
105 | 80 | 62 | 36.2232 | 542000 | 489000 | 61.8 | 21000 | 7355.8101 |  | 1
105 | 80 | 57 | 22.3618 | 519000 | 519000 | 61.5 | 21000 | 7355.8101 |  | 1
115 | 80 | 75 | 79.7527 | 577000 | 130000 | 69.8 | 12000 | 2535.9832 |  | 1
115 | 80 | 72 | 68.6171 | 547000 | 177000 | 69.3 | 12000 | 2535.9832 |  | 1
115 | 80 | 67 | 51.5724 | 498000 | 253000 | 68.8 | 12000 | 2273.4246 |  | 1
115 | 80 | 62 | 36.2232 | 451000 | 327000 | 68.7 | 12000 | 2273.4246 |  | 1
115 | 80 | 57 | 22.3618 | 408000 | 381000 | 69 | 12000 | 2273.4246 |  | 1
115 | 80 | 75 | 79.7527 | 604000 | 142000 | 70.2 | 15000 | 3640.3966 |  | 1
115 | 80 | 72 | 68.6171 | 573000 | 197000 | 69.6 | 15000 | 3640.3966 |  | 1
115 | 80 | 67 | 51.5724 | 524000 | 288000 | 68.9 | 15000 | 3640.3966 |  | 1
115 | 80 | 62 | 36.2232 | 477000 | 376000 | 68.6 | 15000 | 3369.5028 |  | 1
115 | 80 | 57 | 22.3618 | 439000 | 433000 | 68.2 | 15000 | 3369.5028 |  | 1
115 | 80 | 75 | 79.7527 | 631000 | 162000 | 71 | 18000 | 5232.419 |  | 1
115 | 80 | 72 | 68.6171 | 592000 | 216000 | 69.9 | 18000 | 5232.419 |  | 1
115 | 80 | 67 | 51.5724 | 542000 | 321000 | 69 | 18000 | 5232.419 |  | 1
115 | 80 | 62 | 36.2232 | 494000 | 422000 | 68.5 | 18000 | 4928.1844 |  | 1
115 | 80 | 57 | 22.3618 | 465000 | 465000 | 68.4 | 18000 | 4928.1844 |  | 1
115 | 80 | 75 | 79.7527 | 644000 | 173000 | 71.2 | 21000 | 7355.8101 |  | 1
115 | 80 | 72 | 68.6171 | 605000 | 235000 | 70.1 | 21000 | 7355.8101 |  | 1
115 | 80 | 67 | 51.5724 | 555000 | 353000 | 69.2 | 21000 | 7355.8101 |  | 1
115 | 80 | 62 | 36.2232 | 506000 | 462000 | 68.5 | 21000 | 7355.8101 |  | 1
115 | 80 | 57 | 22.3618 | 489000 | 489000 | 68.4 | 21000 | 6997.3966 |  | 1
75 | 80 | 75 | 79.7527 | 793000 | 276000 | 50.4 | 24000 | 10035.5754 |  | 1
75 | 80 | 72 | 68.6171 | 765000 | 357000 | 49.8 | 24000 | 10035.5754 |  | 1
75 | 80 | 67 | 51.5724 | 795000 | 681000 | 50.9 | 24000 | 10035.5754 |  | 1
75 | 80 | 62 | 36.2232 | 775000 | 740000 | 50.6 | 24000 | 10035.5754 |  | 1
75 | 80 | 57 | 22.3618 | 771000 | 771000 | 50.6 | 24000 | 10035.5754 |  | 1
75 | 80 | 75 | 79.7527 | 804000 | 288000 | 50.6 | 27000 | 13344.648 |  | 1
75 | 80 | 72 | 68.6171 | 774000 | 375000 | 50 | 27000 | 13344.648 |  | 1
75 | 80 | 67 | 51.5724 | 715000 | 514000 | 48.7 | 27000 | 13344.648 |  | 1
75 | 80 | 62 | 36.2232 | 780000 | 758000 | 50.7 | 27000 | 13344.648 |  | 1
75 | 80 | 57 | 22.3618 | 778000 | 778000 | 50.7 | 27000 | 13344.648 |  | 1
85 | 80 | 75 | 79.7527 | 776000 | 264000 | 55.1 | 24000 | 10035.5754 |  | 1
85 | 80 | 72 | 68.6171 | 732000 | 333000 | 53.9 | 24000 | 10035.5754 |  | 1
85 | 80 | 67 | 51.5724 | 674000 | 459000 | 52.6 | 24000 | 10035.5754 |  | 1
85 | 80 | 62 | 36.2232 | 617000 | 577000 | 51.5 | 24000 | 10035.5754 |  | 1
85 | 80 | 57 | 22.3618 | 597000 | 597000 | 51.1 | 24000 | 10035.5754 |  | 1
85 | 80 | 75 | 79.7527 | 767000 | 262000 | 54.7 | 27000 | 13344.648 |  | 1
85 | 80 | 72 | 68.6171 | 742000 | 352000 | 54.2 | 27000 | 13344.648 |  | 1
85 | 80 | 67 | 51.5724 | 694000 | 495000 | 53.3 | 27000 | 13344.648 |  | 1
85 | 80 | 62 | 36.2232 | 637000 | 624000 | 52.3 | 27000 | 13344.648 |  | 1
85 | 80 | 57 | 22.3618 | 617000 | 617000 | 51.5 | 27000 | 13344.648 |  | 1
95 | 80 | 75 | 79.7527 | 730000 | 230000 | 59.5 | 24000 | 10035.5754 |  | 1
95 | 80 | 72 | 68.6171 | 696000 | 307000 | 58.7 | 24000 | 10035.5754 |  | 1
95 | 80 | 67 | 51.5724 | 640000 | 436000 | 57.5 | 24000 | 10035.5754 |  | 1
95 | 80 | 62 | 36.2232 | 586000 | 551000 | 56.4 | 24000 | 10035.5754 |  | 1
95 | 80 | 57 | 22.3618 | 582000 | 582000 | 57 | 24000 | 10035.5754 |  | 1
95 | 80 | 75 | 79.7527 | 754000 | 262000 | 61.1 | 27000 | 13344.648 |  | 1
95 | 80 | 72 | 68.6171 | 704000 | 326000 | 58.8 | 27000 | 13344.648 |  | 1
95 | 80 | 67 | 51.5724 | 658000 | 475000 | 58.1 | 27000 | 13344.648 |  | 1
95 | 80 | 62 | 36.2232 | 596000 | 578000 | 56.6 | 27000 | 13344.648 |  | 1
95 | 80 | 57 | 22.3618 | 601000 | 601000 | 57.3 | 27000 | 13344.648 |  | 1
105 | 80 | 75 | 79.7527 | 698000 | 212000 | 65.4 | 24000 | 10035.5754 |  | 1
105 | 80 | 72 | 68.6171 | 657000 | 281000 | 64.2 | 24000 | 10035.5754 |  | 1
105 | 80 | 67 | 51.5724 | 604000 | 410000 | 63 | 24000 | 10035.5754 |  | 1
105 | 80 | 62 | 36.2232 | 553000 | 518000 | 61.9 | 24000 | 10035.5754 |  | 1
105 | 80 | 57 | 22.3618 | 540000 | 540000 | 61.7 | 24000 | 10035.5754 |  | 1
105 | 80 | 75 | 79.7527 | 699000 | 214000 | 65.2 | 27000 | 13344.648 |  | 1
105 | 80 | 72 | 68.6171 | 666000 | 299000 | 64.4 | 27000 | 13344.648 |  | 1
105 | 80 | 67 | 51.5724 | 621000 | 449000 | 63.6 | 27000 | 13344.648 |  | 1
105 | 80 | 62 | 36.2232 | 577000 | 562000 | 63 | 27000 | 13344.648 |  | 1
105 | 80 | 57 | 22.3618 | 570000 | 570000 | 62.9 | 27000 | 13344.648 |  | 1
115 | 80 | 75 | 79.7527 | 654000 | 184000 | 71.5 | 24000 | 10035.5754 |  | 1
115 | 80 | 72 | 68.6171 | 615000 | 254000 | 70.3 | 24000 | 10035.5754 |  | 1
115 | 80 | 67 | 51.5724 | 574000 | 394000 | 69.7 | 24000 | 10035.5754 |  | 1
115 | 80 | 62 | 36.2232 | 519000 | 487000 | 68.5 | 24000 | 10035.5754 |  | 1
115 | 80 | 57 | 22.3618 | 522000 | 522000 | 69.5 | 24000 | 10035.5754 |  | 1
115 | 80 | 75 | 79.7527 | 654000 | 186000 | 71.3 | 27000 | 13344.648 |  | 1
115 | 80 | 72 | 68.6171 | 623000 | 271000 | 70.5 | 27000 | 13344.648 |  | 1
115 | 80 | 67 | 51.5724 | 573000 | 414000 | 69.4 | 27000 | 13344.648 |  | 1
115 | 80 | 62 | 36.2232 | 530000 | 516000 | 68.6 | 27000 | 13344.648 |  | 1
115 | 80 | 57 | 22.3618 | 524000 | 524000 | 68.6 | 27000 | 13344.648 |  | 1
75 | 80 | 75 | 79.7527 | 703000 | 188000 | 48.9 | 12000 | 2535.9832 |  | 2
75 | 80 | 72 | 68.6171 | 654000 | 224000 | 47.7 | 12000 | 2535.9832 |  | 2
75 | 80 | 67 | 51.5724 | 591000 | 299000 | 46.4 | 12000 | 2535.9832 |  | 2
75 | 80 | 62 | 36.2232 | 539000 | 378000 | 45.3 | 12000 | 2535.9832 |  | 2
75 | 80 | 57 | 22.3618 | 494000 | 457000 | 44.4 | 12000 | 2273.4246 |  | 2
75 | 80 | 75 | 79.7527 | 787000 | 254000 | 50.2 | 15000 | 3640.3966 |  | 2
75 | 80 | 72 | 68.6171 | 718000 | 280000 | 48.9 | 15000 | 3640.3966 |  | 2
75 | 80 | 67 | 51.5724 | 647000 | 364000 | 47.3 | 15000 | 3640.3966 |  | 2
75 | 80 | 62 | 36.2232 | 570000 | 435000 | 45.9 | 15000 | 3640.3966 |  | 2
75 | 80 | 57 | 22.3618 | 533000 | 520000 | 45.1 | 15000 | 3640.3966 |  | 2
75 | 80 | 75 | 79.7527 | 812000 | 270000 | 50.8 | 18000 | 5232.419 |  | 2
75 | 80 | 72 | 68.6171 | 750000 | 312000 | 49.8 | 18000 | 5232.419 |  | 2
75 | 80 | 67 | 51.5724 | 672000 | 406000 | 48 | 18000 | 5232.419 |  | 2
75 | 80 | 62 | 36.2232 | 588000 | 486000 | 46.4 | 18000 | 5232.419 |  | 2
75 | 80 | 57 | 22.3618 | 558000 | 558000 | 45.7 | 18000 | 5232.419 |  | 2
75 | 80 | 75 | 79.7527 | 829000 | 285000 | 51.3 | 21000 | 7355.8101 |  | 2
75 | 80 | 72 | 68.6171 | 752000 | 318000 | 49.9 | 21000 | 7355.8101 |  | 2
75 | 80 | 67 | 51.5724 | 683000 | 439000 | 48.5 | 21000 | 7355.8101 |  | 2
75 | 80 | 62 | 36.2232 | 620000 | 554000 | 47 | 21000 | 7355.8101 |  | 2
75 | 80 | 57 | 22.3618 | 588000 | 588000 | 46.4 | 21000 | 7355.8101 |  | 2
85 | 80 | 75 | 79.7527 | 661000 | 152000 | 52.7 | 12000 | 2535.9832 |  | 2
85 | 80 | 72 | 68.6171 | 621000 | 198000 | 51.8 | 12000 | 2535.9832 |  | 2
85 | 80 | 67 | 51.5724 | 559000 | 273000 | 50.5 | 12000 | 2535.9832 |  | 2
85 | 80 | 62 | 36.2232 | 506000 | 351000 | 49.5 | 12000 | 2535.9832 |  | 2
85 | 80 | 57 | 22.3618 | 462000 | 424000 | 48.7 | 12000 | 2273.4246 |  | 2
85 | 80 | 75 | 79.7527 | 691000 | 163000 | 53.5 | 15000 | 3640.3966 |  | 2
85 | 80 | 72 | 68.6171 | 658000 | 226000 | 52.7 | 15000 | 3640.3966 |  | 2
85 | 80 | 67 | 51.5724 | 592000 | 314000 | 51.2 | 15000 | 3640.3966 |  | 2
85 | 80 | 62 | 36.2232 | 534000 | 405000 | 50 | 15000 | 3640.3966 |  | 2
85 | 80 | 57 | 22.3618 | 504000 | 492000 | 49.3 | 15000 | 3640.3966 |  | 2
85 | 80 | 75 | 79.7527 | 739000 | 203000 | 54.4 | 18000 | 5232.419 |  | 2
85 | 80 | 72 | 68.6171 | 692000 | 261000 | 53.4 | 18000 | 5232.419 |  | 2
85 | 80 | 67 | 51.5724 | 606000 | 346000 | 51.6 | 18000 | 5232.419 |  | 2
85 | 80 | 62 | 36.2232 | 555000 | 458000 | 50.4 | 18000 | 5232.419 |  | 2
85 | 80 | 57 | 22.3618 | 526000 | 526000 | 49.8 | 18000 | 5232.419 |  | 2
85 | 80 | 75 | 79.7527 | 759000 | 221000 | 54.9 | 21000 | 7355.8101 |  | 2
85 | 80 | 72 | 68.6171 | 710000 | 286000 | 53.8 | 21000 | 7355.8101 |  | 2
85 | 80 | 67 | 51.5724 | 639000 | 402000 | 52.2 | 21000 | 7355.8101 |  | 2
85 | 80 | 62 | 36.2232 | 568000 | 507000 | 50.8 | 21000 | 7355.8101 |  | 2
85 | 80 | 57 | 22.3618 | 553000 | 553000 | 50.4 | 21000 | 7355.8101 |  | 2
95 | 80 | 75 | 79.7527 | 621000 | 120000 | 57.4 | 12000 | 2535.9832 |  | 2
95 | 80 | 72 | 68.6171 | 581000 | 165000 | 56.5 | 12000 | 2535.9832 |  | 2
95 | 80 | 67 | 51.5724 | 522000 | 242000 | 55.3 | 12000 | 2535.9832 |  | 2
95 | 80 | 62 | 36.2232 | 472000 | 323000 | 54.4 | 12000 | 2273.4246 |  | 2
95 | 80 | 57 | 22.3618 | 443000 | 413000 | 54.1 | 12000 | 2273.4246 |  | 2
95 | 80 | 75 | 79.7527 | 672000 | 154000 | 58.4 | 15000 | 3640.3966 |  | 2
95 | 80 | 72 | 68.6171 | 611000 | 187000 | 57.2 | 15000 | 3640.3966 |  | 2
95 | 80 | 67 | 51.5724 | 548000 | 278000 | 55.8 | 15000 | 3640.3966 |  | 2
95 | 80 | 62 | 36.2232 | 497000 | 375000 | 54.8 | 15000 | 3369.5028 |  | 2
95 | 80 | 57 | 22.3618 | 473000 | 462000 | 54.2 | 15000 | 3369.5028 |  | 2
95 | 80 | 75 | 79.7527 | 670000 | 142000 | 58.7 | 18000 | 5232.419 |  | 2
95 | 80 | 72 | 68.6171 | 625000 | 203000 | 57.6 | 18000 | 5232.419 |  | 2
95 | 80 | 67 | 51.5724 | 583000 | 331000 | 56.4 | 18000 | 5232.419 |  | 2
95 | 80 | 62 | 36.2232 | 516000 | 426000 | 55.2 | 18000 | 5232.419 |  | 2
95 | 80 | 57 | 22.3618 | 492000 | 492000 | 54.7 | 18000 | 4928.1844 |  | 2
95 | 80 | 75 | 79.7527 | 689000 | 159000 | 59.2 | 21000 | 7355.8101 |  | 2
95 | 80 | 72 | 68.6171 | 668000 | 254000 | 58.4 | 21000 | 7355.8101 |  | 2
95 | 80 | 67 | 51.5724 | 581000 | 352000 | 56.6 | 21000 | 7355.8101 |  | 2
95 | 80 | 62 | 36.2232 | 546000 | 490000 | 55.6 | 21000 | 7355.8101 |  | 2
95 | 80 | 57 | 22.3618 | 516000 | 516000 | 55.1 | 21000 | 7355.8101 |  | 2
105 | 80 | 75 | 79.7527 | 576000 | 87000 | 62.9 | 12000 | 2535.9832 |  | 2
105 | 80 | 72 | 68.6171 | 538000 | 132000 | 62 | 12000 | 2535.9832 |  | 2
105 | 80 | 67 | 51.5724 | 483000 | 212000 | 61 | 12000 | 2273.4246 |  | 2
105 | 80 | 62 | 36.2232 | 436000 | 294000 | 60.8 | 12000 | 2273.4246 |  | 2
105 | 80 | 57 | 22.3618 | 410000 | 378000 | 61 | 12000 | 2273.4246 |  | 2
105 | 80 | 75 | 79.7527 | 628000 | 122000 | 64 | 15000 | 3640.3966 |  | 2
105 | 80 | 72 | 68.6171 | 564000 | 151000 | 62.6 | 15000 | 3640.3966 |  | 2
105 | 80 | 67 | 51.5724 | 505000 | 244000 | 61.2 | 15000 | 3640.3966 |  | 2
105 | 80 | 62 | 36.2232 | 458000 | 344000 | 60.6 | 15000 | 3369.5028 |  | 2
105 | 80 | 57 | 22.3618 | 441000 | 432000 | 60.4 | 15000 | 3369.5028 |  | 2
105 | 80 | 75 | 79.7527 | 625000 | 110000 | 64.2 | 18000 | 5232.419 |  | 2
105 | 80 | 72 | 68.6171 | 586000 | 174000 | 63.1 | 18000 | 5232.419 |  | 2
105 | 80 | 67 | 51.5724 | 521000 | 280000 | 61.6 | 18000 | 5232.419 |  | 2
105 | 80 | 62 | 36.2232 | 474000 | 393000 | 60.6 | 18000 | 4928.1844 |  | 2
105 | 80 | 57 | 22.3618 | 457000 | 457000 | 60.5 | 18000 | 4928.1844 |  | 2
105 | 80 | 75 | 79.7527 | 644000 | 127000 | 64.7 | 21000 | 7355.8101 |  | 2
105 | 80 | 72 | 68.6171 | 597000 | 193000 | 63.4 | 21000 | 7355.8101 |  | 2
105 | 80 | 67 | 51.5724 | 534000 | 315000 | 61.8 | 21000 | 7355.8101 |  | 2
105 | 80 | 62 | 36.2232 | 493000 | 440000 | 60.9 | 21000 | 6997.3966 |  | 2
105 | 80 | 57 | 22.3618 | 478000 | 478000 | 60.6 | 21000 | 6997.3966 |  | 2
115 | 80 | 75 | 79.7527 | 529000 | 52000 | 69.6 | 12000 | 2535.9832 |  | 2
115 | 80 | 72 | 68.6171 | 493000 | 99000 | 68.7 | 12000 | 2273.4246 |  | 2
115 | 80 | 67 | 51.5724 | 440000 | 180000 | 68.2 | 12000 | 2273.4246 |  | 2
115 | 80 | 62 | 36.2232 | 396000 | 265000 | 68.7 | 12000 | 2029.6201 |  | 2
115 | 80 | 57 | 22.3618 | 379000 | 349000 | 69 | 12000 | 2029.6201 |  | 2
115 | 80 | 75 | 79.7527 | 553000 | 60000 | 70.1 | 15000 | 3640.3966 |  | 2
115 | 80 | 72 | 68.6171 | 514000 | 113000 | 69 | 15000 | 3640.3966 |  | 2
115 | 80 | 67 | 51.5724 | 459000 | 210000 | 68 | 15000 | 3369.5028 |  | 2
115 | 80 | 62 | 36.2232 | 415000 | 312000 | 68 | 15000 | 3369.5028 |  | 2
115 | 80 | 57 | 22.3618 | 400000 | 387000 | 68.4 | 15000 | 3106.9441 |  | 2
115 | 80 | 75 | 79.7527 | 573000 | 74000 | 70.7 | 18000 | 5232.419 |  | 2
115 | 80 | 72 | 68.6171 | 530000 | 133000 | 69.3 | 18000 | 5232.419 |  | 2
115 | 80 | 67 | 51.5724 | 473000 | 243000 | 68 | 18000 | 4928.1844 |  | 2
115 | 80 | 62 | 36.2232 | 432000 | 361000 | 67.7 | 18000 | 4928.1844 |  | 2
115 | 80 | 57 | 22.3618 | 420000 | 420000 | 67.8 | 18000 | 4928.1844 |  | 2
115 | 80 | 75 | 79.7527 | 587000 | 86000 | 71.2 | 21000 | 7355.8101 |  | 2
115 | 80 | 72 | 68.6171 | 544000 | 155000 | 69.6 | 21000 | 7355.8101 |  | 2
115 | 80 | 67 | 51.5724 | 482000 | 276000 | 68.1 | 21000 | 6997.3966 |  | 2
115 | 80 | 62 | 36.2232 | 451000 | 400000 | 67.5 | 21000 | 6997.3966 |  | 2
115 | 80 | 57 | 22.3618 | 438000 | 438000 | 67.6 | 21000 | 6997.3966 |  | 2
75 | 80 | 75 | 79.7527 | 847000 | 301000 | 51.7 | 24000 | 10035.5754 |  | 2
75 | 80 | 72 | 68.6171 | 805000 | 384000 | 50.8 | 24000 | 10035.5754 |  | 2
75 | 80 | 67 | 51.5724 | 691000 | 471000 | 48.6 | 24000 | 10035.5754 |  | 2
75 | 80 | 62 | 36.2232 | 637000 | 599000 | 47.4 | 24000 | 10035.5754 |  | 2
75 | 80 | 57 | 22.3618 | 607000 | 607000 | 46.9 | 24000 | 10035.5754 |  | 2
75 | 80 | 75 | 79.7527 | 859000 | 321000 | 52.1 | 27000 | 13344.648 |  | 2
75 | 80 | 72 | 68.6171 | 791000 | 379000 | 50.7 | 27000 | 13344.648 |  | 2
75 | 80 | 67 | 51.5724 | 720000 | 526000 | 49.1 | 27000 | 13344.648 |  | 2
75 | 80 | 62 | 36.2232 | 662000 | 638000 | 47.8 | 27000 | 13344.648 |  | 2
75 | 80 | 57 | 22.3618 | 654000 | 654000 | 47.6 | 27000 | 13344.648 |  | 2
85 | 80 | 75 | 79.7527 | 776000 | 239000 | 55.3 | 24000 | 10035.5754 |  | 2
85 | 80 | 72 | 68.6171 | 725000 | 312000 | 54.2 | 24000 | 10035.5754 |  | 2
85 | 80 | 67 | 51.5724 | 651000 | 440000 | 52.5 | 24000 | 10035.5754 |  | 2
85 | 80 | 62 | 36.2232 | 591000 | 552000 | 51.2 | 24000 | 10035.5754 |  | 2
85 | 80 | 57 | 22.3618 | 574000 | 574000 | 50.9 | 24000 | 10035.5754 |  | 2
85 | 80 | 75 | 79.7527 | 795000 | 261000 | 55.9 | 27000 | 13344.648 |  | 2
85 | 80 | 72 | 68.6171 | 737000 | 337000 | 54.5 | 27000 | 13344.648 |  | 2
85 | 80 | 67 | 51.5724 | 662000 | 478000 | 52.8 | 27000 | 13344.648 |  | 2
85 | 80 | 62 | 36.2232 | 601000 | 584000 | 51.5 | 27000 | 13344.648 |  | 2
85 | 80 | 57 | 22.3618 | 599000 | 599000 | 51.5 | 27000 | 13344.648 |  | 2
95 | 80 | 75 | 79.7527 | 701000 | 173000 | 59.6 | 24000 | 10035.5754 |  | 2
95 | 80 | 72 | 68.6171 | 683000 | 279000 | 58.8 | 24000 | 10035.5754 |  | 2
95 | 80 | 67 | 51.5724 | 609000 | 407000 | 57.1 | 24000 | 10035.5754 |  | 2
95 | 80 | 62 | 36.2232 | 550000 | 513000 | 55.8 | 24000 | 10035.5754 |  | 2
95 | 80 | 57 | 22.3618 | 535000 | 535000 | 55.5 | 24000 | 10035.5754 |  | 2
95 | 80 | 75 | 79.7527 | 747000 | 225000 | 60.3 | 27000 | 13344.648 |  | 2
95 | 80 | 72 | 68.6171 | 694000 | 304000 | 59.1 | 27000 | 13344.648 |  | 2
95 | 80 | 67 | 51.5724 | 619000 | 443000 | 57.3 | 27000 | 13344.648 |  | 2
95 | 80 | 62 | 36.2232 | 561000 | 546000 | 56.1 | 27000 | 13344.648 |  | 2
95 | 80 | 57 | 22.3618 | 554000 | 554000 | 56 | 27000 | 13344.648 |  | 2
105 | 80 | 75 | 79.7527 | 656000 | 141000 | 65.1 | 24000 | 10035.5754 |  | 2
105 | 80 | 72 | 68.6171 | 610000 | 218000 | 63.7 | 24000 | 10035.5754 |  | 2
105 | 80 | 67 | 51.5724 | 544000 | 351000 | 62.1 | 24000 | 10035.5754 |  | 2
105 | 80 | 62 | 36.2232 | 509000 | 474000 | 61.2 | 24000 | 10035.5754 |  | 2
105 | 80 | 57 | 22.3618 | 495000 | 495000 | 61 | 24000 | 9618.8156 |  | 2
105 | 80 | 75 | 79.7527 | 667000 | 156000 | 65.4 | 27000 | 13344.648 |  | 2
105 | 80 | 72 | 68.6171 | 618000 | 238000 | 64 | 27000 | 13344.648 |  | 2
105 | 80 | 67 | 51.5724 | 550000 | 385000 | 62.3 | 27000 | 13344.648 |  | 2
105 | 80 | 62 | 36.2232 | 519000 | 505000 | 61.4 | 27000 | 13344.648 |  | 2
105 | 80 | 57 | 22.3618 | 512000 | 512000 | 61.3 | 27000 | 13344.648 |  | 2
115 | 80 | 75 | 79.7527 | 599000 | 100000 | 71.7 | 24000 | 10035.5754 |  | 2
115 | 80 | 72 | 68.6171 | 553000 | 175000 | 69.9 | 24000 | 10035.5754 |  | 2
115 | 80 | 67 | 51.5724 | 491000 | 311000 | 68.2 | 24000 | 9618.8156 |  | 2
115 | 80 | 62 | 36.2232 | 465000 | 432000 | 67.6 | 24000 | 9618.8156 |  | 2
115 | 80 | 57 | 22.3618 | 453000 | 453000 | 67.5 | 24000 | 9618.8156 |  | 2
115 | 80 | 75 | 79.7527 | 609000 | 115000 | 72.1 | 27000 | 13344.648 |  | 2
115 | 80 | 72 | 68.6171 | 561000 | 197000 | 70.1 | 27000 | 13344.648 |  | 2
115 | 80 | 67 | 51.5724 | 498000 | 346000 | 68.3 | 27000 | 12861.2067 |  | 2
115 | 80 | 62 | 36.2232 | 471000 | 460000 | 67.7 | 27000 | 12861.2067 |  | 2
115 | 80 | 57 | 22.3618 | 466000 | 466000 | 67.6 | 27000 | 12861.2067 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 15
Degradation Coefficient (C_d) |  | 48/50 070 (70 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 791000 | 255000 | 52.2 | 14000 | 3217.3855 |  | 1
75 | 80 | 72 | 68.6171 | 754000 | 309000 | 51.2 | 14000 | 3217.3855 |  | 1
75 | 80 | 67 | 51.5724 | 683000 | 393000 | 49.8 | 14000 | 3217.3855 |  | 1
75 | 80 | 62 | 36.2232 | 644000 | 488000 | 48.8 | 14000 | 3217.3855 |  | 1
75 | 80 | 57 | 22.3618 | 576000 | 552000 | 47.5 | 14000 | 3217.3855 |  | 1
75 | 80 | 75 | 79.7527 | 812000 | 257000 | 53 | 17500 | 4936.5196 |  | 1
75 | 80 | 72 | 68.6171 | 787000 | 336000 | 52.1 | 17500 | 4936.5196 |  | 1
75 | 80 | 67 | 51.5724 | 726000 | 440000 | 50.6 | 17500 | 4936.5196 |  | 1
75 | 80 | 62 | 36.2232 | 676000 | 549000 | 49.5 | 17500 | 4936.5196 |  | 1
75 | 80 | 57 | 22.3618 | 627000 | 627000 | 48.6 | 17500 | 4936.5196 |  | 1
75 | 80 | 75 | 79.7527 | 855000 | 292000 | 54.3 | 21000 | 7355.8101 |  | 1
75 | 80 | 72 | 68.6171 | 813000 | 363000 | 53.1 | 21000 | 7355.8101 |  | 1
75 | 80 | 67 | 51.5724 | 749000 | 483000 | 51.2 | 21000 | 7355.8101 |  | 1
75 | 80 | 62 | 36.2232 | 671000 | 580000 | 49.6 | 21000 | 7355.8101 |  | 1
75 | 80 | 57 | 22.3618 | 663000 | 663000 | 49.3 | 21000 | 7355.8101 |  | 1
75 | 80 | 75 | 79.7527 | 875000 | 308000 | 54.8 | 24500 | 10546.1061 |  | 1
75 | 80 | 72 | 68.6171 | 813000 | 369000 | 53.1 | 24500 | 10546.1061 |  | 1
75 | 80 | 67 | 51.5724 | 767000 | 525000 | 51.7 | 24500 | 10546.1061 |  | 1
75 | 80 | 62 | 36.2232 | 703000 | 648000 | 50.4 | 24500 | 10546.1061 |  | 1
75 | 80 | 57 | 22.3618 | 681000 | 681000 | 49.6 | 24500 | 10546.1061 |  | 1
85 | 80 | 75 | 79.7527 | 738000 | 209000 | 56.1 | 14000 | 3217.3855 |  | 1
85 | 80 | 72 | 68.6171 | 724000 | 286000 | 55.5 | 14000 | 3217.3855 |  | 1
85 | 80 | 67 | 51.5724 | 665000 | 374000 | 54.1 | 14000 | 3217.3855 |  | 1
85 | 80 | 62 | 36.2232 | 618000 | 467000 | 53.2 | 14000 | 3217.3855 |  | 1
85 | 80 | 57 | 22.3618 | 551000 | 529000 | 51.8 | 14000 | 3217.3855 |  | 1
85 | 80 | 75 | 79.7527 | 774000 | 229000 | 57.2 | 17500 | 4936.5196 |  | 1
85 | 80 | 72 | 68.6171 | 738000 | 295000 | 56.2 | 17500 | 4936.5196 |  | 1
85 | 80 | 67 | 51.5724 | 695000 | 416000 | 54.9 | 17500 | 4936.5196 |  | 1
85 | 80 | 62 | 36.2232 | 637000 | 517000 | 53.6 | 17500 | 4936.5196 |  | 1
85 | 80 | 57 | 22.3618 | 588000 | 588000 | 52.5 | 17500 | 4936.5196 |  | 1
85 | 80 | 75 | 79.7527 | 815000 | 264000 | 58.4 | 21000 | 7355.8101 |  | 1
85 | 80 | 72 | 68.6171 | 776000 | 337000 | 57.3 | 21000 | 7355.8101 |  | 1
85 | 80 | 67 | 51.5724 | 716000 | 458000 | 55.4 | 21000 | 7355.8101 |  | 1
85 | 80 | 62 | 36.2232 | 668000 | 584000 | 54.3 | 21000 | 7355.8101 |  | 1
85 | 80 | 57 | 22.3618 | 623000 | 623000 | 53.3 | 21000 | 7355.8101 |  | 1
85 | 80 | 75 | 79.7527 | 833000 | 279000 | 59 | 24500 | 10546.1061 |  | 1
85 | 80 | 72 | 68.6171 | 793000 | 361000 | 57.8 | 24500 | 10546.1061 |  | 1
85 | 80 | 67 | 51.5724 | 731000 | 497000 | 56.1 | 24500 | 10546.1061 |  | 1
85 | 80 | 62 | 36.2232 | 672000 | 624000 | 54.7 | 24500 | 10546.1061 |  | 1
85 | 80 | 57 | 22.3618 | 675000 | 675000 | 55.7 | 24500 | 10546.1061 |  | 1
95 | 80 | 75 | 79.7527 | 723000 | 205000 | 61.7 | 14000 | 3217.3855 |  | 1
95 | 80 | 72 | 68.6171 | 687000 | 258000 | 60.7 | 14000 | 3217.3855 |  | 1
95 | 80 | 67 | 51.5724 | 627000 | 344000 | 59.2 | 14000 | 3217.3855 |  | 1
95 | 80 | 62 | 36.2232 | 595000 | 453000 | 59.7 | 14000 | 3217.3855 |  | 1
95 | 80 | 57 | 22.3618 | 543000 | 522000 | 59.3 | 14000 | 3217.3855 |  | 1
95 | 80 | 75 | 79.7527 | 754000 | 221000 | 62.6 | 17500 | 4936.5196 |  | 1
95 | 80 | 72 | 68.6171 | 718000 | 285000 | 61.6 | 17500 | 4936.5196 |  | 1
95 | 80 | 67 | 51.5724 | 660000 | 390000 | 60.1 | 17500 | 4936.5196 |  | 1
95 | 80 | 62 | 36.2232 | 579000 | 467000 | 58.3 | 17500 | 4936.5196 |  | 1
95 | 80 | 57 | 22.3618 | 577000 | 577000 | 59.8 | 17500 | 4936.5196 |  | 1
95 | 80 | 75 | 79.7527 | 775000 | 236000 | 63.3 | 21000 | 7355.8101 |  | 1
95 | 80 | 72 | 68.6171 | 739000 | 310000 | 62.2 | 21000 | 7355.8101 |  | 1
95 | 80 | 67 | 51.5724 | 681000 | 431000 | 60.6 | 21000 | 7355.8101 |  | 1
95 | 80 | 62 | 36.2232 | 646000 | 571000 | 60.7 | 21000 | 7355.8101 |  | 1
95 | 80 | 57 | 22.3618 | 616000 | 616000 | 60.4 | 21000 | 7355.8101 |  | 1
95 | 80 | 75 | 79.7527 | 791000 | 250000 | 63.8 | 24500 | 10546.1061 |  | 1
95 | 80 | 72 | 68.6171 | 753000 | 333000 | 62.7 | 24500 | 10546.1061 |  | 1
95 | 80 | 67 | 51.5724 | 696000 | 472000 | 61.1 | 24500 | 10546.1061 |  | 1
95 | 80 | 62 | 36.2232 | 639000 | 597000 | 59.6 | 24500 | 10546.1061 |  | 1
95 | 80 | 57 | 22.3618 | 621000 | 621000 | 59.2 | 24500 | 10546.1061 |  | 1
105 | 80 | 75 | 79.7527 | 685000 | 178000 | 67.3 | 14000 | 3217.3855 |  | 1
105 | 80 | 72 | 68.6171 | 650000 | 232000 | 66.4 | 14000 | 3217.3855 |  | 1
105 | 80 | 67 | 51.5724 | 605000 | 333000 | 65.9 | 14000 | 3217.3855 |  | 1
105 | 80 | 62 | 36.2232 | 565000 | 431000 | 65.7 | 14000 | 3217.3855 |  | 1
105 | 80 | 57 | 22.3618 | 517000 | 498000 | 65.5 | 14000 | 3217.3855 |  | 1
105 | 80 | 75 | 79.7527 | 714000 | 193000 | 68.2 | 17500 | 4936.5196 |  | 1
105 | 80 | 72 | 68.6171 | 679000 | 257000 | 67.2 | 17500 | 4936.5196 |  | 1
105 | 80 | 67 | 51.5724 | 624000 | 364000 | 65.8 | 17500 | 4936.5196 |  | 1
105 | 80 | 62 | 36.2232 | 593000 | 491000 | 66.2 | 17500 | 4936.5196 |  | 1
105 | 80 | 57 | 22.3618 | 552000 | 552000 | 65.9 | 17500 | 4936.5196 |  | 1
105 | 80 | 75 | 79.7527 | 733000 | 207000 | 68.8 | 21000 | 7355.8101 |  | 1
105 | 80 | 72 | 68.6171 | 699000 | 282000 | 67.8 | 21000 | 7355.8101 |  | 1
105 | 80 | 67 | 51.5724 | 643000 | 405000 | 66.3 | 21000 | 7355.8101 |  | 1
105 | 80 | 62 | 36.2232 | 613000 | 547000 | 66.7 | 21000 | 7355.8101 |  | 1
105 | 80 | 57 | 22.3618 | 586000 | 586000 | 66.6 | 21000 | 7355.8101 |  | 1
105 | 80 | 75 | 79.7527 | 747000 | 221000 | 69.3 | 24500 | 10546.1061 |  | 1
105 | 80 | 72 | 68.6171 | 713000 | 305000 | 68.2 | 24500 | 10546.1061 |  | 1
105 | 80 | 67 | 51.5724 | 657000 | 444000 | 66.7 | 24500 | 10546.1061 |  | 1
105 | 80 | 62 | 36.2232 | 604000 | 560000 | 65.3 | 24500 | 10546.1061 |  | 1
105 | 80 | 57 | 22.3618 | 589000 | 589000 | 64.9 | 24500 | 10546.1061 |  | 1
115 | 80 | 75 | 79.7527 | 643000 | 150000 | 73.7 | 14000 | 3217.3855 |  | 1
115 | 80 | 72 | 68.6171 | 610000 | 205000 | 72.8 | 14000 | 3217.3855 |  | 1
115 | 80 | 67 | 51.5724 | 583000 | 321000 | 73.4 | 14000 | 3217.3855 |  | 1
115 | 80 | 62 | 36.2232 | 532000 | 408000 | 72.9 | 14000 | 3217.3855 |  | 1
115 | 80 | 57 | 22.3618 | 483000 | 471000 | 72.7 | 14000 | 2950.6592 |  | 1
115 | 80 | 75 | 79.7527 | 670000 | 163000 | 74.5 | 17500 | 4936.5196 |  | 1
115 | 80 | 72 | 68.6171 | 637000 | 229000 | 73.6 | 17500 | 4936.5196 |  | 1
115 | 80 | 67 | 51.5724 | 584000 | 337000 | 72.2 | 17500 | 4936.5196 |  | 1
115 | 80 | 62 | 36.2232 | 558000 | 467000 | 73.1 | 17500 | 4936.5196 |  | 1
115 | 80 | 57 | 22.3618 | 522000 | 522000 | 73.1 | 17500 | 4936.5196 |  | 1
115 | 80 | 75 | 79.7527 | 705000 | 195000 | 75.9 | 21000 | 7355.8101 |  | 1
115 | 80 | 72 | 68.6171 | 655000 | 253000 | 74.1 | 21000 | 7355.8101 |  | 1
115 | 80 | 67 | 51.5724 | 602000 | 377000 | 72.7 | 21000 | 7355.8101 |  | 1
115 | 80 | 62 | 36.2232 | 576000 | 522000 | 73.5 | 21000 | 7355.8101 |  | 1
115 | 80 | 57 | 22.3618 | 555000 | 555000 | 73.5 | 21000 | 7355.8101 |  | 1
115 | 80 | 75 | 79.7527 | 718000 | 209000 | 76.3 | 24500 | 10546.1061 |  | 1
115 | 80 | 72 | 68.6171 | 668000 | 275000 | 74.5 | 24500 | 10546.1061 |  | 1
115 | 80 | 67 | 51.5724 | 615000 | 416000 | 73 | 24500 | 10546.1061 |  | 1
115 | 80 | 62 | 36.2232 | 567000 | 526000 | 71.7 | 24500 | 10546.1061 |  | 1
115 | 80 | 57 | 22.3618 | 554000 | 554000 | 71.4 | 24500 | 10546.1061 |  | 1
75 | 80 | 75 | 79.7527 | 703000 | 648000 | 50.4 | 28000 | 14599.095 |  | 1
75 | 80 | 72 | 68.6171 | 888000 | 332000 | 55.2 | 28000 | 14599.095 |  | 1
75 | 80 | 67 | 51.5724 | 847000 | 414000 | 54.1 | 28000 | 14599.095 |  | 1
75 | 80 | 62 | 36.2232 | 777000 | 561000 | 52.3 | 28000 | 14599.095 |  | 1
75 | 80 | 57 | 22.3618 | 717000 | 717000 | 50.5 | 28000 | 14599.095 |  | 1
75 | 80 | 75 | 79.7527 | 897000 | 333000 | 55.5 | 30000 | 17351.7933 |  | 1
75 | 80 | 72 | 68.6171 | 854000 | 428000 | 54.3 | 30000 | 17351.7933 |  | 1
75 | 80 | 67 | 51.5724 | 783000 | 582000 | 52.5 | 30000 | 17351.7933 |  | 1
75 | 80 | 62 | 36.2232 | 696000 | 681000 | 50.4 | 30000 | 17351.7933 |  | 1
75 | 80 | 57 | 22.3618 | 728000 | 728000 | 50.8 | 30000 | 17351.7933 |  | 1
85 | 80 | 75 | 79.7527 | 847000 | 294000 | 59.4 | 28000 | 14599.095 |  | 1
85 | 80 | 72 | 68.6171 | 806000 | 385000 | 58.2 | 28000 | 14599.095 |  | 1
85 | 80 | 67 | 51.5724 | 744000 | 536000 | 56.5 | 28000 | 14599.095 |  | 1
85 | 80 | 62 | 36.2232 | 683000 | 657000 | 54.9 | 28000 | 14599.095 |  | 1
85 | 80 | 57 | 22.3618 | 675000 | 675000 | 54.7 | 28000 | 14599.095 |  | 1
85 | 80 | 75 | 79.7527 | 853000 | 303000 | 59.6 | 30000 | 17351.7933 |  | 1
85 | 80 | 72 | 68.6171 | 812000 | 399000 | 58.4 | 30000 | 17351.7933 |  | 1
85 | 80 | 67 | 51.5724 | 750000 | 558000 | 56.7 | 30000 | 17351.7933 |  | 1
85 | 80 | 62 | 36.2232 | 715000 | 700000 | 56.9 | 30000 | 17351.7933 |  | 1
85 | 80 | 57 | 22.3618 | 709000 | 709000 | 56.3 | 30000 | 17351.7933 |  | 1
95 | 80 | 75 | 79.7527 | 802000 | 265000 | 64.2 | 28000 | 14599.095 |  | 1
95 | 80 | 72 | 68.6171 | 766000 | 357000 | 63.1 | 28000 | 14599.095 |  | 1
95 | 80 | 67 | 51.5724 | 707000 | 510000 | 61.4 | 28000 | 14599.095 |  | 1
95 | 80 | 62 | 36.2232 | 677000 | 654000 | 61.5 | 28000 | 14599.095 |  | 1
95 | 80 | 57 | 22.3618 | 669000 | 669000 | 61.3 | 28000 | 14599.095 |  | 1
95 | 80 | 75 | 79.7527 | 808000 | 273000 | 64.4 | 30000 | 17351.7933 |  | 1
95 | 80 | 72 | 68.6171 | 771000 | 370000 | 63.3 | 30000 | 17351.7933 |  | 1
95 | 80 | 67 | 51.5724 | 713000 | 531000 | 61.6 | 30000 | 17351.7933 |  | 1
95 | 80 | 62 | 36.2232 | 685000 | 674000 | 61.8 | 30000 | 17351.7933 |  | 1
95 | 80 | 57 | 22.3618 | 608000 | 608000 | 59.2 | 30000 | 17351.7933 |  | 1
105 | 80 | 75 | 79.7527 | 758000 | 235000 | 69.7 | 28000 | 14599.095 |  | 1
105 | 80 | 72 | 68.6171 | 724000 | 328000 | 68.6 | 28000 | 14599.095 |  | 1
105 | 80 | 67 | 51.5724 | 668000 | 482000 | 67 | 28000 | 14599.095 |  | 1
105 | 80 | 62 | 36.2232 | 643000 | 623000 | 67.5 | 28000 | 14599.095 |  | 1
105 | 80 | 57 | 22.3618 | 635000 | 635000 | 67.4 | 28000 | 14599.095 |  | 1
105 | 80 | 75 | 79.7527 | 763000 | 242000 | 69.8 | 30000 | 17351.7933 |  | 1
105 | 80 | 72 | 68.6171 | 729000 | 341000 | 68.8 | 30000 | 17351.7933 |  | 1
105 | 80 | 67 | 51.5724 | 672000 | 503000 | 67.2 | 30000 | 17351.7933 |  | 1
105 | 80 | 62 | 36.2232 | 652000 | 643000 | 67.8 | 30000 | 17351.7933 |  | 1
105 | 80 | 57 | 22.3618 | 646000 | 646000 | 67.6 | 30000 | 17351.7933 |  | 1
115 | 80 | 75 | 79.7527 | 711000 | 204000 | 75.9 | 28000 | 14599.095 |  | 1
115 | 80 | 72 | 68.6171 | 697000 | 318000 | 75.7 | 28000 | 14599.095 |  | 1
115 | 80 | 67 | 51.5724 | 624000 | 453000 | 73.3 | 28000 | 14599.095 |  | 1
115 | 80 | 62 | 36.2232 | 581000 | 561000 | 72.1 | 28000 | 14599.095 |  | 1
115 | 80 | 57 | 22.3618 | 573000 | 573000 | 71.9 | 28000 | 14599.095 |  | 1
115 | 80 | 75 | 79.7527 | 738000 | 235000 | 77 | 30000 | 17351.7933 |  | 1
115 | 80 | 72 | 68.6171 | 701000 | 331000 | 75.9 | 30000 | 17351.7933 |  | 1
115 | 80 | 67 | 51.5724 | 629000 | 474000 | 73.5 | 30000 | 17351.7933 |  | 1
115 | 80 | 62 | 36.2232 | 587000 | 580000 | 72.3 | 30000 | 17351.7933 |  | 1
115 | 80 | 57 | 22.3618 | 610000 | 610000 | 74.3 | 30000 | 17351.7933 |  | 1
75 | 80 | 75 | 79.7527 | 798000 | 236000 | 52.9 | 14000 | 3217.3855 |  | 2
75 | 80 | 72 | 68.6171 | 759000 | 292000 | 51.8 | 14000 | 3217.3855 |  | 2
75 | 80 | 67 | 51.5724 | 699000 | 386000 | 50.3 | 14000 | 3217.3855 |  | 2
75 | 80 | 62 | 36.2232 | 643000 | 478000 | 49 | 14000 | 3217.3855 |  | 2
75 | 80 | 57 | 22.3618 | 604000 | 578000 | 48.1 | 14000 | 3217.3855 |  | 2
75 | 80 | 75 | 79.7527 | 835000 | 253000 | 53.9 | 17500 | 4936.5196 |  | 2
75 | 80 | 72 | 68.6171 | 793000 | 320000 | 52.8 | 17500 | 4936.5196 |  | 2
75 | 80 | 67 | 51.5724 | 732000 | 433000 | 51.1 | 17500 | 4936.5196 |  | 2
75 | 80 | 62 | 36.2232 | 675000 | 544000 | 49.7 | 17500 | 4936.5196 |  | 2
75 | 80 | 57 | 22.3618 | 635000 | 631000 | 48.8 | 17500 | 4936.5196 |  | 2
75 | 80 | 75 | 79.7527 | 861000 | 271000 | 54.7 | 21000 | 7355.8101 |  | 2
75 | 80 | 72 | 68.6171 | 817000 | 348000 | 53.5 | 21000 | 7355.8101 |  | 2
75 | 80 | 67 | 51.5724 | 754000 | 478000 | 51.8 | 21000 | 7355.8101 |  | 2
75 | 80 | 62 | 36.2232 | 698000 | 607000 | 50.3 | 21000 | 7355.8101 |  | 2
75 | 80 | 57 | 22.3618 | 669000 | 669000 | 49.6 | 21000 | 7355.8101 |  | 2
75 | 80 | 75 | 79.7527 | 879000 | 288000 | 55.3 | 24500 | 10546.1061 |  | 2
75 | 80 | 72 | 68.6171 | 836000 | 375000 | 54.1 | 24500 | 10546.1061 |  | 2
75 | 80 | 67 | 51.5724 | 769000 | 522000 | 52.2 | 24500 | 10546.1061 |  | 2
75 | 80 | 62 | 36.2232 | 716000 | 664000 | 50.8 | 24500 | 10546.1061 |  | 2
75 | 80 | 57 | 22.3618 | 700000 | 700000 | 50.3 | 24500 | 10546.1061 |  | 2
85 | 80 | 75 | 79.7527 | 762000 | 207000 | 57 | 14000 | 3217.3855 |  | 2
85 | 80 | 72 | 68.6171 | 725000 | 264000 | 56 | 14000 | 3217.3855 |  | 2
85 | 80 | 67 | 51.5724 | 668000 | 361000 | 54.6 | 14000 | 3217.3855 |  | 2
85 | 80 | 62 | 36.2232 | 610000 | 451000 | 53.3 | 14000 | 3217.3855 |  | 2
85 | 80 | 57 | 22.3618 | 586000 | 558000 | 52.7 | 14000 | 3217.3855 |  | 2
85 | 80 | 75 | 79.7527 | 795000 | 222000 | 58 | 17500 | 4936.5196 |  | 2
85 | 80 | 72 | 68.6171 | 757000 | 290000 | 57 | 17500 | 4936.5196 |  | 2
85 | 80 | 67 | 51.5724 | 697000 | 405000 | 55.3 | 17500 | 4936.5196 |  | 2
85 | 80 | 62 | 36.2232 | 644000 | 519000 | 54 | 17500 | 4936.5196 |  | 2
85 | 80 | 57 | 22.3618 | 600000 | 598000 | 53.1 | 17500 | 4936.5196 |  | 2
85 | 80 | 75 | 79.7527 | 817000 | 237000 | 58.7 | 21000 | 7355.8101 |  | 2
85 | 80 | 72 | 68.6171 | 778000 | 316000 | 57.6 | 21000 | 7355.8101 |  | 2
85 | 80 | 67 | 51.5724 | 718000 | 449000 | 55.9 | 21000 | 7355.8101 |  | 2
85 | 80 | 62 | 36.2232 | 664000 | 579000 | 54.5 | 21000 | 7355.8101 |  | 2
85 | 80 | 57 | 22.3618 | 638000 | 638000 | 53.9 | 21000 | 7355.8101 |  | 2
85 | 80 | 75 | 79.7527 | 833000 | 253000 | 59.3 | 24500 | 10546.1061 |  | 2
85 | 80 | 72 | 68.6171 | 793000 | 342000 | 58.1 | 24500 | 10546.1061 |  | 2
85 | 80 | 67 | 51.5724 | 733000 | 493000 | 56.4 | 24500 | 10546.1061 |  | 2
85 | 80 | 62 | 36.2232 | 683000 | 636000 | 55 | 24500 | 10546.1061 |  | 2
85 | 80 | 57 | 22.3618 | 667000 | 667000 | 54.6 | 24500 | 10546.1061 |  | 2
95 | 80 | 75 | 79.7527 | 723000 | 176000 | 62 | 14000 | 3217.3855 |  | 2
95 | 80 | 72 | 68.6171 | 687000 | 235000 | 61 | 14000 | 3217.3855 |  | 2
95 | 80 | 67 | 51.5724 | 632000 | 333000 | 59.6 | 14000 | 3217.3855 |  | 2
95 | 80 | 62 | 36.2232 | 578000 | 427000 | 58.4 | 14000 | 3217.3855 |  | 2
95 | 80 | 57 | 22.3618 | 560000 | 534000 | 58.2 | 14000 | 3217.3855 |  | 2
95 | 80 | 75 | 79.7527 | 752000 | 189000 | 62.8 | 17500 | 4936.5196 |  | 2
95 | 80 | 72 | 68.6171 | 716000 | 259000 | 61.8 | 17500 | 4936.5196 |  | 2
95 | 80 | 67 | 51.5724 | 661000 | 377000 | 60.3 | 17500 | 4936.5196 |  | 2
95 | 80 | 62 | 36.2232 | 610000 | 492000 | 59.1 | 17500 | 4936.5196 |  | 2
95 | 80 | 57 | 22.3618 | 568000 | 562000 | 58.1 | 17500 | 4936.5196 |  | 2
95 | 80 | 75 | 79.7527 | 773000 | 203000 | 63.5 | 21000 | 7355.8101 |  | 2
95 | 80 | 72 | 68.6171 | 735000 | 284000 | 62.4 | 21000 | 7355.8101 |  | 2
95 | 80 | 67 | 51.5724 | 679000 | 419000 | 60.9 | 21000 | 7355.8101 |  | 2
95 | 80 | 62 | 36.2232 | 631000 | 553000 | 59.6 | 21000 | 7355.8101 |  | 2
95 | 80 | 57 | 22.3618 | 607000 | 607000 | 59 | 21000 | 7355.8101 |  | 2
95 | 80 | 75 | 79.7527 | 787000 | 218000 | 64 | 24500 | 10546.1061 |  | 2
95 | 80 | 72 | 68.6171 | 749000 | 308000 | 62.9 | 24500 | 10546.1061 |  | 2
95 | 80 | 67 | 51.5724 | 693000 | 462000 | 61.3 | 24500 | 10546.1061 |  | 2
95 | 80 | 62 | 36.2232 | 649000 | 600000 | 60 | 24500 | 10546.1061 |  | 2
95 | 80 | 57 | 22.3618 | 634000 | 634000 | 59.7 | 24500 | 10546.1061 |  | 2
105 | 80 | 75 | 79.7527 | 680000 | 145000 | 67.7 | 14000 | 3217.3855 |  | 2
105 | 80 | 72 | 68.6171 | 646000 | 205000 | 66.7 | 14000 | 3217.3855 |  | 2
105 | 80 | 67 | 51.5724 | 594000 | 305000 | 65.6 | 14000 | 3217.3855 |  | 2
105 | 80 | 62 | 36.2232 | 548000 | 405000 | 65.2 | 14000 | 3217.3855 |  | 2
105 | 80 | 57 | 22.3618 | 533000 | 508000 | 65.1 | 14000 | 3217.3855 |  | 2
105 | 80 | 75 | 79.7527 | 706000 | 155000 | 68.5 | 17500 | 4936.5196 |  | 2
105 | 80 | 72 | 68.6171 | 671000 | 226000 | 67.5 | 17500 | 4936.5196 |  | 2
105 | 80 | 67 | 51.5724 | 618000 | 346000 | 66.1 | 17500 | 4936.5196 |  | 2
105 | 80 | 62 | 36.2232 | 570000 | 463000 | 65.3 | 17500 | 4936.5196 |  | 2
105 | 80 | 57 | 22.3618 | 528000 | 528000 | 64.7 | 17500 | 4936.5196 |  | 2
105 | 80 | 75 | 79.7527 | 724000 | 167000 | 69.1 | 21000 | 7355.8101 |  | 2
105 | 80 | 72 | 68.6171 | 688000 | 249000 | 68 | 21000 | 7355.8101 |  | 2
105 | 80 | 67 | 51.5724 | 636000 | 387000 | 66.5 | 21000 | 7355.8101 |  | 2
105 | 80 | 62 | 36.2232 | 592000 | 523000 | 65.6 | 21000 | 7355.8101 |  | 2
105 | 80 | 57 | 22.3618 | 569000 | 569000 | 65.2 | 21000 | 7355.8101 |  | 2
105 | 80 | 75 | 79.7527 | 737000 | 181000 | 69.5 | 24500 | 10546.1061 |  | 2
105 | 80 | 72 | 68.6171 | 701000 | 273000 | 68.4 | 24500 | 10546.1061 |  | 2
105 | 80 | 67 | 51.5724 | 648000 | 429000 | 66.9 | 24500 | 10546.1061 |  | 2
105 | 80 | 62 | 36.2232 | 610000 | 563000 | 65.8 | 24500 | 10546.1061 |  | 2
105 | 80 | 57 | 22.3618 | 598000 | 598000 | 65.7 | 24500 | 10546.1061 |  | 2
115 | 80 | 75 | 79.7527 | 633000 | 111000 | 74.5 | 14000 | 3217.3855 |  | 2
115 | 80 | 72 | 68.6171 | 601000 | 173000 | 73.8 | 14000 | 3217.3855 |  | 2
115 | 80 | 67 | 51.5724 | 553000 | 276000 | 73.2 | 14000 | 3217.3855 |  | 2
115 | 80 | 62 | 36.2232 | 504000 | 373000 | 73.1 | 14000 | 3217.3855 |  | 2
115 | 80 | 57 | 22.3618 | 502000 | 479000 | 73.5 | 14000 | 3217.3855 |  | 2
115 | 80 | 75 | 79.7527 | 656000 | 120000 | 75.1 | 17500 | 4936.5196 |  | 2
115 | 80 | 72 | 68.6171 | 624000 | 193000 | 74.2 | 17500 | 4936.5196 |  | 2
115 | 80 | 67 | 51.5724 | 575000 | 316000 | 73.4 | 17500 | 4936.5196 |  | 2
115 | 80 | 62 | 36.2232 | 532000 | 442000 | 73 | 17500 | 4936.5196 |  | 2
115 | 80 | 57 | 22.3618 | 507000 | 507000 | 72.9 | 17500 | 4936.5196 |  | 2
115 | 80 | 75 | 79.7527 | 671000 | 130000 | 75.5 | 21000 | 7355.8101 |  | 2
115 | 80 | 72 | 68.6171 | 638000 | 214000 | 74.6 | 21000 | 7355.8101 |  | 2
115 | 80 | 67 | 51.5724 | 590000 | 355000 | 73.6 | 21000 | 7355.8101 |  | 2
115 | 80 | 62 | 36.2232 | 559000 | 494000 | 73.1 | 21000 | 7355.8101 |  | 2
115 | 80 | 57 | 22.3618 | 536000 | 536000 | 72.9 | 21000 | 7355.8101 |  | 2
115 | 80 | 75 | 79.7527 | 683000 | 143000 | 75.9 | 24500 | 10546.1061 |  | 2
115 | 80 | 72 | 68.6171 | 649000 | 236000 | 74.9 | 24500 | 10546.1061 |  | 2
115 | 80 | 67 | 51.5724 | 601000 | 396000 | 73.7 | 24500 | 10546.1061 |  | 2
115 | 80 | 62 | 36.2232 | 572000 | 527000 | 73.1 | 24500 | 10546.1061 |  | 2
115 | 80 | 57 | 22.3618 | 556000 | 556000 | 73 | 24500 | 10546.1061 |  | 2
75 | 80 | 75 | 79.7527 | 894000 | 305000 | 55.7 | 28000 | 14599.095 |  | 2
75 | 80 | 72 | 68.6171 | 849000 | 403000 | 54.5 | 28000 | 14599.095 |  | 2
75 | 80 | 67 | 51.5724 | 783000 | 567000 | 52.7 | 28000 | 14599.095 |  | 2
75 | 80 | 62 | 36.2232 | 733000 | 705000 | 51.2 | 28000 | 14599.095 |  | 2
75 | 80 | 57 | 22.3618 | 723000 | 723000 | 51 | 28000 | 14599.095 |  | 2
75 | 80 | 75 | 79.7527 | 901000 | 314000 | 56 | 30000 | 17351.7933 |  | 2
75 | 80 | 72 | 68.6171 | 851000 | 414000 | 54.4 | 30000 | 17351.7933 |  | 2
75 | 80 | 67 | 51.5724 | 788000 | 590000 | 52.8 | 30000 | 17351.7933 |  | 2
75 | 80 | 62 | 36.2232 | 741000 | 728000 | 51.5 | 30000 | 17351.7933 |  | 2
75 | 80 | 57 | 22.3618 | 736000 | 736000 | 51.3 | 30000 | 17351.7933 |  | 2
85 | 80 | 75 | 79.7527 | 845000 | 269000 | 59.7 | 28000 | 14599.095 |  | 2
85 | 80 | 72 | 68.6171 | 805000 | 368000 | 58.5 | 28000 | 14599.095 |  | 2
85 | 80 | 67 | 51.5724 | 745000 | 536000 | 56.8 | 28000 | 14599.095 |  | 2
85 | 80 | 62 | 36.2232 | 701000 | 675000 | 55.5 | 28000 | 14599.095 |  | 2
85 | 80 | 57 | 22.3618 | 692000 | 692000 | 55.3 | 28000 | 14599.095 |  | 2
85 | 80 | 75 | 79.7527 | 852000 | 278000 | 59.9 | 30000 | 17351.7933 |  | 2
85 | 80 | 72 | 68.6171 | 810000 | 383000 | 58.7 | 30000 | 17351.7933 |  | 2
85 | 80 | 67 | 51.5724 | 750000 | 560000 | 56.9 | 30000 | 17351.7933 |  | 2
85 | 80 | 62 | 36.2232 | 709000 | 696000 | 55.7 | 30000 | 17351.7933 |  | 2
85 | 80 | 57 | 22.3618 | 703000 | 703000 | 55.6 | 30000 | 17351.7933 |  | 2
95 | 80 | 75 | 79.7527 | 798000 | 233000 | 64.4 | 28000 | 14599.095 |  | 2
95 | 80 | 72 | 68.6171 | 760000 | 334000 | 63.3 | 28000 | 14599.095 |  | 2
95 | 80 | 67 | 51.5724 | 703000 | 503000 | 61.6 | 28000 | 14599.095 |  | 2
95 | 80 | 62 | 36.2232 | 666000 | 641000 | 60.5 | 28000 | 14599.095 |  | 2
95 | 80 | 57 | 22.3618 | 659000 | 659000 | 60.3 | 28000 | 14599.095 |  | 2
95 | 80 | 75 | 79.7527 | 804000 | 241000 | 64.6 | 30000 | 17351.7933 |  | 2
95 | 80 | 72 | 68.6171 | 765000 | 348000 | 63.4 | 30000 | 17351.7933 |  | 2
95 | 80 | 67 | 51.5724 | 708000 | 527000 | 61.8 | 30000 | 17351.7933 |  | 2
95 | 80 | 62 | 36.2232 | 673000 | 662000 | 60.7 | 30000 | 17351.7933 |  | 2
95 | 80 | 57 | 22.3618 | 664000 | 664000 | 60.5 | 30000 | 17351.7933 |  | 2
105 | 80 | 75 | 79.7527 | 747000 | 195000 | 69.9 | 28000 | 14599.095 |  | 2
105 | 80 | 72 | 68.6171 | 710000 | 297000 | 68.8 | 28000 | 14599.095 |  | 2
105 | 80 | 67 | 51.5724 | 657000 | 470000 | 67.2 | 28000 | 14599.095 |  | 2
105 | 80 | 62 | 36.2232 | 626000 | 603000 | 66.3 | 28000 | 14599.095 |  | 2
105 | 80 | 57 | 22.3618 | 619000 | 619000 | 66.1 | 28000 | 14599.095 |  | 2
105 | 80 | 75 | 79.7527 | 752000 | 203000 | 70 | 30000 | 17351.7933 |  | 2
105 | 80 | 72 | 68.6171 | 715000 | 311000 | 68.9 | 30000 | 17351.7933 |  | 2
105 | 80 | 67 | 51.5724 | 661000 | 492000 | 67.4 | 30000 | 17351.7933 |  | 2
105 | 80 | 62 | 36.2232 | 633000 | 624000 | 66.5 | 30000 | 17351.7933 |  | 2
105 | 80 | 57 | 22.3618 | 628000 | 628000 | 66.4 | 30000 | 17351.7933 |  | 2
115 | 80 | 75 | 79.7527 | 691000 | 156000 | 76.2 | 28000 | 14599.095 |  | 2
115 | 80 | 72 | 68.6171 | 657000 | 260000 | 75.2 | 28000 | 14599.095 |  | 2
115 | 80 | 67 | 51.5724 | 609000 | 436000 | 73.9 | 28000 | 14599.095 |  | 2
115 | 80 | 62 | 36.2232 | 583000 | 563000 | 73.3 | 28000 | 14599.095 |  | 2
115 | 80 | 57 | 22.3618 | 573000 | 573000 | 73.2 | 28000 | 14599.095 |  | 2
115 | 80 | 75 | 79.7527 | 696000 | 164000 | 76.4 | 30000 | 17351.7933 |  | 2
115 | 80 | 72 | 68.6171 | 660000 | 273000 | 75.3 | 30000 | 17351.7933 |  | 2
115 | 80 | 67 | 51.5724 | 613000 | 458000 | 74 | 30000 | 17351.7933 |  | 2
115 | 80 | 62 | 36.2232 | 589000 | 583000 | 73.4 | 30000 | 17351.7933 |  | 2
115 | 80 | 57 | 22.3618 | 582000 | 582000 | 73.3 | 30000 | 17351.7933 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 16
Degradation Coefficient (C_d) |  | 48/50 075 (75 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 847000 | 281000 | 56.6 | 14000 | 4632.2849 |  | 1
75 | 80 | 72 | 68.6171 | 771000 | 299000 | 54.6 | 14000 | 4632.2849 |  | 1
75 | 80 | 67 | 51.5724 | 745000 | 432000 | 54.8 | 14000 | 4632.2849 |  | 1
75 | 80 | 62 | 36.2232 | 681000 | 507000 | 53.8 | 14000 | 4632.2849 |  | 1
75 | 80 | 57 | 22.3618 | 619000 | 582000 | 53 | 14000 | 4632.2849 |  | 1
75 | 80 | 75 | 79.7527 | 871000 | 284000 | 57.3 | 17500 | 6013.8436 |  | 1
75 | 80 | 72 | 68.6171 | 829000 | 347000 | 56.2 | 17500 | 6013.8436 |  | 1
75 | 80 | 67 | 51.5724 | 760000 | 447000 | 54.5 | 17500 | 6013.8436 |  | 1
75 | 80 | 62 | 36.2232 | 720000 | 572000 | 54.5 | 17500 | 6013.8436 |  | 1
75 | 80 | 57 | 22.3618 | 659000 | 649000 | 53.9 | 17500 | 6013.8436 |  | 1
75 | 80 | 75 | 79.7527 | 900000 | 301000 | 58.2 | 21000 | 8501.8994 |  | 1
75 | 80 | 72 | 68.6171 | 856000 | 373000 | 57 | 21000 | 8501.8994 |  | 1
75 | 80 | 67 | 51.5724 | 789000 | 494000 | 55.2 | 21000 | 8501.8994 |  | 1
75 | 80 | 62 | 36.2232 | 725000 | 610000 | 53.7 | 21000 | 8501.8994 |  | 1
75 | 80 | 57 | 22.3618 | 674000 | 674000 | 52.5 | 21000 | 8501.8994 |  | 1
75 | 80 | 75 | 79.7527 | 914000 | 310000 | 58.7 | 24500 | 11717.2011 |  | 1
75 | 80 | 72 | 68.6171 | 868000 | 391000 | 57.4 | 24500 | 11717.2011 |  | 1
75 | 80 | 67 | 51.5724 | 809000 | 530000 | 55.8 | 24500 | 11717.2011 |  | 1
75 | 80 | 62 | 36.2232 | 743000 | 665000 | 54.1 | 24500 | 11717.2011 |  | 1
75 | 80 | 57 | 22.3618 | 709000 | 709000 | 53.3 | 24500 | 11717.2011 |  | 1
85 | 80 | 75 | 79.7527 | 803000 | 246000 | 61.1 | 14000 | 4632.2849 |  | 1
85 | 80 | 72 | 68.6171 | 756000 | 293000 | 59.9 | 14000 | 4632.2849 |  | 1
85 | 80 | 67 | 51.5724 | 715000 | 403000 | 59.9 | 14000 | 4632.2849 |  | 1
85 | 80 | 62 | 36.2232 | 653000 | 486000 | 59.1 | 14000 | 4632.2849 |  | 1
85 | 80 | 57 | 22.3618 | 593000 | 562000 | 58.1 | 14000 | 4632.2849 |  | 1
85 | 80 | 75 | 79.7527 | 832000 | 254000 | 61.9 | 17500 | 6013.8436 |  | 1
85 | 80 | 72 | 68.6171 | 817000 | 344000 | 62.1 | 17500 | 6013.8436 |  | 1
85 | 80 | 67 | 51.5724 | 713000 | 410000 | 58.9 | 17500 | 6013.8436 |  | 1
85 | 80 | 62 | 36.2232 | 668000 | 527000 | 57.8 | 17500 | 6013.8436 |  | 1
85 | 80 | 57 | 22.3618 | 632000 | 623000 | 58.4 | 17500 | 6013.8436 |  | 1
85 | 80 | 75 | 79.7527 | 860000 | 272000 | 62.8 | 21000 | 8501.8994 |  | 1
85 | 80 | 72 | 68.6171 | 819000 | 346000 | 61.7 | 21000 | 8501.8994 |  | 1
85 | 80 | 67 | 51.5724 | 755000 | 468000 | 59.9 | 21000 | 8501.8994 |  | 1
85 | 80 | 62 | 36.2232 | 681000 | 576000 | 58.3 | 21000 | 8501.8994 |  | 1
85 | 80 | 57 | 22.3618 | 670000 | 670000 | 59.6 | 21000 | 8501.8994 |  | 1
85 | 80 | 75 | 79.7527 | 878000 | 287000 | 63.4 | 24500 | 11717.2011 |  | 1
85 | 80 | 72 | 68.6171 | 838000 | 371000 | 62.2 | 24500 | 11717.2011 |  | 1
85 | 80 | 67 | 51.5724 | 773000 | 508000 | 60.4 | 24500 | 11717.2011 |  | 1
85 | 80 | 62 | 36.2232 | 710000 | 639000 | 58.8 | 24500 | 11717.2011 |  | 1
85 | 80 | 57 | 22.3618 | 680000 | 680000 | 58.1 | 24500 | 11717.2011 |  | 1
95 | 80 | 75 | 79.7527 | 759000 | 212000 | 66.4 | 14000 | 4632.2849 |  | 1
95 | 80 | 72 | 68.6171 | 720000 | 266000 | 65.4 | 14000 | 4632.2849 |  | 1
95 | 80 | 67 | 51.5724 | 681000 | 378000 | 65.6 | 14000 | 4632.2849 |  | 1
95 | 80 | 62 | 36.2232 | 623000 | 464000 | 64.8 | 14000 | 4632.2849 |  | 1
95 | 80 | 57 | 22.3618 | 566000 | 540000 | 64.5 | 14000 | 4632.2849 |  | 1
95 | 80 | 75 | 79.7527 | 794000 | 227000 | 67.4 | 17500 | 6013.8436 |  | 1
95 | 80 | 72 | 68.6171 | 755000 | 292000 | 66.4 | 17500 | 6013.8436 |  | 1
95 | 80 | 67 | 51.5724 | 694000 | 399000 | 64.7 | 17500 | 6013.8436 |  | 1
95 | 80 | 62 | 36.2232 | 603000 | 471000 | 62.6 | 17500 | 6013.8436 |  | 1
95 | 80 | 57 | 22.3618 | 606000 | 599000 | 64.9 | 17500 | 6013.8436 |  | 1
95 | 80 | 75 | 79.7527 | 818000 | 242000 | 68.2 | 21000 | 8501.8994 |  | 1
95 | 80 | 72 | 68.6171 | 779000 | 317000 | 67.1 | 21000 | 8501.8994 |  | 1
95 | 80 | 67 | 51.5724 | 717000 | 441000 | 65.4 | 21000 | 8501.8994 |  | 1
95 | 80 | 62 | 36.2232 | 682000 | 585000 | 66 | 21000 | 8501.8994 |  | 1
95 | 80 | 57 | 22.3618 | 641000 | 641000 | 65.6 | 21000 | 8501.8994 |  | 1
95 | 80 | 75 | 79.7527 | 859000 | 282000 | 69.9 | 24500 | 11717.2011 |  | 1
95 | 80 | 72 | 68.6171 | 797000 | 341000 | 67.6 | 24500 | 11717.2011 |  | 1
95 | 80 | 67 | 51.5724 | 734000 | 480000 | 65.9 | 24500 | 11717.2011 |  | 1
95 | 80 | 62 | 36.2232 | 674000 | 611000 | 64.3 | 24500 | 11717.2011 |  | 1
95 | 80 | 57 | 22.3618 | 648000 | 648000 | 63.7 | 24500 | 11717.2011 |  | 1
105 | 80 | 75 | 79.7527 | 718000 | 183000 | 72.6 | 14000 | 4632.2849 |  | 1
105 | 80 | 72 | 68.6171 | 681000 | 238000 | 71.6 | 14000 | 4632.2849 |  | 1
105 | 80 | 67 | 51.5724 | 647000 | 354000 | 72.3 | 14000 | 4632.2849 |  | 1
105 | 80 | 62 | 36.2232 | 590000 | 440000 | 71.5 | 14000 | 4632.2849 |  | 1
105 | 80 | 57 | 22.3618 | 533000 | 508000 | 71.1 | 14000 | 4632.2849 |  | 1
105 | 80 | 75 | 79.7527 | 751000 | 198000 | 73.6 | 17500 | 6013.8436 |  | 1
105 | 80 | 72 | 68.6171 | 714000 | 263000 | 72.6 | 17500 | 6013.8436 |  | 1
105 | 80 | 67 | 51.5724 | 654000 | 371000 | 71 | 17500 | 6013.8436 |  | 1
105 | 80 | 62 | 36.2232 | 621000 | 501000 | 71.9 | 17500 | 6013.8436 |  | 1
105 | 80 | 57 | 22.3618 | 576000 | 576000 | 72.1 | 17500 | 6013.8436 |  | 1
105 | 80 | 75 | 79.7527 | 773000 | 212000 | 74.3 | 21000 | 8501.8994 |  | 1
105 | 80 | 72 | 68.6171 | 736000 | 287000 | 73.2 | 21000 | 8501.8994 |  | 1
105 | 80 | 67 | 51.5724 | 677000 | 412000 | 71.6 | 21000 | 8501.8994 |  | 1
105 | 80 | 62 | 36.2232 | 645000 | 559000 | 72.6 | 21000 | 8501.8994 |  | 1
105 | 80 | 57 | 22.3618 | 610000 | 610000 | 72.3 | 21000 | 8501.8994 |  | 1
105 | 80 | 75 | 79.7527 | 789000 | 226000 | 74.9 | 24500 | 11717.2011 |  | 1
105 | 80 | 72 | 68.6171 | 752000 | 311000 | 73.7 | 24500 | 11717.2011 |  | 1
105 | 80 | 67 | 51.5724 | 692000 | 451000 | 72.1 | 24500 | 11717.2011 |  | 1
105 | 80 | 62 | 36.2232 | 634000 | 582000 | 70.5 | 24500 | 11717.2011 |  | 1
105 | 80 | 57 | 22.3618 | 613000 | 613000 | 70 | 24500 | 11717.2011 |  | 1
115 | 80 | 75 | 79.7527 | 674000 | 154000 | 79.6 | 14000 | 4632.2849 |  | 1
115 | 80 | 72 | 68.6171 | 639000 | 209000 | 78.7 | 14000 | 4632.2849 |  | 1
115 | 80 | 67 | 51.5724 | 611000 | 330000 | 80.2 | 14000 | 4632.2849 |  | 1
115 | 80 | 62 | 36.2232 | 555000 | 415000 | 79.6 | 14000 | 4632.2849 |  | 1
115 | 80 | 57 | 22.3618 | 510000 | 486000 | 80.4 | 14000 | 4632.2849 |  | 1
115 | 80 | 75 | 79.7527 | 704000 | 167000 | 80.5 | 17500 | 6013.8436 |  | 1
115 | 80 | 72 | 68.6171 | 669000 | 233000 | 79.5 | 17500 | 6013.8436 |  | 1
115 | 80 | 67 | 51.5724 | 613000 | 342000 | 78.1 | 17500 | 6013.8436 |  | 1
115 | 80 | 62 | 36.2232 | 581000 | 472000 | 79.8 | 17500 | 6013.8436 |  | 1
115 | 80 | 57 | 22.3618 | 509000 | 485000 | 80 | 17500 | 6013.8436 |  | 1
115 | 80 | 75 | 79.7527 | 724000 | 180000 | 81.2 | 21000 | 8501.8994 |  | 1
115 | 80 | 72 | 68.6171 | 689000 | 256000 | 80.1 | 21000 | 8501.8994 |  | 1
115 | 80 | 67 | 51.5724 | 633000 | 382000 | 78.6 | 21000 | 8501.8994 |  | 1
115 | 80 | 62 | 36.2232 | 607000 | 533000 | 80.3 | 21000 | 8501.8994 |  | 1
115 | 80 | 57 | 22.3618 | 576000 | 576000 | 80.2 | 21000 | 8501.8994 |  | 1
115 | 80 | 75 | 79.7527 | 764000 | 219000 | 83.1 | 24500 | 11717.2011 |  | 1
115 | 80 | 72 | 68.6171 | 704000 | 279000 | 80.6 | 24500 | 11717.2011 |  | 1
115 | 80 | 67 | 51.5724 | 647000 | 421000 | 79 | 24500 | 11717.2011 |  | 1
115 | 80 | 62 | 36.2232 | 622000 | 570000 | 80.7 | 24500 | 11717.2011 |  | 1
115 | 80 | 57 | 22.3618 | 577000 | 577000 | 77.3 | 24500 | 11717.2011 |  | 1
75 | 80 | 75 | 79.7527 | 939000 | 329000 | 59.3 | 28000 | 15747.2682 |  | 1
75 | 80 | 72 | 68.6171 | 893000 | 424000 | 58.1 | 28000 | 15747.2682 |  | 1
75 | 80 | 67 | 51.5724 | 823000 | 575000 | 56.2 | 28000 | 15747.2682 |  | 1
75 | 80 | 62 | 36.2232 | 780000 | 736000 | 55.8 | 28000 | 15747.2682 |  | 1
75 | 80 | 57 | 22.3618 | 736000 | 736000 | 54 | 28000 | 15747.2682 |  | 1
75 | 80 | 75 | 79.7527 | 947000 | 338000 | 59.6 | 30000 | 18470.7933 |  | 1
75 | 80 | 72 | 68.6171 | 900000 | 437000 | 58.3 | 30000 | 18470.7933 |  | 1
75 | 80 | 67 | 51.5724 | 830000 | 596000 | 56.4 | 30000 | 18470.7933 |  | 1
75 | 80 | 62 | 36.2232 | 764000 | 741000 | 54.7 | 30000 | 18470.7933 |  | 1
75 | 80 | 57 | 22.3618 | 773000 | 773000 | 55.8 | 30000 | 18470.7933 |  | 1
85 | 80 | 75 | 79.7527 | 893000 | 302000 | 63.9 | 28000 | 15747.2682 |  | 1
85 | 80 | 72 | 68.6171 | 852000 | 394000 | 62.7 | 28000 | 15747.2682 |  | 1
85 | 80 | 67 | 51.5724 | 787000 | 547000 | 60.9 | 28000 | 15747.2682 |  | 1
85 | 80 | 62 | 36.2232 | 724000 | 685000 | 59.2 | 28000 | 15747.2682 |  | 1
85 | 80 | 57 | 22.3618 | 706000 | 706000 | 58.8 | 28000 | 15747.2682 |  | 1
85 | 80 | 75 | 79.7527 | 900000 | 310000 | 64.1 | 30000 | 18470.7933 |  | 1
85 | 80 | 72 | 68.6171 | 884000 | 433000 | 64 | 30000 | 18470.7933 |  | 1
85 | 80 | 67 | 51.5724 | 817000 | 593000 | 62.2 | 30000 | 18470.7933 |  | 1
85 | 80 | 62 | 36.2232 | 731000 | 703000 | 59.4 | 30000 | 18470.7933 |  | 1
85 | 80 | 57 | 22.3618 | 719000 | 719000 | 59.1 | 30000 | 18470.7933 |  | 1
95 | 80 | 75 | 79.7527 | 849000 | 271000 | 69.2 | 28000 | 15747.2682 |  | 1
95 | 80 | 72 | 68.6171 | 810000 | 365000 | 68 | 28000 | 15747.2682 |  | 1
95 | 80 | 67 | 51.5724 | 747000 | 519000 | 66.3 | 28000 | 15747.2682 |  | 1
95 | 80 | 62 | 36.2232 | 687000 | 649000 | 64.6 | 28000 | 15747.2682 |  | 1
95 | 80 | 57 | 22.3618 | 673000 | 673000 | 64.3 | 28000 | 15747.2682 |  | 1
95 | 80 | 75 | 79.7527 | 854000 | 283000 | 69.4 | 30000 | 18470.7933 |  | 1
95 | 80 | 72 | 68.6171 | 817000 | 373000 | 68.3 | 30000 | 18470.7933 |  | 1
95 | 80 | 67 | 51.5724 | 753000 | 540000 | 66.5 | 30000 | 18470.7933 |  | 1
95 | 80 | 62 | 36.2232 | 696000 | 670000 | 64.9 | 30000 | 18470.7933 |  | 1
95 | 80 | 57 | 22.3618 | 685000 | 685000 | 64.6 | 30000 | 18470.7933 |  | 1
105 | 80 | 75 | 79.7527 | 802000 | 235000 | 75.3 | 28000 | 15747.2682 |  | 1
105 | 80 | 72 | 68.6171 | 764000 | 334000 | 74.1 | 28000 | 15747.2682 |  | 1
105 | 80 | 67 | 51.5724 | 705000 | 489000 | 72.4 | 28000 | 15747.2682 |  | 1
105 | 80 | 62 | 36.2232 | 650000 | 614000 | 70.9 | 28000 | 15747.2682 |  | 1
105 | 80 | 57 | 22.3618 | 637000 | 637000 | 70.6 | 28000 | 15747.2682 |  | 1
105 | 80 | 75 | 79.7527 | 830000 | 280000 | 76.7 | 30000 | 18470.7933 |  | 1
105 | 80 | 72 | 68.6171 | 770000 | 346000 | 74.3 | 30000 | 18470.7933 |  | 1
105 | 80 | 67 | 51.5724 | 710000 | 510000 | 72.6 | 30000 | 18470.7933 |  | 1
105 | 80 | 62 | 36.2232 | 658000 | 634000 | 71.1 | 30000 | 18470.7933 |  | 1
105 | 80 | 57 | 22.3618 | 649000 | 649000 | 70.9 | 30000 | 18470.7933 |  | 1
115 | 80 | 75 | 79.7527 | 750000 | 206000 | 82.1 | 28000 | 15747.2682 |  | 1
115 | 80 | 72 | 68.6171 | 715000 | 301000 | 81 | 28000 | 15747.2682 |  | 1
115 | 80 | 67 | 51.5724 | 658000 | 458000 | 79.3 | 28000 | 15747.2682 |  | 1
115 | 80 | 62 | 36.2232 | 635000 | 605000 | 80.9 | 28000 | 15747.2682 |  | 1
115 | 80 | 57 | 22.3618 | 599000 | 599000 | 77.8 | 28000 | 15747.2682 |  | 1
115 | 80 | 75 | 79.7527 | 787000 | 236000 | 83.9 | 30000 | 18470.7933 |  | 1
115 | 80 | 72 | 68.6171 | 720000 | 314000 | 81.2 | 30000 | 18470.7933 |  | 1
115 | 80 | 67 | 51.5724 | 663000 | 479000 | 79.5 | 30000 | 18470.7933 |  | 1
115 | 80 | 62 | 36.2232 | 617000 | 596000 | 78.2 | 30000 | 18470.7933 |  | 1
115 | 80 | 57 | 22.3618 | 609000 | 609000 | 78 | 30000 | 18470.7933 |  | 1
75 | 80 | 75 | 79.7527 | 871000 | 277000 | 57.3 | 14000 | 4632.2849 |  | 2
75 | 80 | 72 | 68.6171 | 825000 | 330000 | 56.1 | 14000 | 4632.2849 |  | 2
75 | 80 | 67 | 51.5724 | 758000 | 421000 | 54.4 | 14000 | 4632.2849 |  | 2
75 | 80 | 62 | 36.2232 | 693000 | 508000 | 53 | 14000 | 4632.2849 |  | 2
75 | 80 | 57 | 22.3618 | 647000 | 606000 | 52.4 | 14000 | 4632.2849 |  | 2
75 | 80 | 75 | 79.7527 | 913000 | 296000 | 58.6 | 17500 | 6013.8436 |  | 2
75 | 80 | 72 | 68.6171 | 869000 | 363000 | 57.3 | 17500 | 6013.8436 |  | 2
75 | 80 | 67 | 51.5724 | 799000 | 472000 | 55.5 | 17500 | 6013.8436 |  | 2
75 | 80 | 62 | 36.2232 | 726000 | 572000 | 53.5 | 17500 | 6013.8436 |  | 2
75 | 80 | 57 | 22.3618 | 674000 | 660000 | 52.5 | 17500 | 6013.8436 |  | 2
75 | 80 | 75 | 79.7527 | 946000 | 317000 | 59.5 | 21000 | 8501.8994 |  | 2
75 | 80 | 72 | 68.6171 | 896000 | 391000 | 58.1 | 21000 | 8501.8994 |  | 2
75 | 80 | 67 | 51.5724 | 837000 | 530000 | 56.5 | 21000 | 8501.8994 |  | 2
75 | 80 | 62 | 36.2232 | 761000 | 644000 | 54.5 | 21000 | 8501.8994 |  | 2
75 | 80 | 57 | 22.3618 | 717000 | 717000 | 53.5 | 21000 | 8501.8994 |  | 2
75 | 80 | 75 | 79.7527 | 966000 | 333000 | 60.2 | 24500 | 11717.2011 |  | 2
75 | 80 | 72 | 68.6171 | 919000 | 421000 | 58.8 | 24500 | 11717.2011 |  | 2
75 | 80 | 67 | 51.5724 | 847000 | 561000 | 56.8 | 24500 | 11717.2011 |  | 2
75 | 80 | 62 | 36.2232 | 773000 | 697000 | 54.8 | 24500 | 11717.2011 |  | 2
75 | 80 | 57 | 22.3618 | 753000 | 753000 | 54.4 | 24500 | 11717.2011 |  | 2
85 | 80 | 75 | 79.7527 | 836000 | 250000 | 62.1 | 14000 | 4632.2849 |  | 2
85 | 80 | 72 | 68.6171 | 794000 | 306000 | 61 | 14000 | 4632.2849 |  | 2
85 | 80 | 67 | 51.5724 | 741000 | 411000 | 59.7 | 14000 | 4632.2849 |  | 2
85 | 80 | 62 | 36.2232 | 680000 | 502000 | 58.6 | 14000 | 4632.2849 |  | 2
85 | 80 | 57 | 22.3618 | 616000 | 580000 | 57.2 | 14000 | 4632.2849 |  | 2
85 | 80 | 75 | 79.7527 | 876000 | 268000 | 63.3 | 17500 | 6013.8436 |  | 2
85 | 80 | 72 | 68.6171 | 834000 | 336000 | 62.1 | 17500 | 6013.8436 |  | 2
85 | 80 | 67 | 51.5724 | 766000 | 447000 | 60.3 | 17500 | 6013.8436 |  | 2
85 | 80 | 62 | 36.2232 | 717000 | 569000 | 59.3 | 17500 | 6013.8436 |  | 2
85 | 80 | 57 | 22.3618 | 650000 | 636000 | 57.5 | 17500 | 6013.8436 |  | 2
85 | 80 | 75 | 79.7527 | 907000 | 289000 | 64.2 | 21000 | 8501.8994 |  | 2
85 | 80 | 72 | 68.6171 | 866000 | 369000 | 63 | 21000 | 8501.8994 |  | 2
85 | 80 | 67 | 51.5724 | 792000 | 493000 | 61 | 21000 | 8501.8994 |  | 2
85 | 80 | 62 | 36.2232 | 743000 | 633000 | 59.9 | 21000 | 8501.8994 |  | 2
85 | 80 | 57 | 22.3618 | 689000 | 689000 | 58.4 | 21000 | 8501.8994 |  | 2
85 | 80 | 75 | 79.7527 | 923000 | 302000 | 64.8 | 24500 | 11717.2011 |  | 2
85 | 80 | 72 | 68.6171 | 880000 | 392000 | 63.5 | 24500 | 11717.2011 |  | 2
85 | 80 | 67 | 51.5724 | 812000 | 539000 | 61.6 | 24500 | 11717.2011 |  | 2
85 | 80 | 62 | 36.2232 | 747000 | 677000 | 59.9 | 24500 | 11717.2011 |  | 2
85 | 80 | 57 | 22.3618 | 741000 | 741000 | 60 | 24500 | 11717.2011 |  | 2
95 | 80 | 75 | 79.7527 | 798000 | 222000 | 67.7 | 14000 | 4632.2849 |  | 2
95 | 80 | 72 | 68.6171 | 769000 | 291000 | 67 | 14000 | 4632.2849 |  | 2
95 | 80 | 67 | 51.5724 | 708000 | 387000 | 65.6 | 14000 | 4632.2849 |  | 2
95 | 80 | 62 | 36.2232 | 649000 | 480000 | 64.6 | 14000 | 4632.2849 |  | 2
95 | 80 | 57 | 22.3618 | 592000 | 559000 | 64 | 14000 | 4632.2849 |  | 2
95 | 80 | 75 | 79.7527 | 836000 | 238000 | 68.9 | 17500 | 6013.8436 |  | 2
95 | 80 | 72 | 68.6171 | 804000 | 317000 | 68 | 17500 | 6013.8436 |  | 2
95 | 80 | 67 | 51.5724 | 729000 | 420000 | 65.9 | 17500 | 6013.8436 |  | 2
95 | 80 | 62 | 36.2232 | 684000 | 546000 | 65.1 | 17500 | 6013.8436 |  | 2
95 | 80 | 57 | 22.3618 | 619000 | 607000 | 63.3 | 17500 | 6013.8436 |  | 2
95 | 80 | 75 | 79.7527 | 861000 | 255000 | 69.7 | 21000 | 8501.8994 |  | 2
95 | 80 | 72 | 68.6171 | 820000 | 334000 | 68.4 | 21000 | 8501.8994 |  | 2
95 | 80 | 67 | 51.5724 | 765000 | 477000 | 67 | 21000 | 8501.8994 |  | 2
95 | 80 | 62 | 36.2232 | 706000 | 606000 | 65.5 | 21000 | 8501.8994 |  | 2
95 | 80 | 57 | 22.3618 | 657000 | 657000 | 64.1 | 21000 | 8501.8994 |  | 2
95 | 80 | 75 | 79.7527 | 880000 | 271000 | 70.3 | 24500 | 11717.2011 |  | 2
95 | 80 | 72 | 68.6171 | 842000 | 365000 | 69.1 | 24500 | 11717.2011 |  | 2
95 | 80 | 67 | 51.5724 | 782000 | 520000 | 67.4 | 24500 | 11717.2011 |  | 2
95 | 80 | 62 | 36.2232 | 711000 | 647000 | 65.5 | 24500 | 11717.2011 |  | 2
95 | 80 | 57 | 22.3618 | 708000 | 708000 | 65.7 | 24500 | 11717.2011 |  | 2
105 | 80 | 75 | 79.7527 | 756000 | 192000 | 74.2 | 14000 | 4632.2849 |  | 2
105 | 80 | 72 | 68.6171 | 729000 | 263000 | 73.5 | 14000 | 4632.2849 |  | 2
105 | 80 | 67 | 51.5724 | 671000 | 362000 | 72.6 | 14000 | 4632.2849 |  | 2
105 | 80 | 62 | 36.2232 | 615000 | 456000 | 72.1 | 14000 | 4632.2849 |  | 2
105 | 80 | 57 | 22.3618 | 565000 | 533000 | 72 | 14000 | 4632.2849 |  | 2
105 | 80 | 75 | 79.7527 | 798000 | 214000 | 75.4 | 17500 | 6013.8436 |  | 2
105 | 80 | 72 | 68.6171 | 752000 | 277000 | 74.1 | 17500 | 6013.8436 |  | 2
105 | 80 | 67 | 51.5724 | 702000 | 405000 | 73 | 17500 | 6013.8436 |  | 2
105 | 80 | 62 | 36.2232 | 647000 | 519000 | 72.3 | 17500 | 6013.8436 |  | 2
105 | 80 | 57 | 22.3618 | 586000 | 576000 | 70.7 | 17500 | 6013.8436 |  | 2
105 | 80 | 75 | 79.7527 | 818000 | 226000 | 76.1 | 21000 | 8501.8994 |  | 2
105 | 80 | 72 | 68.6171 | 776000 | 304000 | 74.8 | 21000 | 8501.8994 |  | 2
105 | 80 | 67 | 51.5724 | 724000 | 448000 | 73.4 | 21000 | 8501.8994 |  | 2
105 | 80 | 62 | 36.2232 | 670000 | 580000 | 72.5 | 21000 | 8501.8994 |  | 2
105 | 80 | 57 | 22.3618 | 623000 | 623000 | 71.3 | 21000 | 8501.8994 |  | 2
105 | 80 | 75 | 79.7527 | 833000 | 239000 | 76.6 | 24500 | 11717.2011 |  | 2
105 | 80 | 72 | 68.6171 | 796000 | 333000 | 75.4 | 24500 | 11717.2011 |  | 2
105 | 80 | 67 | 51.5724 | 739000 | 490000 | 73.8 | 24500 | 11717.2011 |  | 2
105 | 80 | 62 | 36.2232 | 671000 | 610000 | 72 | 24500 | 11717.2011 |  | 2
105 | 80 | 57 | 22.3618 | 674000 | 674000 | 72.7 | 24500 | 11717.2011 |  | 2
115 | 80 | 75 | 79.7527 | 711000 | 162000 | 82 | 14000 | 4632.2849 |  | 2
115 | 80 | 72 | 68.6171 | 688000 | 235000 | 81.7 | 14000 | 4632.2849 |  | 2
115 | 80 | 67 | 51.5724 | 631000 | 334000 | 81 | 14000 | 4632.2849 |  | 2
115 | 80 | 62 | 36.2232 | 578000 | 429000 | 81 | 14000 | 4632.2849 |  | 2
115 | 80 | 57 | 22.3618 | 533000 | 504000 | 81.3 | 14000 | 4632.2849 |  | 2
115 | 80 | 75 | 79.7527 | 750000 | 183000 | 83 | 17500 | 6013.8436 |  | 2
115 | 80 | 72 | 68.6171 | 706000 | 247000 | 81.8 | 17500 | 6013.8436 |  | 2
115 | 80 | 67 | 51.5724 | 646000 | 362000 | 80.6 | 17500 | 6013.8436 |  | 2
115 | 80 | 62 | 36.2232 | 607000 | 492000 | 80.9 | 17500 | 6013.8436 |  | 2
115 | 80 | 57 | 22.3618 | 574000 | 568000 | 80.9 | 17500 | 6013.8436 |  | 2
115 | 80 | 75 | 79.7527 | 770000 | 194000 | 83.6 | 21000 | 8501.8994 |  | 2
115 | 80 | 72 | 68.6171 | 728000 | 272000 | 82.4 | 21000 | 8501.8994 |  | 2
115 | 80 | 67 | 51.5724 | 680000 | 418000 | 81.4 | 21000 | 8501.8994 |  | 2
115 | 80 | 62 | 36.2232 | 629000 | 551000 | 81 | 21000 | 8501.8994 |  | 2
115 | 80 | 57 | 22.3618 | 586000 | 586000 | 79.8 | 21000 | 8501.8994 |  | 2
115 | 80 | 75 | 79.7527 | 781000 | 205000 | 84 | 24500 | 11717.2011 |  | 2
115 | 80 | 72 | 68.6171 | 744000 | 297000 | 82.8 | 24500 | 11717.2011 |  | 2
115 | 80 | 67 | 51.5724 | 694000 | 460000 | 81.7 | 24500 | 11717.2011 |  | 2
115 | 80 | 62 | 36.2232 | 631000 | 573000 | 80.1 | 24500 | 11717.2011 |  | 2
115 | 80 | 57 | 22.3618 | 635000 | 635000 | 81 | 24500 | 11717.2011 |  | 2
75 | 80 | 75 | 79.7527 | 983000 | 351000 | 60.7 | 28000 | 15747.2682 |  | 2
75 | 80 | 72 | 68.6171 | 936000 | 449000 | 59.4 | 28000 | 15747.2682 |  | 2
75 | 80 | 67 | 51.5724 | 862000 | 611000 | 57.3 | 28000 | 15747.2682 |  | 2
75 | 80 | 62 | 36.2232 | 796000 | 755000 | 55.5 | 28000 | 15747.2682 |  | 2
75 | 80 | 57 | 22.3618 | 783000 | 783000 | 55.2 | 28000 | 15747.2682 |  | 2
75 | 80 | 75 | 79.7527 | 990000 | 360000 | 60.9 | 30000 | 18470.7933 |  | 2
75 | 80 | 72 | 68.6171 | 944000 | 465000 | 59.6 | 30000 | 18470.7933 |  | 2
75 | 80 | 67 | 51.5724 | 869000 | 636000 | 57.5 | 30000 | 18470.7933 |  | 2
75 | 80 | 62 | 36.2232 | 806000 | 777000 | 55.8 | 30000 | 18470.7933 |  | 2
75 | 80 | 57 | 22.3618 | 797000 | 797000 | 55.6 | 30000 | 18470.7933 |  | 2
85 | 80 | 75 | 79.7527 | 939000 | 320000 | 65.4 | 28000 | 15747.2682 |  | 2
85 | 80 | 72 | 68.6171 | 898000 | 422000 | 64.1 | 28000 | 15747.2682 |  | 2
85 | 80 | 67 | 51.5724 | 826000 | 583000 | 62 | 28000 | 15747.2682 |  | 2
85 | 80 | 62 | 36.2232 | 764000 | 721000 | 60.3 | 28000 | 15747.2682 |  | 2
85 | 80 | 57 | 22.3618 | 768000 | 768000 | 60.6 | 28000 | 15747.2682 |  | 2
85 | 80 | 75 | 79.7527 | 974000 | 369000 | 69.7 | 30000 | 18470.7933 |  | 2
85 | 80 | 72 | 68.6171 | 902000 | 434000 | 64.2 | 30000 | 18470.7933 |  | 2
85 | 80 | 67 | 51.5724 | 840000 | 615000 | 62.4 | 30000 | 18470.7933 |  | 2
85 | 80 | 62 | 36.2232 | 790000 | 762000 | 61.2 | 30000 | 18470.7933 |  | 2
85 | 80 | 57 | 22.3618 | 761000 | 761000 | 60.1 | 30000 | 18470.7933 |  | 2
95 | 80 | 75 | 79.7527 | 895000 | 289000 | 70.8 | 28000 | 15747.2682 |  | 2
95 | 80 | 72 | 68.6171 | 852000 | 388000 | 69.5 | 28000 | 15747.2682 |  | 2
95 | 80 | 67 | 51.5724 | 786000 | 554000 | 67.6 | 28000 | 15747.2682 |  | 2
95 | 80 | 62 | 36.2232 | 747000 | 706000 | 66.7 | 28000 | 15747.2682 |  | 2
95 | 80 | 57 | 22.3618 | 733000 | 733000 | 66.3 | 28000 | 15747.2682 |  | 2
95 | 80 | 75 | 79.7527 | 932000 | 346000 | 75.8 | 30000 | 18470.7933 |  | 2
95 | 80 | 72 | 68.6171 | 856000 | 395000 | 69.6 | 30000 | 18470.7933 |  | 2
95 | 80 | 67 | 51.5724 | 800000 | 586000 | 68 | 30000 | 18470.7933 |  | 2
95 | 80 | 62 | 36.2232 | 755000 | 729000 | 66.9 | 30000 | 18470.7933 |  | 2
95 | 80 | 57 | 22.3618 | 747000 | 747000 | 66.7 | 30000 | 18470.7933 |  | 2
105 | 80 | 75 | 79.7527 | 846000 | 251000 | 77 | 28000 | 15747.2682 |  | 2
105 | 80 | 72 | 68.6171 | 806000 | 356000 | 75.8 | 28000 | 15747.2682 |  | 2
105 | 80 | 67 | 51.5724 | 750000 | 532000 | 74.2 | 28000 | 15747.2682 |  | 2
105 | 80 | 62 | 36.2232 | 709000 | 671000 | 73.2 | 28000 | 15747.2682 |  | 2
105 | 80 | 57 | 22.3618 | 697000 | 697000 | 73 | 28000 | 15747.2682 |  | 2
105 | 80 | 75 | 79.7527 | 850000 | 273000 | 77.2 | 30000 | 18470.7933 |  | 2
105 | 80 | 72 | 68.6171 | 812000 | 371000 | 76 | 30000 | 18470.7933 |  | 2
105 | 80 | 67 | 51.5724 | 755000 | 555000 | 74.4 | 30000 | 18470.7933 |  | 2
105 | 80 | 62 | 36.2232 | 717000 | 693000 | 73.4 | 30000 | 18470.7933 |  | 2
105 | 80 | 57 | 22.3618 | 709000 | 709000 | 73.2 | 30000 | 18470.7933 |  | 2
115 | 80 | 75 | 79.7527 | 794000 | 220000 | 84.4 | 28000 | 15747.2682 |  | 2
115 | 80 | 72 | 68.6171 | 755000 | 323000 | 83.2 | 28000 | 15747.2682 |  | 2
115 | 80 | 67 | 51.5724 | 704000 | 500000 | 81.9 | 28000 | 15747.2682 |  | 2
115 | 80 | 62 | 36.2232 | 668000 | 634000 | 81.3 | 28000 | 15747.2682 |  | 2
115 | 80 | 57 | 22.3618 | 658000 | 658000 | 81.2 | 28000 | 15747.2682 |  | 2
115 | 80 | 75 | 79.7527 | 802000 | 222000 | 84.6 | 30000 | 18470.7933 |  | 2
115 | 80 | 72 | 68.6171 | 761000 | 338000 | 83.4 | 30000 | 18470.7933 |  | 2
115 | 80 | 67 | 51.5724 | 708000 | 523000 | 82 | 30000 | 18470.7933 |  | 2
115 | 80 | 62 | 36.2232 | 676000 | 656000 | 81.4 | 30000 | 18470.7933 |  | 2
115 | 80 | 57 | 22.3618 | 669000 | 669000 | 81.4 | 30000 | 18470.7933 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 17
Degradation Coefficient (C_d) |  | 48/50 090 (90 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 1075000 | 396000 | 61.1 | 18000 | 5757.5363 |  | 1
75 | 80 | 72 | 68.6171 | 1017000 | 454000 | 60.1 | 18000 | 5757.5363 |  | 1
75 | 80 | 67 | 51.5724 | 922000 | 541000 | 58.5 | 18000 | 5757.5363 |  | 1
75 | 80 | 62 | 36.2232 | 863000 | 656000 | 58.1 | 18000 | 5757.5363 |  | 1
75 | 80 | 57 | 22.3618 | 788000 | 744000 | 57.2 | 18000 | 5757.5363 |  | 1
75 | 80 | 75 | 79.7527 | 1154000 | 450000 | 62.8 | 22500 | 9252.067 |  | 1
75 | 80 | 72 | 68.6171 | 1072000 | 493000 | 61.1 | 22500 | 9252.067 |  | 1
75 | 80 | 67 | 51.5724 | 1003000 | 629000 | 60.3 | 22500 | 9252.067 |  | 1
75 | 80 | 62 | 36.2232 | 915000 | 736000 | 58.8 | 22500 | 9252.067 |  | 1
75 | 80 | 57 | 22.3618 | 836000 | 819000 | 57.7 | 22500 | 9252.067 |  | 1
75 | 80 | 75 | 79.7527 | 1171000 | 452000 | 63 | 27000 | 14142.743 |  | 1
75 | 80 | 72 | 68.6171 | 1135000 | 553000 | 62.5 | 27000 | 14142.743 |  | 1
75 | 80 | 67 | 51.5724 | 1017000 | 658000 | 60.2 | 27000 | 14142.743 |  | 1
75 | 80 | 62 | 36.2232 | 925000 | 782000 | 58.6 | 27000 | 14142.743 |  | 1
75 | 80 | 57 | 22.3618 | 883000 | 883000 | 58.4 | 27000 | 14142.743 |  | 1
75 | 80 | 75 | 79.7527 | 1201000 | 475000 | 63.6 | 31500 | 20679.6201 |  | 1
75 | 80 | 72 | 68.6171 | 1142000 | 563000 | 62.4 | 31500 | 20679.6201 |  | 1
75 | 80 | 67 | 51.5724 | 1045000 | 707000 | 60.7 | 31500 | 20679.6201 |  | 1
75 | 80 | 62 | 36.2232 | 952000 | 846000 | 59.1 | 31500 | 20679.6201 |  | 1
75 | 80 | 57 | 22.3618 | 923000 | 923000 | 59 | 31500 | 20679.6201 |  | 1
85 | 80 | 75 | 79.7527 | 1052000 | 387000 | 68.2 | 18000 | 5757.5363 |  | 1
85 | 80 | 72 | 68.6171 | 964000 | 413000 | 66.3 | 18000 | 5757.5363 |  | 1
85 | 80 | 67 | 51.5724 | 884000 | 513000 | 64.9 | 18000 | 5757.5363 |  | 1
85 | 80 | 62 | 36.2232 | 828000 | 629000 | 64.9 | 18000 | 5757.5363 |  | 1
85 | 80 | 57 | 22.3618 | 752000 | 712000 | 64 | 18000 | 5757.5363 |  | 1
85 | 80 | 75 | 79.7527 | 1080000 | 391000 | 68.5 | 22500 | 9252.067 |  | 1
85 | 80 | 72 | 68.6171 | 1013000 | 449000 | 67.3 | 22500 | 9252.067 |  | 1
85 | 80 | 67 | 51.5724 | 933000 | 570000 | 65.8 | 22500 | 9252.067 |  | 1
85 | 80 | 62 | 36.2232 | 876000 | 707000 | 65.5 | 22500 | 9252.067 |  | 1
85 | 80 | 57 | 22.3618 | 807000 | 791000 | 64.6 | 22500 | 9252.067 |  | 1
85 | 80 | 75 | 79.7527 | 1117000 | 414000 | 69.2 | 27000 | 14142.743 |  | 1
85 | 80 | 72 | 68.6171 | 1083000 | 516000 | 68.8 | 27000 | 14142.743 |  | 1
85 | 80 | 67 | 51.5724 | 995000 | 649000 | 67.3 | 27000 | 14142.743 |  | 1
85 | 80 | 62 | 36.2232 | 910000 | 778000 | 65.9 | 27000 | 14142.743 |  | 1
85 | 80 | 57 | 22.3618 | 844000 | 844000 | 65.1 | 27000 | 14142.743 |  | 1
85 | 80 | 75 | 79.7527 | 1144000 | 436000 | 69.8 | 31500 | 20679.6201 |  | 1
85 | 80 | 72 | 68.6171 | 1088000 | 525000 | 68.7 | 31500 | 20679.6201 |  | 1
85 | 80 | 67 | 51.5724 | 996000 | 673000 | 67 | 31500 | 20679.6201 |  | 1
85 | 80 | 62 | 36.2232 | 935000 | 841000 | 66.4 | 31500 | 20679.6201 |  | 1
85 | 80 | 57 | 22.3618 | 887000 | 887000 | 65.7 | 31500 | 20679.6201 |  | 1
95 | 80 | 75 | 79.7527 | 977000 | 327000 | 74.7 | 18000 | 5757.5363 |  | 1
95 | 80 | 72 | 68.6171 | 950000 | 413000 | 74.6 | 18000 | 5757.5363 |  | 1
95 | 80 | 67 | 51.5724 | 868000 | 508000 | 73.6 | 18000 | 5757.5363 |  | 1
95 | 80 | 62 | 36.2232 | 790000 | 600000 | 72.8 | 18000 | 5757.5363 |  | 1
95 | 80 | 57 | 22.3618 | 718000 | 686000 | 71.9 | 18000 | 5757.5363 |  | 1
95 | 80 | 75 | 79.7527 | 1026000 | 354000 | 75.7 | 22500 | 9252.067 |  | 1
95 | 80 | 72 | 68.6171 | 972000 | 423000 | 74.6 | 22500 | 9252.067 |  | 1
95 | 80 | 67 | 51.5724 | 914000 | 564000 | 74.1 | 22500 | 9252.067 |  | 1
95 | 80 | 62 | 36.2232 | 835000 | 677000 | 73.3 | 22500 | 9252.067 |  | 1
95 | 80 | 57 | 22.3618 | 771000 | 756000 | 72.4 | 22500 | 9252.067 |  | 1
95 | 80 | 75 | 79.7527 | 1080000 | 396000 | 77 | 27000 | 14142.743 |  | 1
95 | 80 | 72 | 68.6171 | 1006000 | 456000 | 75.3 | 27000 | 14142.743 |  | 1
95 | 80 | 67 | 51.5724 | 946000 | 615000 | 74.6 | 27000 | 14142.743 |  | 1
95 | 80 | 62 | 36.2232 | 866000 | 746000 | 73.6 | 27000 | 14142.743 |  | 1
95 | 80 | 57 | 22.3618 | 808000 | 808000 | 73 | 27000 | 14142.743 |  | 1
95 | 80 | 75 | 79.7527 | 1086000 | 396000 | 77 | 31500 | 20679.6201 |  | 1
95 | 80 | 72 | 68.6171 | 1053000 | 508000 | 76.5 | 31500 | 20679.6201 |  | 1
95 | 80 | 67 | 51.5724 | 944000 | 637000 | 74.2 | 31500 | 20679.6201 |  | 1
95 | 80 | 62 | 36.2232 | 890000 | 807000 | 73.9 | 31500 | 20679.6201 |  | 1
95 | 80 | 57 | 22.3618 | 849000 | 849000 | 73.5 | 31500 | 20679.6201 |  | 1
105 | 80 | 75 | 79.7527 | 924000 | 291000 | 83 | 18000 | 5757.5363 |  | 1
105 | 80 | 72 | 68.6171 | 839000 | 315000 | 81.6 | 18000 | 5757.5363 |  | 1
105 | 80 | 67 | 51.5724 | 823000 | 476000 | 82.5 | 18000 | 5757.5363 |  | 1
105 | 80 | 62 | 36.2232 | 750000 | 570000 | 81.9 | 18000 | 5757.5363 |  | 1
105 | 80 | 57 | 22.3618 | 689000 | 656000 | 81.1 | 18000 | 5757.5363 |  | 1
105 | 80 | 75 | 79.7527 | 991000 | 337000 | 84.5 | 22500 | 9252.067 |  | 1
105 | 80 | 72 | 68.6171 | 943000 | 410000 | 83.8 | 22500 | 9252.067 |  | 1
105 | 80 | 67 | 51.5724 | 865000 | 529000 | 82.9 | 22500 | 9252.067 |  | 1
105 | 80 | 62 | 36.2232 | 790000 | 645000 | 82.2 | 22500 | 9252.067 |  | 1
105 | 80 | 57 | 22.3618 | 734000 | 721000 | 81.5 | 22500 | 9252.067 |  | 1
105 | 80 | 75 | 79.7527 | 1000000 | 336000 | 84.5 | 27000 | 14142.743 |  | 1
105 | 80 | 72 | 68.6171 | 972000 | 440000 | 84.2 | 27000 | 14142.743 |  | 1
105 | 80 | 67 | 51.5724 | 894000 | 579000 | 83.3 | 27000 | 14142.743 |  | 1
105 | 80 | 62 | 36.2232 | 819000 | 712000 | 82.5 | 27000 | 14142.743 |  | 1
105 | 80 | 57 | 22.3618 | 770000 | 770000 | 82 | 27000 | 14142.743 |  | 1
105 | 80 | 75 | 79.7527 | 1041000 | 372000 | 85.6 | 31500 | 20679.6201 |  | 1
105 | 80 | 72 | 68.6171 | 993000 | 468000 | 84.6 | 31500 | 20679.6201 |  | 1
105 | 80 | 67 | 51.5724 | 916000 | 625000 | 83.5 | 31500 | 20679.6201 |  | 1
105 | 80 | 62 | 36.2232 | 843000 | 773000 | 82.8 | 31500 | 20679.6201 |  | 1
105 | 80 | 57 | 22.3618 | 807000 | 807000 | 82.4 | 31500 | 20679.6201 |  | 1
115 | 80 | 75 | 79.7527 | 868000 | 253000 | 92.8 | 18000 | 5757.5363 |  | 1
115 | 80 | 72 | 68.6171 | 848000 | 342000 | 93.3 | 18000 | 5757.5363 |  | 1
115 | 80 | 67 | 51.5724 | 774000 | 442000 | 92.8 | 18000 | 5757.5363 |  | 1
115 | 80 | 62 | 36.2232 | 708000 | 544000 | 92.4 | 18000 | 5757.5363 |  | 1
115 | 80 | 57 | 22.3618 | 648000 | 617000 | 91.8 | 18000 | 5757.5363 |  | 1
115 | 80 | 75 | 79.7527 | 931000 | 297000 | 94.2 | 22500 | 9252.067 |  | 1
115 | 80 | 72 | 68.6171 | 886000 | 371000 | 93.7 | 22500 | 9252.067 |  | 1
115 | 80 | 67 | 51.5724 | 812000 | 493000 | 93 | 22500 | 9252.067 |  | 1
115 | 80 | 62 | 36.2232 | 742000 | 611000 | 92.6 | 22500 | 9252.067 |  | 1
115 | 80 | 57 | 22.3618 | 694000 | 682000 | 92 | 22500 | 9252.067 |  | 1
115 | 80 | 75 | 79.7527 | 956000 | 313000 | 94.5 | 27000 | 14142.743 |  | 1
115 | 80 | 72 | 68.6171 | 912000 | 399000 | 94 | 27000 | 14142.743 |  | 1
115 | 80 | 67 | 51.5724 | 838000 | 540000 | 93.3 | 27000 | 14142.743 |  | 1
115 | 80 | 62 | 36.2232 | 769000 | 675000 | 92.7 | 27000 | 14142.743 |  | 1
115 | 80 | 57 | 22.3618 | 728000 | 728000 | 92.5 | 27000 | 14142.743 |  | 1
115 | 80 | 75 | 79.7527 | 974000 | 329000 | 94.8 | 31500 | 20679.6201 |  | 1
115 | 80 | 72 | 68.6171 | 930000 | 426000 | 94.2 | 31500 | 20679.6201 |  | 1
115 | 80 | 67 | 51.5724 | 858000 | 586000 | 93.4 | 31500 | 20679.6201 |  | 1
115 | 80 | 62 | 36.2232 | 790000 | 728000 | 92.9 | 31500 | 20679.6201 |  | 1
115 | 80 | 57 | 22.3618 | 762000 | 762000 | 92.7 | 31500 | 20679.6201 |  | 1
75 | 80 | 75 | 79.7527 | 1209000 | 481000 | 63.8 | 36000 | 25095.1899 |  | 1
75 | 80 | 72 | 68.6171 | 1164000 | 594000 | 62.9 | 36000 | 25095.1899 |  | 1
75 | 80 | 67 | 51.5724 | 1068000 | 757000 | 61.2 | 36000 | 25095.1899 |  | 1
75 | 80 | 62 | 36.2232 | 972000 | 903000 | 59.5 | 36000 | 25095.1899 |  | 1
75 | 80 | 57 | 22.3618 | 932000 | 932000 | 58.7 | 36000 | 25095.1899 |  | 1
85 | 80 | 75 | 79.7527 | 1165000 | 456000 | 70.2 | 36000 | 25095.1899 |  | 1
85 | 80 | 72 | 68.6171 | 1109000 | 555000 | 69.1 | 36000 | 25095.1899 |  | 1
85 | 80 | 67 | 51.5724 | 1041000 | 745000 | 68.1 | 36000 | 25095.1899 |  | 1
85 | 80 | 62 | 36.2232 | 929000 | 869000 | 65.8 | 36000 | 25095.1899 |  | 1
85 | 80 | 57 | 22.3618 | 923000 | 923000 | 66.2 | 36000 | 25095.1899 |  | 1
95 | 80 | 75 | 79.7527 | 1105000 | 415000 | 77.4 | 36000 | 25095.1899 |  | 1
95 | 80 | 72 | 68.6171 | 1051000 | 516000 | 76.3 | 36000 | 25095.1899 |  | 1
95 | 80 | 67 | 51.5724 | 963000 | 683000 | 74.6 | 36000 | 25095.1899 |  | 1
95 | 80 | 62 | 36.2232 | 908000 | 863000 | 74.2 | 36000 | 25095.1899 |  | 1
95 | 80 | 57 | 22.3618 | 882000 | 882000 | 73.9 | 36000 | 25095.1899 |  | 1
105 | 80 | 75 | 79.7527 | 1041000 | 373000 | 85.5 | 36000 | 25095.1899 |  | 1
105 | 80 | 72 | 68.6171 | 990000 | 475000 | 84.4 | 36000 | 25095.1899 |  | 1
105 | 80 | 67 | 51.5724 | 932000 | 669000 | 83.8 | 36000 | 25095.1899 |  | 1
105 | 80 | 62 | 36.2232 | 860000 | 815000 | 82.9 | 36000 | 25095.1899 |  | 1
105 | 80 | 57 | 22.3618 | 838000 | 838000 | 82.7 | 36000 | 25095.1899 |  | 1
115 | 80 | 75 | 79.7527 | 973000 | 329000 | 94.6 | 36000 | 25095.1899 |  | 1
115 | 80 | 72 | 68.6171 | 926000 | 433000 | 93.8 | 36000 | 25095.1899 |  | 1
115 | 80 | 67 | 51.5724 | 872000 | 629000 | 93.6 | 36000 | 25095.1899 |  | 1
115 | 80 | 62 | 36.2232 | 810000 | 767000 | 93 | 36000 | 25095.1899 |  | 1
115 | 80 | 57 | 22.3618 | 791000 | 791000 | 92.9 | 36000 | 25095.1899 |  | 1
75 | 80 | 75 | 79.7527 | 1134000 | 398000 | 62.5 | 18000 | 5757.5363 |  | 2
75 | 80 | 72 | 68.6171 | 1074000 | 462000 | 61.4 | 18000 | 5757.5363 |  | 2
75 | 80 | 67 | 51.5724 | 981000 | 566000 | 59.7 | 18000 | 5757.5363 |  | 2
75 | 80 | 62 | 36.2232 | 894000 | 668000 | 58.3 | 18000 | 5757.5363 |  | 2
75 | 80 | 57 | 22.3618 | 822000 | 773000 | 57.4 | 18000 | 5757.5363 |  | 2
75 | 80 | 75 | 79.7527 | 1191000 | 425000 | 63.6 | 22500 | 9252.067 |  | 2
75 | 80 | 72 | 68.6171 | 1131000 | 503000 | 62.5 | 22500 | 9252.067 |  | 2
75 | 80 | 67 | 51.5724 | 1036000 | 630000 | 60.7 | 22500 | 9252.067 |  | 2
75 | 80 | 62 | 36.2232 | 948000 | 755000 | 59.2 | 22500 | 9252.067 |  | 2
75 | 80 | 57 | 22.3618 | 878000 | 859000 | 57.9 | 22500 | 9252.067 |  | 2
75 | 80 | 75 | 79.7527 | 1230000 | 450000 | 64.5 | 27000 | 14142.743 |  | 2
75 | 80 | 72 | 68.6171 | 1170000 | 540000 | 63.3 | 27000 | 14142.743 |  | 2
75 | 80 | 67 | 51.5724 | 1075000 | 690000 | 61.5 | 27000 | 14142.743 |  | 2
75 | 80 | 62 | 36.2232 | 985000 | 837000 | 59.9 | 27000 | 14142.743 |  | 2
75 | 80 | 57 | 22.3618 | 932000 | 932000 | 58.9 | 27000 | 14142.743 |  | 2
75 | 80 | 75 | 79.7527 | 1259000 | 474000 | 65.1 | 31500 | 20679.6201 |  | 2
75 | 80 | 72 | 68.6171 | 1198000 | 577000 | 63.9 | 31500 | 20679.6201 |  | 2
75 | 80 | 67 | 51.5724 | 1103000 | 748000 | 62 | 31500 | 20679.6201 |  | 2
75 | 80 | 62 | 36.2232 | 1014000 | 911000 | 60.4 | 31500 | 20679.6201 |  | 2
75 | 80 | 57 | 22.3618 | 974000 | 974000 | 59.7 | 31500 | 20679.6201 |  | 2
85 | 80 | 75 | 79.7527 | 1080000 | 358000 | 68.8 | 18000 | 5757.5363 |  | 2
85 | 80 | 72 | 68.6171 | 1023000 | 424000 | 67.7 | 18000 | 5757.5363 |  | 2
85 | 80 | 67 | 51.5724 | 935000 | 531000 | 66.2 | 18000 | 5757.5363 |  | 2
85 | 80 | 62 | 36.2232 | 853000 | 636000 | 65.3 | 18000 | 5757.5363 |  | 2
85 | 80 | 57 | 22.3618 | 781000 | 736000 | 64.5 | 18000 | 5757.5363 |  | 2
85 | 80 | 75 | 79.7527 | 1133000 | 383000 | 69.9 | 22500 | 9252.067 |  | 2
85 | 80 | 72 | 68.6171 | 1076000 | 462000 | 68.8 | 22500 | 9252.067 |  | 2
85 | 80 | 67 | 51.5724 | 985000 | 592000 | 67.1 | 22500 | 9252.067 |  | 2
85 | 80 | 62 | 36.2232 | 902000 | 721000 | 65.8 | 22500 | 9252.067 |  | 2
85 | 80 | 57 | 22.3618 | 843000 | 826000 | 64.9 | 22500 | 9252.067 |  | 2
85 | 80 | 75 | 79.7527 | 1169000 | 406000 | 70.7 | 27000 | 14142.743 |  | 2
85 | 80 | 72 | 68.6171 | 1111000 | 498000 | 69.5 | 27000 | 14142.743 |  | 2
85 | 80 | 67 | 51.5724 | 1021000 | 650000 | 67.8 | 27000 | 14142.743 |  | 2
85 | 80 | 62 | 36.2232 | 937000 | 800000 | 66.2 | 27000 | 14142.743 |  | 2
85 | 80 | 57 | 22.3618 | 886000 | 886000 | 65.6 | 27000 | 14142.743 |  | 2
85 | 80 | 75 | 79.7527 | 1196000 | 429000 | 71.3 | 31500 | 20679.6201 |  | 2
85 | 80 | 72 | 68.6171 | 1138000 | 533000 | 70.1 | 31500 | 20679.6201 |  | 2
85 | 80 | 67 | 51.5724 | 1046000 | 706000 | 68.3 | 31500 | 20679.6201 |  | 2
85 | 80 | 62 | 36.2232 | 964000 | 872000 | 66.7 | 31500 | 20679.6201 |  | 2
85 | 80 | 57 | 22.3618 | 930000 | 930000 | 66.1 | 31500 | 20679.6201 |  | 2
95 | 80 | 75 | 79.7527 | 1025000 | 318000 | 76.1 | 18000 | 5757.5363 |  | 2
95 | 80 | 72 | 68.6171 | 970000 | 386000 | 75.2 | 18000 | 5757.5363 |  | 2
95 | 80 | 67 | 51.5724 | 887000 | 495000 | 74.2 | 18000 | 5757.5363 |  | 2
95 | 80 | 62 | 36.2232 | 810000 | 603000 | 73.6 | 18000 | 5757.5363 |  | 2
95 | 80 | 57 | 22.3618 | 743000 | 702000 | 73 | 18000 | 5757.5363 |  | 2
95 | 80 | 75 | 79.7527 | 1072000 | 340000 | 77.1 | 22500 | 9252.067 |  | 2
95 | 80 | 72 | 68.6171 | 1018000 | 420000 | 76 | 22500 | 9252.067 |  | 2
95 | 80 | 67 | 51.5724 | 933000 | 554000 | 74.7 | 22500 | 9252.067 |  | 2
95 | 80 | 62 | 36.2232 | 855000 | 685000 | 73.9 | 22500 | 9252.067 |  | 2
95 | 80 | 57 | 22.3618 | 801000 | 785000 | 73.2 | 22500 | 9252.067 |  | 2
95 | 80 | 75 | 79.7527 | 1105000 | 361000 | 77.9 | 27000 | 14142.743 |  | 2
95 | 80 | 72 | 68.6171 | 1050000 | 454000 | 76.7 | 27000 | 14142.743 |  | 2
95 | 80 | 67 | 51.5724 | 965000 | 610000 | 75.2 | 27000 | 14142.743 |  | 2
95 | 80 | 62 | 36.2232 | 887000 | 762000 | 74.2 | 27000 | 14142.743 |  | 2
95 | 80 | 57 | 22.3618 | 843000 | 843000 | 73.8 | 27000 | 14142.743 |  | 2
95 | 80 | 75 | 79.7527 | 1129000 | 382000 | 78.4 | 31500 | 20679.6201 |  | 2
95 | 80 | 72 | 68.6171 | 1074000 | 487000 | 77.3 | 31500 | 20679.6201 |  | 2
95 | 80 | 67 | 51.5724 | 988000 | 664000 | 75.5 | 31500 | 20679.6201 |  | 2
95 | 80 | 62 | 36.2232 | 912000 | 831000 | 74.5 | 31500 | 20679.6201 |  | 2
95 | 80 | 57 | 22.3618 | 885000 | 885000 | 74.1 | 31500 | 20679.6201 |  | 2
105 | 80 | 75 | 79.7527 | 965000 | 277000 | 84.9 | 18000 | 5757.5363 |  | 2
105 | 80 | 72 | 68.6171 | 914000 | 345000 | 84.4 | 18000 | 5757.5363 |  | 2
105 | 80 | 67 | 51.5724 | 835000 | 458000 | 83.8 | 18000 | 5757.5363 |  | 2
105 | 80 | 62 | 36.2232 | 762000 | 568000 | 83.7 | 18000 | 5757.5363 |  | 2
105 | 80 | 57 | 22.3618 | 710000 | 672000 | 83.4 | 18000 | 5757.5363 |  | 2
105 | 80 | 75 | 79.7527 | 1008000 | 295000 | 85.5 | 22500 | 9252.067 |  | 2
105 | 80 | 72 | 68.6171 | 957000 | 377000 | 84.8 | 22500 | 9252.067 |  | 2
105 | 80 | 67 | 51.5724 | 877000 | 513000 | 84.1 | 22500 | 9252.067 |  | 2
105 | 80 | 62 | 36.2232 | 804000 | 648000 | 83.7 | 22500 | 9252.067 |  | 2
105 | 80 | 57 | 22.3618 | 758000 | 744000 | 83.2 | 22500 | 9252.067 |  | 2
105 | 80 | 75 | 79.7527 | 1036000 | 313000 | 86 | 27000 | 14142.743 |  | 2
105 | 80 | 72 | 68.6171 | 986000 | 409000 | 85.2 | 27000 | 14142.743 |  | 2
105 | 80 | 67 | 51.5724 | 905000 | 567000 | 84.3 | 27000 | 14142.743 |  | 2
105 | 80 | 62 | 36.2232 | 834000 | 722000 | 83.7 | 27000 | 14142.743 |  | 2
105 | 80 | 57 | 22.3618 | 798000 | 798000 | 83.5 | 27000 | 14142.743 |  | 2
105 | 80 | 75 | 79.7527 | 1058000 | 332000 | 86.5 | 31500 | 20679.6201 |  | 2
105 | 80 | 72 | 68.6171 | 1006000 | 440000 | 85.5 | 31500 | 20679.6201 |  | 2
105 | 80 | 67 | 51.5724 | 926000 | 620000 | 84.5 | 31500 | 20679.6201 |  | 2
105 | 80 | 62 | 36.2232 | 858000 | 793000 | 83.8 | 31500 | 20679.6201 |  | 2
105 | 80 | 57 | 22.3618 | 836000 | 836000 | 83.6 | 31500 | 20679.6201 |  | 2
115 | 80 | 75 | 79.7527 | 903000 | 233000 | 95.3 | 18000 | 5757.5363 |  | 2
115 | 80 | 72 | 68.6171 | 855000 | 304000 | 95 | 18000 | 5757.5363 |  | 2
115 | 80 | 67 | 51.5724 | 780000 | 418000 | 95 | 18000 | 5757.5363 |  | 2
115 | 80 | 62 | 36.2232 | 714000 | 536000 | 95.6 | 18000 | 5757.5363 |  | 2
115 | 80 | 57 | 22.3618 | 664000 | 626000 | 95.6 | 18000 | 5757.5363 |  | 2
115 | 80 | 75 | 79.7527 | 940000 | 248000 | 95.7 | 22500 | 9252.067 |  | 2
115 | 80 | 72 | 68.6171 | 892000 | 332000 | 95.2 | 22500 | 9252.067 |  | 2
115 | 80 | 67 | 51.5724 | 817000 | 471000 | 94.9 | 22500 | 9252.067 |  | 2
115 | 80 | 62 | 36.2232 | 748000 | 608000 | 95.1 | 22500 | 9252.067 |  | 2
115 | 80 | 57 | 22.3618 | 712000 | 700000 | 94.9 | 22500 | 9252.067 |  | 2
115 | 80 | 75 | 79.7527 | 965000 | 264000 | 96 | 27000 | 14142.743 |  | 2
115 | 80 | 72 | 68.6171 | 917000 | 361000 | 95.4 | 27000 | 14142.743 |  | 2
115 | 80 | 67 | 51.5724 | 842000 | 523000 | 94.9 | 27000 | 14142.743 |  | 2
115 | 80 | 62 | 36.2232 | 777000 | 680000 | 94.8 | 27000 | 14142.743 |  | 2
115 | 80 | 57 | 22.3618 | 748000 | 748000 | 94.9 | 27000 | 14142.743 |  | 2
115 | 80 | 75 | 79.7527 | 984000 | 282000 | 96.3 | 31500 | 20679.6201 |  | 2
115 | 80 | 72 | 68.6171 | 935000 | 391000 | 95.6 | 31500 | 20679.6201 |  | 2
115 | 80 | 67 | 51.5724 | 860000 | 575000 | 95 | 31500 | 20679.6201 |  | 2
115 | 80 | 62 | 36.2232 | 803000 | 735000 | 94.6 | 31500 | 20679.6201 |  | 2
115 | 80 | 57 | 22.3618 | 783000 | 783000 | 94.7 | 31500 | 20679.6201 |  | 2
75 | 80 | 75 | 79.7527 | 1281000 | 497000 | 65.6 | 36000 | 25095.1899 |  | 2
75 | 80 | 72 | 68.6171 | 1220000 | 611000 | 64.4 | 36000 | 25095.1899 |  | 2
75 | 80 | 67 | 51.5724 | 1124000 | 803000 | 62.5 | 36000 | 25095.1899 |  | 2
75 | 80 | 62 | 36.2232 | 1038000 | 978000 | 60.9 | 36000 | 25095.1899 |  | 2
75 | 80 | 57 | 22.3618 | 1014000 | 1014000 | 60.4 | 36000 | 25095.1899 |  | 2
85 | 80 | 75 | 79.7527 | 1216000 | 450000 | 71.8 | 36000 | 25095.1899 |  | 2
85 | 80 | 72 | 68.6171 | 1157000 | 566000 | 70.5 | 36000 | 25095.1899 |  | 2
85 | 80 | 67 | 51.5724 | 1066000 | 760000 | 68.7 | 36000 | 25095.1899 |  | 2
85 | 80 | 62 | 36.2232 | 986000 | 935000 | 67.2 | 36000 | 25095.1899 |  | 2
85 | 80 | 57 | 22.3618 | 967000 | 967000 | 66.8 | 36000 | 25095.1899 |  | 2
95 | 80 | 75 | 79.7527 | 1148000 | 402000 | 78.8 | 36000 | 25095.1899 |  | 2
95 | 80 | 72 | 68.6171 | 1092000 | 520000 | 77.7 | 36000 | 25095.1899 |  | 2
95 | 80 | 67 | 51.5724 | 1005000 | 717000 | 75.9 | 36000 | 25095.1899 |  | 2
95 | 80 | 62 | 36.2232 | 934000 | 888000 | 74.7 | 36000 | 25095.1899 |  | 2
95 | 80 | 57 | 22.3618 | 919000 | 919000 | 74.5 | 36000 | 25095.1899 |  | 2
105 | 80 | 75 | 79.7527 | 1074000 | 352000 | 86.9 | 36000 | 25095.1899 |  | 2
105 | 80 | 72 | 68.6171 | 1022000 | 471000 | 85.8 | 36000 | 25095.1899 |  | 2
105 | 80 | 67 | 51.5724 | 942000 | 672000 | 84.7 | 36000 | 25095.1899 |  | 2
105 | 80 | 62 | 36.2232 | 881000 | 837000 | 83.9 | 36000 | 25095.1899 |  | 2
105 | 80 | 57 | 22.3618 | 867000 | 867000 | 83.8 | 36000 | 25095.1899 |  | 2
115 | 80 | 75 | 79.7527 | 998000 | 300000 | 96.5 | 36000 | 25095.1899 |  | 2
115 | 80 | 72 | 68.6171 | 949000 | 421000 | 95.8 | 36000 | 25095.1899 |  | 2
115 | 80 | 67 | 51.5724 | 874000 | 624000 | 95 | 36000 | 25095.1899 |  | 2
115 | 80 | 62 | 36.2232 | 824000 | 783000 | 94.6 | 36000 | 25095.1899 |  | 2
115 | 80 | 57 | 22.3618 | 812000 | 812000 | 94.6 | 36000 | 25095.1899 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 18
Degradation Coefficient (C_d) |  | 48/50P2,P3,P4,P5100 (100 TONS) — SubCool
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 80 | 75 | 79.7527 | 1146000 | 418000 | 67.9 | 20000 | 7141.1788 |  | 1
75 | 80 | 72 | 68.6171 | 1084000 | 481000 | 66.6 | 20000 | 7141.1788 |  | 1
75 | 80 | 67 | 51.5724 | 987000 | 581000 | 64.7 | 20000 | 7141.1788 |  | 1
75 | 80 | 62 | 36.2232 | 897000 | 680000 | 63.1 | 20000 | 7141.1788 |  | 1
75 | 80 | 57 | 22.3618 | 815000 | 773000 | 61.7 | 20000 | 7141.1788 |  | 1
75 | 80 | 75 | 79.7527 | 1203000 | 450000 | 69.1 | 25000 | 11785.9665 |  | 1
75 | 80 | 72 | 68.6171 | 1165000 | 548000 | 68.7 | 25000 | 11785.9665 |  | 1
75 | 80 | 67 | 51.5724 | 1042000 | 645000 | 65.9 | 25000 | 11785.9665 |  | 1
75 | 80 | 62 | 36.2232 | 949000 | 764000 | 64.1 | 25000 | 11785.9665 |  | 1
75 | 80 | 57 | 22.3618 | 873000 | 850000 | 62.5 | 25000 | 11785.9665 |  | 1
75 | 80 | 75 | 79.7527 | 1261000 | 494000 | 70.6 | 30000 | 18262.4134 |  | 1
75 | 80 | 72 | 68.6171 | 1167000 | 547000 | 68.5 | 30000 | 18262.4134 |  | 1
75 | 80 | 67 | 51.5724 | 1071000 | 693000 | 66.5 | 30000 | 18262.4134 |  | 1
75 | 80 | 62 | 36.2232 | 986000 | 841000 | 64.8 | 30000 | 18262.4134 |  | 1
75 | 80 | 57 | 22.3618 | 932000 | 932000 | 63.9 | 30000 | 18262.4134 |  | 1
85 | 80 | 75 | 79.7527 | 1064000 | 351000 | 74.1 | 20000 | 7141.1788 |  | 1
85 | 80 | 72 | 68.6171 | 1005000 | 414000 | 72.8 | 20000 | 7141.1788 |  | 1
85 | 80 | 67 | 51.5724 | 946000 | 551000 | 71.6 | 20000 | 7141.1788 |  | 1
85 | 80 | 62 | 36.2232 | 856000 | 648000 | 70.1 | 20000 | 7141.1788 |  | 1
85 | 80 | 57 | 22.3618 | 779000 | 735000 | 68.7 | 20000 | 7141.1788 |  | 1
85 | 80 | 75 | 79.7527 | 1111000 | 373000 | 75.2 | 25000 | 11785.9665 |  | 1
85 | 80 | 72 | 68.6171 | 1053000 | 450000 | 73.9 | 25000 | 11785.9665 |  | 1
85 | 80 | 67 | 51.5724 | 991000 | 607000 | 72.5 | 25000 | 11785.9665 |  | 1
85 | 80 | 62 | 36.2232 | 913000 | 739000 | 71.1 | 25000 | 11785.9665 |  | 1
85 | 80 | 57 | 22.3618 | 836000 | 814000 | 69.5 | 25000 | 11785.9665 |  | 1
85 | 80 | 75 | 79.7527 | 1141000 | 390000 | 76 | 30000 | 18262.4134 |  | 1
85 | 80 | 72 | 68.6171 | 1089000 | 484000 | 74.8 | 30000 | 18262.4134 |  | 1
85 | 80 | 67 | 51.5724 | 1003000 | 638000 | 73 | 30000 | 18262.4134 |  | 1
85 | 80 | 62 | 36.2232 | 939000 | 805000 | 71.5 | 30000 | 18262.4134 |  | 1
85 | 80 | 57 | 22.3618 | 892000 | 892000 | 70.8 | 30000 | 18262.4134 |  | 1
95 | 80 | 75 | 79.7527 | 1004000 | 306000 | 81.6 | 20000 | 7141.1788 |  | 1
95 | 80 | 72 | 68.6171 | 941000 | 365000 | 80.2 | 20000 | 7141.1788 |  | 1
95 | 80 | 67 | 51.5724 | 894000 | 511000 | 79.5 | 20000 | 7141.1788 |  | 1
95 | 80 | 62 | 36.2232 | 813000 | 614000 | 78.3 | 20000 | 7141.1788 |  | 1
95 | 80 | 57 | 22.3618 | 762000 | 719000 | 77.8 | 20000 | 7141.1788 |  | 1
95 | 80 | 75 | 79.7527 | 1042000 | 321000 | 82.6 | 25000 | 11785.9665 |  | 1
95 | 80 | 72 | 68.6171 | 995000 | 408000 | 81.5 | 25000 | 11785.9665 |  | 1
95 | 80 | 67 | 51.5724 | 906000 | 535000 | 79.6 | 25000 | 11785.9665 |  | 1
95 | 80 | 62 | 36.2232 | 857000 | 695000 | 78.9 | 25000 | 11785.9665 |  | 1
95 | 80 | 57 | 22.3618 | 814000 | 793000 | 78.4 | 25000 | 11785.9665 |  | 1
95 | 80 | 75 | 79.7527 | 1073000 | 340000 | 83.4 | 30000 | 18262.4134 |  | 1
95 | 80 | 72 | 68.6171 | 1024000 | 437000 | 82.3 | 30000 | 18262.4134 |  | 1
95 | 80 | 67 | 51.5724 | 945000 | 596000 | 80.5 | 30000 | 18262.4134 |  | 1
95 | 80 | 62 | 36.2232 | 889000 | 767000 | 79.5 | 30000 | 18262.4134 |  | 1
95 | 80 | 57 | 22.3618 | 850000 | 850000 | 79 | 30000 | 18262.4134 |  | 1
105 | 80 | 75 | 79.7527 | 931000 | 251000 | 90 | 20000 | 7141.1788 |  | 1
105 | 80 | 72 | 68.6171 | 898000 | 337000 | 89.4 | 20000 | 7141.1788 |  | 1
105 | 80 | 67 | 51.5724 | 843000 | 474000 | 88.9 | 20000 | 7141.1788 |  | 1
105 | 80 | 62 | 36.2232 | 766000 | 579000 | 87.8 | 20000 | 7141.1788 |  | 1
105 | 80 | 57 | 22.3618 | 724000 | 683000 | 87.5 | 20000 | 7141.1788 |  | 1
105 | 80 | 75 | 79.7527 | 976000 | 274000 | 91.1 | 25000 | 11785.9665 |  | 1
105 | 80 | 72 | 68.6171 | 926000 | 356000 | 90 | 25000 | 11785.9665 |  | 1
105 | 80 | 67 | 51.5724 | 846000 | 490000 | 88.7 | 25000 | 11785.9665 |  | 1
105 | 80 | 62 | 36.2232 | 807000 | 658000 | 88.3 | 25000 | 11785.9665 |  | 1
105 | 80 | 57 | 22.3618 | 771000 | 753000 | 88 | 25000 | 11785.9665 |  | 1
105 | 80 | 75 | 79.7527 | 1003000 | 291000 | 91.8 | 30000 | 18262.4134 |  | 1
105 | 80 | 72 | 68.6171 | 955000 | 387000 | 90.7 | 30000 | 18262.4134 |  | 1
105 | 80 | 67 | 51.5724 | 866000 | 533000 | 89 | 30000 | 18262.4134 |  | 1
105 | 80 | 62 | 36.2232 | 836000 | 727000 | 88.8 | 30000 | 18262.4134 |  | 1
105 | 80 | 57 | 22.3618 | 805000 | 805000 | 88.5 | 30000 | 18262.4134 |  | 1
115 | 80 | 75 | 79.7527 | 867000 | 206000 | 100.2 | 20000 | 7141.1788 |  | 1
115 | 80 | 72 | 68.6171 | 835000 | 292000 | 99.7 | 20000 | 7141.1788 |  | 1
115 | 80 | 67 | 51.5724 | 792000 | 439000 | 99.9 | 20000 | 7141.1788 |  | 1
115 | 80 | 62 | 36.2232 | 715000 | 543000 | 98.8 | 20000 | 7141.1788 |  | 1
115 | 80 | 57 | 22.3618 | 683000 | 644000 | 98.7 | 20000 | 7141.1788 |  | 1
115 | 80 | 75 | 79.7527 | 905000 | 225000 | 100.9 | 25000 | 11785.9665 |  | 1
115 | 80 | 72 | 68.6171 | 859000 | 309000 | 100.1 | 25000 | 11785.9665 |  | 1
115 | 80 | 67 | 51.5724 | 797000 | 460000 | 99.5 | 25000 | 11785.9665 |  | 1
115 | 80 | 62 | 36.2232 | 762000 | 628000 | 99.5 | 25000 | 11785.9665 |  | 1
115 | 80 | 57 | 22.3618 | 726000 | 710000 | 99 | 25000 | 11785.9665 |  | 1
115 | 80 | 75 | 79.7527 | 927000 | 238000 | 101.4 | 30000 | 18262.4134 |  | 1
115 | 80 | 72 | 68.6171 | 882000 | 335000 | 100.6 | 30000 | 18262.4134 |  | 1
115 | 80 | 67 | 51.5724 | 823000 | 508000 | 99.7 | 30000 | 18262.4134 |  | 1
115 | 80 | 62 | 36.2232 | 779000 | 686000 | 99.5 | 30000 | 18262.4134 |  | 1
115 | 80 | 57 | 22.3618 | 756000 | 756000 | 99.4 | 30000 | 18262.4134 |  | 1
75 | 80 | 75 | 79.7527 | 1273000 | 499000 | 70.8 | 35000 | 27101.8883 |  | 1
75 | 80 | 72 | 68.6171 | 1210000 | 597000 | 69.4 | 35000 | 27101.8883 |  | 1
75 | 80 | 67 | 51.5724 | 1133000 | 781000 | 68.1 | 35000 | 27101.8883 |  | 1
75 | 80 | 62 | 36.2232 | 1020000 | 915000 | 65.5 | 35000 | 27101.8883 |  | 1
75 | 80 | 57 | 22.3618 | 973000 | 973000 | 64.6 | 35000 | 27101.8883 |  | 1
75 | 80 | 75 | 79.7527 | 1296000 | 522000 | 71.4 | 40000 | 38473.1788 |  | 1
75 | 80 | 72 | 68.6171 | 1233000 | 630000 | 70 | 40000 | 38473.1788 |  | 1
75 | 80 | 67 | 51.5724 | 1157000 | 834000 | 68.7 | 40000 | 38473.1788 |  | 1
75 | 80 | 62 | 36.2232 | 1036000 | 968000 | 65.9 | 40000 | 38473.1788 |  | 1
75 | 80 | 57 | 22.3618 | 998000 | 998000 | 65 | 40000 | 38473.1788 |  | 1
85 | 80 | 75 | 79.7527 | 1164000 | 408000 | 76.6 | 35000 | 27101.8883 |  | 1
85 | 80 | 72 | 68.6171 | 1107000 | 510000 | 75.3 | 35000 | 27101.8883 |  | 1
85 | 80 | 67 | 51.5724 | 1024000 | 685000 | 73.4 | 35000 | 27101.8883 |  | 1
85 | 80 | 62 | 36.2232 | 969000 | 875000 | 72.2 | 35000 | 27101.8883 |  | 1
85 | 80 | 57 | 22.3618 | 917000 | 917000 | 71 | 35000 | 27101.8883 |  | 1
85 | 80 | 75 | 79.7527 | 1186000 | 429000 | 77.2 | 40000 | 38473.1788 |  | 1
85 | 80 | 72 | 68.6171 | 1130000 | 543000 | 75.8 | 40000 | 38473.1788 |  | 1
85 | 80 | 67 | 51.5724 | 1043000 | 734000 | 74 | 40000 | 38473.1788 |  | 1
85 | 80 | 62 | 36.2232 | 967000 | 906000 | 72.3 | 40000 | 38473.1788 |  | 1
85 | 80 | 57 | 22.3618 | 964000 | 964000 | 72.1 | 40000 | 38473.1788 |  | 1
95 | 80 | 75 | 79.7527 | 1096000 | 359000 | 84 | 35000 | 27101.8883 |  | 1
95 | 80 | 72 | 68.6171 | 1044000 | 465000 | 82.8 | 35000 | 27101.8883 |  | 1
95 | 80 | 67 | 51.5724 | 961000 | 638000 | 80.9 | 35000 | 27101.8883 |  | 1
95 | 80 | 62 | 36.2232 | 914000 | 829000 | 79.9 | 35000 | 27101.8883 |  | 1
95 | 80 | 57 | 22.3618 | 886000 | 886000 | 79.5 | 35000 | 27101.8883 |  | 1
95 | 80 | 75 | 79.7527 | 1114000 | 377000 | 84.5 | 40000 | 38473.1788 |  | 1
95 | 80 | 72 | 68.6171 | 1059000 | 490000 | 83.2 | 40000 | 38473.1788 |  | 1
95 | 80 | 67 | 51.5724 | 979000 | 687000 | 81.4 | 40000 | 38473.1788 |  | 1
95 | 80 | 62 | 36.2232 | 935000 | 875000 | 80.3 | 40000 | 38473.1788 |  | 1
95 | 80 | 57 | 22.3618 | 876000 | 876000 | 79 | 40000 | 38473.1788 |  | 1
105 | 80 | 75 | 79.7527 | 1021000 | 306000 | 92.4 | 35000 | 27101.8883 |  | 1
105 | 80 | 72 | 68.6171 | 974000 | 415000 | 91.2 | 35000 | 27101.8883 |  | 1
105 | 80 | 67 | 51.5724 | 900000 | 595000 | 89.7 | 35000 | 27101.8883 |  | 1
105 | 80 | 62 | 36.2232 | 860000 | 782000 | 89.1 | 35000 | 27101.8883 |  | 1
105 | 80 | 57 | 22.3618 | 838000 | 838000 | 88.9 | 35000 | 27101.8883 |  | 1
105 | 80 | 75 | 79.7527 | 1037000 | 322000 | 92.8 | 40000 | 38473.1788 |  | 1
105 | 80 | 72 | 68.6171 | 990000 | 442000 | 91.7 | 40000 | 38473.1788 |  | 1
105 | 80 | 67 | 51.5724 | 918000 | 644000 | 90.1 | 40000 | 38473.1788 |  | 1
105 | 80 | 62 | 36.2232 | 886000 | 828000 | 89.6 | 40000 | 38473.1788 |  | 1
105 | 80 | 57 | 22.3618 | 825000 | 825000 | 88.2 | 40000 | 38473.1788 |  | 1
115 | 80 | 75 | 79.7527 | 944000 | 252000 | 101.8 | 35000 | 27101.8883 |  | 1
115 | 80 | 72 | 68.6171 | 901000 | 363000 | 100.9 | 35000 | 27101.8883 |  | 1
115 | 80 | 67 | 51.5724 | 833000 | 547000 | 99.9 | 35000 | 27101.8883 |  | 1
115 | 80 | 62 | 36.2232 | 806000 | 729000 | 99.8 | 35000 | 27101.8883 |  | 1
115 | 80 | 57 | 22.3618 | 787000 | 787000 | 99.7 | 35000 | 27101.8883 |  | 1
115 | 80 | 75 | 79.7527 | 824000 | 765000 | 100 | 40000 | 38473.1788 |  | 1
115 | 80 | 72 | 68.6171 | 955000 | 265000 | 102.1 | 40000 | 38473.1788 |  | 1
115 | 80 | 67 | 51.5724 | 913000 | 388000 | 101.2 | 40000 | 38473.1788 |  | 1
115 | 80 | 62 | 36.2232 | 841000 | 586000 | 100 | 40000 | 38473.1788 |  | 1
115 | 80 | 57 | 22.3618 | 813000 | 813000 | 99.9 | 40000 | 38473.1788 |  | 1
75 | 80 | 75 | 79.7527 | 1210000 | 417000 | 69.7 | 20000 | 7141.1788 |  | 2
75 | 80 | 72 | 68.6171 | 1148000 | 489000 | 68.3 | 20000 | 7141.1788 |  | 2
75 | 80 | 67 | 51.5724 | 1077000 | 633000 | 66.8 | 20000 | 7141.1788 |  | 2
75 | 80 | 62 | 36.2232 | 994000 | 756000 | 65.4 | 20000 | 7141.1788 |  | 2
75 | 80 | 57 | 22.3618 | 900000 | 848000 | 64.1 | 20000 | 7141.1788 |  | 2
75 | 80 | 75 | 79.7527 | 1255000 | 433000 | 70.8 | 25000 | 11785.9665 |  | 2
75 | 80 | 72 | 68.6171 | 1205000 | 531000 | 69.6 | 25000 | 11785.9665 |  | 2
75 | 80 | 67 | 51.5724 | 1119000 | 687000 | 67.7 | 25000 | 11785.9665 |  | 2
75 | 80 | 62 | 36.2232 | 1042000 | 843000 | 66.2 | 25000 | 11785.9665 |  | 2
75 | 80 | 57 | 22.3618 | 951000 | 924000 | 64.1 | 25000 | 11785.9665 |  | 2
75 | 80 | 75 | 79.7527 | 1306000 | 470000 | 72.1 | 30000 | 18262.4134 |  | 2
75 | 80 | 72 | 68.6171 | 1243000 | 571000 | 70.6 | 30000 | 18262.4134 |  | 2
75 | 80 | 67 | 51.5724 | 1145000 | 738000 | 68.4 | 30000 | 18262.4134 |  | 2
75 | 80 | 62 | 36.2232 | 1080000 | 929000 | 67 | 30000 | 18262.4134 |  | 2
75 | 80 | 57 | 22.3618 | 1025000 | 1025000 | 66 | 30000 | 18262.4134 |  | 2
85 | 80 | 75 | 79.7527 | 1152000 | 374000 | 76.4 | 20000 | 7141.1788 |  | 2
85 | 80 | 72 | 68.6171 | 1116000 | 471000 | 75.5 | 20000 | 7141.1788 |  | 2
85 | 80 | 67 | 51.5724 | 1016000 | 584000 | 73.3 | 20000 | 7141.1788 |  | 2
85 | 80 | 62 | 36.2232 | 942000 | 714000 | 72.6 | 20000 | 7141.1788 |  | 2
85 | 80 | 57 | 22.3618 | 863000 | 811000 | 71.7 | 20000 | 7141.1788 |  | 2
85 | 80 | 75 | 79.7527 | 1204000 | 398000 | 77.7 | 25000 | 11785.9665 |  | 2
85 | 80 | 72 | 68.6171 | 1140000 | 482000 | 76.2 | 25000 | 11785.9665 |  | 2
85 | 80 | 67 | 51.5724 | 1077000 | 658000 | 74.8 | 25000 | 11785.9665 |  | 2
85 | 80 | 62 | 36.2232 | 993000 | 806000 | 73.2 | 25000 | 11785.9665 |  | 2
85 | 80 | 57 | 22.3618 | 933000 | 907000 | 72.4 | 25000 | 11785.9665 |  | 2
85 | 80 | 75 | 79.7527 | 1274000 | 461000 | 79 | 30000 | 18262.4134 |  | 2
85 | 80 | 72 | 68.6171 | 1213000 | 560000 | 77.6 | 30000 | 18262.4134 |  | 2
85 | 80 | 67 | 51.5724 | 1136000 | 745000 | 76.2 | 30000 | 18262.4134 |  | 2
85 | 80 | 62 | 36.2232 | 1029000 | 889000 | 73.8 | 30000 | 18262.4134 |  | 2
85 | 80 | 57 | 22.3618 | 981000 | 981000 | 73.1 | 30000 | 18262.4134 |  | 2
95 | 80 | 75 | 79.7527 | 1091000 | 329000 | 84.2 | 20000 | 7141.1788 |  | 2
95 | 80 | 72 | 68.6171 | 1035000 | 405000 | 82.9 | 20000 | 7141.1788 |  | 2
95 | 80 | 67 | 51.5724 | 965000 | 546000 | 81.9 | 20000 | 7141.1788 |  | 2
95 | 80 | 62 | 36.2232 | 876000 | 659000 | 80.7 | 20000 | 7141.1788 |  | 2
95 | 80 | 57 | 22.3618 | 825000 | 774000 | 80.9 | 20000 | 7141.1788 |  | 2
95 | 80 | 75 | 79.7527 | 1139000 | 350000 | 85.4 | 25000 | 11785.9665 |  | 2
95 | 80 | 72 | 68.6171 | 1083000 | 441000 | 84.1 | 25000 | 11785.9665 |  | 2
95 | 80 | 67 | 51.5724 | 1017000 | 614000 | 82.8 | 25000 | 11785.9665 |  | 2
95 | 80 | 62 | 36.2232 | 926000 | 752000 | 81.3 | 25000 | 11785.9665 |  | 2
95 | 80 | 57 | 22.3618 | 890000 | 866000 | 81.3 | 25000 | 11785.9665 |  | 2
95 | 80 | 75 | 79.7527 | 1171000 | 370000 | 86.3 | 30000 | 18262.4134 |  | 2
95 | 80 | 72 | 68.6171 | 1110000 | 471000 | 84.8 | 30000 | 18262.4134 |  | 2
95 | 80 | 67 | 51.5724 | 1026000 | 650000 | 82.9 | 30000 | 18262.4134 |  | 2
95 | 80 | 62 | 36.2232 | 975000 | 848000 | 82.3 | 30000 | 18262.4134 |  | 2
95 | 80 | 57 | 22.3618 | 935000 | 935000 | 81.8 | 30000 | 18262.4134 |  | 2
105 | 80 | 75 | 79.7527 | 1027000 | 283000 | 93.4 | 20000 | 7141.1788 |  | 2
105 | 80 | 72 | 68.6171 | 1000000 | 387000 | 93.2 | 20000 | 7141.1788 |  | 2
105 | 80 | 67 | 51.5724 | 909000 | 505000 | 92 | 20000 | 7141.1788 |  | 2
105 | 80 | 62 | 36.2232 | 824000 | 621000 | 91.3 | 20000 | 7141.1788 |  | 2
105 | 80 | 57 | 22.3618 | 758000 | 709000 | 90.3 | 20000 | 7141.1788 |  | 2
105 | 80 | 75 | 79.7527 | 1068000 | 300000 | 94.3 | 25000 | 11785.9665 |  | 2
105 | 80 | 72 | 68.6171 | 1013000 | 390000 | 93.2 | 25000 | 11785.9665 |  | 2
105 | 80 | 67 | 51.5724 | 957000 | 571000 | 92.7 | 25000 | 11785.9665 |  | 2
105 | 80 | 62 | 36.2232 | 888000 | 728000 | 92.2 | 25000 | 11785.9665 |  | 2
105 | 80 | 57 | 22.3618 | 844000 | 823000 | 91.8 | 25000 | 11785.9665 |  | 2
105 | 80 | 75 | 79.7527 | 1097000 | 318000 | 95 | 30000 | 18262.4134 |  | 2
105 | 80 | 72 | 68.6171 | 1041000 | 422000 | 93.8 | 30000 | 18262.4134 |  | 2
105 | 80 | 67 | 51.5724 | 924000 | 567000 | 91.7 | 30000 | 18262.4134 |  | 2
105 | 80 | 62 | 36.2232 | 919000 | 805000 | 92.4 | 30000 | 18262.4134 |  | 2
105 | 80 | 57 | 22.3618 | 885000 | 885000 | 92.2 | 30000 | 18262.4134 |  | 2
115 | 80 | 75 | 79.7527 | 960000 | 237000 | 104.3 | 20000 | 7141.1788 |  | 2
115 | 80 | 72 | 68.6171 | 935000 | 342000 | 104.5 | 20000 | 7141.1788 |  | 2
115 | 80 | 67 | 51.5724 | 849000 | 476000 | 103.8 | 20000 | 7141.1788 |  | 2
115 | 80 | 62 | 36.2232 | 789000 | 602000 | 104.7 | 20000 | 7141.1788 |  | 2
115 | 80 | 57 | 22.3618 | 715000 | 669000 | 102.8 | 20000 | 7141.1788 |  | 2
115 | 80 | 75 | 79.7527 | 987000 | 242000 | 104.7 | 25000 | 11785.9665 |  | 2
115 | 80 | 72 | 68.6171 | 929000 | 327000 | 103.8 | 25000 | 11785.9665 |  | 2
115 | 80 | 67 | 51.5724 | 892000 | 541000 | 104.2 | 25000 | 11785.9665 |  | 2
115 | 80 | 62 | 36.2232 | 811000 | 668000 | 103.5 | 25000 | 11785.9665 |  | 2
115 | 80 | 57 | 22.3618 | 794000 | 775000 | 104.2 | 25000 | 11785.9665 |  | 2
115 | 80 | 75 | 79.7527 | 1010000 | 255000 | 105.2 | 30000 | 18262.4134 |  | 2
115 | 80 | 72 | 68.6171 | 971000 | 374000 | 104.6 | 30000 | 18262.4134 |  | 2
115 | 80 | 67 | 51.5724 | 893000 | 556000 | 103.7 | 30000 | 18262.4134 |  | 2
115 | 80 | 62 | 36.2232 | 844000 | 736000 | 103.3 | 30000 | 18262.4134 |  | 2
115 | 80 | 57 | 22.3618 | 810000 | 810000 | 103.1 | 30000 | 18262.4134 |  | 2
75 | 80 | 75 | 79.7527 | 1334000 | 494000 | 72.9 | 35000 | 27101.8883 |  | 2
75 | 80 | 72 | 68.6171 | 1272000 | 609000 | 71.4 | 35000 | 27101.8883 |  | 2
75 | 80 | 67 | 51.5724 | 1173000 | 800000 | 69.1 | 35000 | 27101.8883 |  | 2
75 | 80 | 62 | 36.2232 | 1099000 | 996000 | 67.3 | 35000 | 27101.8883 |  | 2
75 | 80 | 57 | 22.3618 | 1046000 | 1046000 | 66.2 | 35000 | 27101.8883 |  | 2
75 | 80 | 75 | 79.7527 | 1356000 | 517000 | 73.6 | 40000 | 38473.1788 |  | 2
75 | 80 | 72 | 68.6171 | 1293000 | 646000 | 72 | 40000 | 38473.1788 |  | 2
75 | 80 | 67 | 51.5724 | 1220000 | 885000 | 69.8 | 40000 | 38473.1788 |  | 2
75 | 80 | 62 | 36.2232 | 1135000 | 1072000 | 68.2 | 40000 | 38473.1788 |  | 2
75 | 80 | 57 | 22.3618 | 1114000 | 1114000 | 67.7 | 40000 | 38473.1788 |  | 2
85 | 80 | 75 | 79.7527 | 1302000 | 487000 | 79.7 | 35000 | 27101.8883 |  | 2
85 | 80 | 72 | 68.6171 | 1263000 | 621000 | 79.1 | 35000 | 27101.8883 |  | 2
85 | 80 | 67 | 51.5724 | 1111000 | 753000 | 75.7 | 35000 | 27101.8883 |  | 2
85 | 80 | 62 | 36.2232 | 1056000 | 962000 | 74.4 | 35000 | 27101.8883 |  | 2
85 | 80 | 57 | 22.3618 | 1018000 | 1018000 | 73.5 | 35000 | 27101.8883 |  | 2
85 | 80 | 75 | 79.7527 | 1323000 | 510000 | 80.3 | 40000 | 38473.1788 |  | 2
85 | 80 | 72 | 68.6171 | 1262000 | 636000 | 78.9 | 40000 | 38473.1788 |  | 2
85 | 80 | 67 | 51.5724 | 1129000 | 809000 | 76.2 | 40000 | 38473.1788 |  | 2
85 | 80 | 62 | 36.2232 | 1078000 | 1010000 | 74.9 | 40000 | 38473.1788 |  | 2
85 | 80 | 57 | 22.3618 | 1051000 | 1051000 | 74.2 | 40000 | 38473.1788 |  | 2
95 | 80 | 75 | 79.7527 | 1194000 | 391000 | 87 | 35000 | 27101.8883 |  | 2
95 | 80 | 72 | 68.6171 | 1138000 | 510000 | 85.6 | 35000 | 27101.8883 |  | 2
95 | 80 | 67 | 51.5724 | 1049000 | 708000 | 83.5 | 35000 | 27101.8883 |  | 2
95 | 80 | 62 | 36.2232 | 991000 | 904000 | 82.3 | 35000 | 27101.8883 |  | 2
95 | 80 | 57 | 22.3618 | 978000 | 978000 | 82.3 | 35000 | 27101.8883 |  | 2
95 | 80 | 75 | 79.7527 | 1208000 | 407000 | 87.5 | 40000 | 38473.1788 |  | 2
95 | 80 | 72 | 68.6171 | 1147000 | 535000 | 85.9 | 40000 | 38473.1788 |  | 2
95 | 80 | 67 | 51.5724 | 1067000 | 765000 | 83.9 | 40000 | 38473.1788 |  | 2
95 | 80 | 62 | 36.2232 | 1014000 | 949000 | 82.6 | 40000 | 38473.1788 |  | 2
95 | 80 | 57 | 22.3618 | 1012000 | 1012000 | 82.8 | 40000 | 38473.1788 |  | 2
105 | 80 | 75 | 79.7527 | 1117000 | 337000 | 95.6 | 35000 | 27101.8883 |  | 2
105 | 80 | 72 | 68.6171 | 1058000 | 451000 | 94.2 | 35000 | 27101.8883 |  | 2
105 | 80 | 67 | 51.5724 | 976000 | 654000 | 92.7 | 35000 | 27101.8883 |  | 2
105 | 80 | 62 | 36.2232 | 935000 | 850000 | 92.2 | 35000 | 27101.8883 |  | 2
105 | 80 | 57 | 22.3618 | 925000 | 925000 | 92.4 | 35000 | 27101.8883 |  | 2
105 | 80 | 75 | 79.7527 | 1133000 | 355000 | 96.1 | 40000 | 38473.1788 |  | 2
105 | 80 | 72 | 68.6171 | 1080000 | 490000 | 94.7 | 40000 | 38473.1788 |  | 2
105 | 80 | 67 | 51.5724 | 995000 | 711000 | 93 | 40000 | 38473.1788 |  | 2
105 | 80 | 62 | 36.2232 | 972000 | 915000 | 92.9 | 40000 | 38473.1788 |  | 2
105 | 80 | 57 | 22.3618 | 957000 | 957000 | 92.7 | 40000 | 38473.1788 |  | 2
115 | 80 | 75 | 79.7527 | 1037000 | 281000 | 105.8 | 35000 | 27101.8883 |  | 2
115 | 80 | 72 | 68.6171 | 980000 | 396000 | 104.7 | 35000 | 27101.8883 |  | 2
115 | 80 | 67 | 51.5724 | 902000 | 602000 | 103.6 | 35000 | 27101.8883 |  | 2
115 | 80 | 62 | 36.2232 | 889000 | 808000 | 104.2 | 35000 | 27101.8883 |  | 2
115 | 80 | 57 | 22.3618 | 869000 | 869000 | 104.1 | 35000 | 27101.8883 |  | 2
115 | 80 | 75 | 79.7527 | 1050000 | 298000 | 106.2 | 40000 | 38473.1788 |  | 2
115 | 80 | 72 | 68.6171 | 994000 | 428000 | 105 | 40000 | 38473.1788 |  | 2
115 | 80 | 67 | 51.5724 | 911000 | 649000 | 103.7 | 40000 | 38473.1788 |  | 2
115 | 80 | 62 | 36.2232 | 896000 | 837000 | 103.8 | 40000 | 38473.1788 |  | 2
115 | 80 | 57 | 22.3618 | 898000 | 898000 | 104.1 | 40000 | 38473.1788 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions