## Table 1
Performance data
Cooling Capacities 48/50 030 (30 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 6000 | [14 empty] | 7500 | [9 empty] | 9000 | [8 empty] | 10500
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  | 62 |  |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  | 75 |  |  | 72 |  | 67 | 62 |  | 57 | 75 |  | 72 | 67 |  | 62 |  | 57
75 | TC SHC kW BF |  |  |  |  | 378 155 22.5 0.00 |  |  |  | 362 167 22.1 0.00 |  | 334 204 21.3 0.22 |  | 308 236 20.8 0.16 |  |  |  | 282 265 20.5 0.14 |  |  | 399 159 23.0 0.00 |  | 379 183 22.5 0.00 |  | 351 224 21.7 0.19 | 325 262 21.2 0.16 |  | 297 292 20.7 0.19 |  |  | 412 166 23.4 0.00 |  |  | 392 195 22.8 0.27 |  | 363 241 22.1 0.20 | 336 285 21.4 0.18 |  | 312 312 21.0 0.26 | 421 175 23.6 0.00 |  | 401 206 23.1 0.25 | 372 256 22.3 0.21 |  | 345 307 21.6 0.19 |  | 327 327 21.3 0.33
85 | TC SHC kW BF |  |  |  |  | 367 150 24.7 0.00 |  |  |  | 353 165 24.4 0.00 |  | 326 201 23.7 0.21 |  | 300 231 23.4 0.15 |  |  |  | 273 259 23.2 0.14 |  |  | 384 155 25.2 0.00 |  | 369 180 24.8 0.16 |  | 342 220 24.1 0.18 | 316 257 23.7 0.16 |  | 290 281 23.1 0.23 |  |  | 396 162 25.6 0.00 |  |  | 380 191 25.1 0.25 |  | 353 236 24.4 0.20 | 327 281 23.9 0.18 |  | 305 305 23.6 0.27 | 404 170 25.8 0.36 |  | 389 202 25.3 0.24 | 361 252 24.7 0.21 |  | 335 303 24.1 0.19 |  | 319 319 23.8 0.35
95 | TC SHC kW BF |  |  |  |  | 357 146 27.4 0.00 |  |  |  | 343 162 27.1 0.00 |  | 316 196 26.6 0.19 |  | 289 226 26.4 0.15 |  |  |  | 264 253 26.1 0.14 |  |  | 373 150 27.9 0.00 |  | 357 176 27.5 0.28 |  | 331 215 27.0 0.18 | 304 252 26.6 0.16 |  | 281 272 26.1 0.26 |  |  | 383 159 28.2 0.00 |  |  | 368 187 27.8 0.24 |  | 341 232 27.3 0.19 | 315 275 26.9 0.17 |  | 295 295 26.6 0.30 | 391 166 28.4 0.31 |  | 376 198 28.0 0.23 | 349 248 27.5 0.21 |  | 322 296 27.1 0.20 |  | 309 309 26.8 0.37
105 | TC SHC kW BF |  |  |  |  | 344 141 30.5 0.00 |  |  |  | 330 158 30.3 0.00 |  | 304 191 30.0 0.17 |  | 277 220 29.8 0.14 |  |  |  | 251 244 30.2 0.16 |  |  | 360 145 31.0 0.00 |  | 344 171 30.7 0.25 |  | 318 210 30.3 0.17 | 291 246 30.0 0.15 |  | 268 268 29.9 0.23 |  |  | 369 154 31.2 0.18 |  |  | 354 182 31.0 0.22 |  | 327 226 30.6 0.19 | 301 269 30.2 0.17 |  | 284 284 30.1 0.32 | 377 162 31.5 0.28 |  | 361 193 31.2 0.22 | 334 242 30.7 0.20 |  | 308 288 30.5 0.20 |  | 297 297 30.2 0.39
115 | TC SHC kW BF |  |  |  |  | 330 135 34.0 0.00 |  |  |  | 315 153 33.9 0.00 |  | 289 185 33.9 0.16 |  | 263 214 34.2 0.14 |  |  |  | 237 234 34.6 0.18 |  |  | 344 141 34.4 0.00 |  | 328 166 34.3 0.22 |  | 302 203 34.1 0.17 | 276 239 34.3 0.15 |  | 256 256 34.6 0.27 |  |  | 352 149 34.7 0.29 |  |  | 337 177 34.6 0.21 |  | 310 219 34.3 0.18 | 285 261 34.4 0.17 |  | 272 272 34.5 0.35 | 360 156 35.1 0.26 |  | 344 187 34.8 0.21 | 317 235 34.4 0.20 |  | 291 279 34.5 0.21 |  | 285 285 34.4 0.42
48/50 030 (30 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 12000 | [14 empty] | 13500 | [9 empty] | 15000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  | 62 |  |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  | 75 |  |  | 72 |  | 67 | 62 |  | 57
75 | TC SHC kW BF |  |  |  |  | 428 182 23.8 0.33 |  |  |  | 408 216 23.3 0.25 |  | 378 272 22.5 0.22 |  | 352 326 21.8 0.22 |  |  |  | 339 339 21.5 0.39 |  |  | 434 189 24.0 0.31 |  | 414 226 23.4 0.25 |  | 383 286 22.6 0.24 | 357 341 21.9 0.25 |  | 349 349 21.8 0.45 |  |  | 439 195 24.1 0.30 |  |  | 418 235 23.6 0.26 |  | 388 300 22.7 0.25 | 360 354 22.0 0.28 |  | 357 357 22.0 0.49
85 | TC SHC kW BF |  |  |  |  | 411 177 26.0 0.30 |  |  |  | 395 212 25.5 0.24 |  | 368 268 24.8 0.22 |  | 341 321 24.3 0.22 |  |  |  | 330 330 24.0 0.41 |  |  | 417 183 26.2 0.29 |  | 400 221 25.7 0.25 |  | 373 282 25.0 0.23 | 346 334 24.4 0.26 |  | 340 340 24.2 0.46 |  |  | 422 190 26.3 0.29 |  |  | 404 230 25.8 0.25 |  | 376 296 25.1 0.25 | 349 348 24.4 0.29 |  | 348 348 24.4 0.50
95 | TC SHC kW BF |  |  |  |  | 398 173 28.6 0.29 |  |  |  | 382 207 28.2 0.23 |  | 355 263 27.6 0.22 |  | 328 313 27.2 0.23 |  |  |  | 320 320 27.0 0.43 |  |  | 404 179 28.8 0.28 |  | 387 217 28.3 0.24 |  | 359 277 27.7 0.23 | 332 327 27.3 0.26 |  | 330 330 27.2 0.48 |  |  | 408 185 28.9 0.28 |  |  | 391 226 28.5 0.25 |  | 363 291 27.8 0.24 | 339 334 27.3 0.32 |  | 338 338 27.3 0.52
105 | TC SHC kW BF |  |  |  |  | 383 168 31.7 0.27 |  |  |  | 367 202 31.4 0.23 |  | 340 257 30.9 0.22 |  | 313 303 30.5 0.24 |  |  |  | 308 308 30.4 0.45 |  |  | 388 175 31.9 0.26 |  | 371 212 31.5 0.24 |  | 344 271 31.0 0.23 | 320 309 30.4 0.32 |  | 317 317 30.6 0.50 |  |  | 392 180 32.0 0.27 |  |  | 375 221 31.6 0.25 |  | 347 285 31.0 0.24 | 326 321 30.7 0.35 |  | 325 325 30.7 0.54
115 | TC SHC kW BF |  |  |  |  | 365 163 35.3 0.25 |  |  |  | 349 196 35.0 0.22 |  | 322 250 34.5 0.21 |  | 296 292 34.4 0.26 |  |  |  | 295 295 34.5 0.47 |  |  | 369 169 35.4 0.25 |  | 353 206 35.1 0.23 |  | 326 264 34.6 0.23 | 303 303 34.5 0.31 |  | 303 303 34.5 0.52 |  |  | 372 175 35.5 0.26 |  |  | 356 214 35.2 0.25 |  | 329 278 34.6 0.24 | 311 310 34.5 0.36 |  | 310 310 34.5 0.56
Performance data (cont)
Cooling Capacities (cont) 48/50 030 (30 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 6000 | [13 empty] | 7500 | [10 empty] | 9000 | [8 empty] | 10500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 384 |  |  | 367 |  | 338 |  |  | 312 |  |  | 289 |  |  | 405 |  | 386 |  | 356 | 329 |  | 307 |  |  |  | 418 |  | 400 |  | 369 | 341 |  | 323 |  | 429 | 410 | 378 |  | 351 |  | 338
75 | SHC kW BF | [5 empty] | 158 22.8 0.00 |  |  | 177 22.3 0.00 |  | 211 21.5 0.10 |  |  | 245 20.8 0.07 |  |  | 277 20.3 0.07 |  |  | 164 23.3 0.00 |  | 192 22.8 0.16 |  | 233 21.9 0.09 | 274 21.2 0.08 |  | 300 20.6 0.17 |  |  |  | 175 23.7 0.13 |  | 205 23.1 0.14 |  | 253 22.3 0.11 | 300 21.5 0.09 |  | 323 21.1 0.23 |  | 183 23.9 0.20 | 217 23.4 0.14 | 271 22.5 0.12 |  | 325 21.8 0.11 |  | 338 21.5 0.31
| TC | [5 empty] | 373 |  |  | 356 |  | 330 |  |  | 305 |  |  | 282 |  |  | 392 |  | 373 |  | 346 | 322 |  | 299 |  |  |  | 404 |  | 386 |  | 358 | 333 |  | 317 |  | 414 | 395 | 367 |  | 342 |  | 331
85 | SHC kW BF | [5 empty] | 153 25.0 0.00 |  |  | 172 24.5 0.00 |  | 208 23.7 0.09 |  |  | 241 23.2 0.07 |  |  | 272 22.9 0.07 |  |  | 161 25.5 0.00 |  | 187 25.0 0.14 |  | 229 24.2 0.09 | 270 23.6 0.08 |  | 299 23.1 0.15 |  |  |  | 170 25.9 0.22 |  | 200 25.3 0.13 |  | 248 24.5 0.10 | 296 23.9 0.09 |  | 317 23.5 0.24 |  | 179 26.1 0.18 | 212 25.6 0.13 | 267 24.8 0.11 |  | 321 24.1 0.11 |  | 331 23.9 0.32
| TC | [5 empty] | 360 |  |  | 346 |  | 322 |  |  | 297 |  |  | 272 |  |  | 377 |  | 362 |  | 337 | 312 |  | 291 |  |  |  | 389 |  | 374 |  | 348 | 323 |  | 309 |  | 399 | 383 | 356 |  | 331 |  | 323
95 | SHC kW BF | [5 empty] | 148 27.5 0.00 |  |  | 169 27.1 0.10 |  | 204 26.5 0.09 |  |  | 237 26.1 0.07 |  |  | 266 26.0 0.07 |  |  | 156 28.0 0.00 |  | 183 27.6 0.13 |  | 225 26.9 0.09 | 266 26.5 0.08 |  | 291 26.2 0.17 |  |  |  | 165 28.4 0.19 |  | 196 27.9 0.12 |  | 244 27.2 0.10 | 292 26.7 0.09 |  | 309 26.5 0.26 |  | 174 28.7 0.16 | 208 28.2 0.13 | 263 27.5 0.11 |  | 315 27.0 0.12 |  | 323 26.8 0.34
| TC | [5 empty] | 350 |  |  | 336 |  | 311 |  |  | 285 |  |  | 260 |  |  | 365 |  | 351 |  | 326 | 300 |  | 281 |  |  |  | 377 |  | 362 |  | 336 | 310 |  | 298 |  | 386 | 370 | 343 |  | 317 |  | 312
105 | SHC kW BF | [5 empty] | 144 30.5 0.00 |  |  | 165 30.2 0.17 |  | 199 29.8 0.08 |  |  | 231 29.6 0.06 |  |  | 257 29.9 0.09 |  |  | 152 31.0 0.13 |  | 179 30.7 0.12 |  | 220 30.2 0.09 | 260 29.9 0.07 |  | 281 29.8 0.20 |  |  |  | 161 31.4 0.17 |  | 191 31.0 0.12 |  | 239 30.5 0.10 | 285 30.3 0.09 |  | 298 30.0 0.29 |  | 170 31.7 0.15 | 203 31.3 0.12 | 257 30.7 0.11 |  | 307 30.5 0.12 |  | 312 30.3 0.36
| TC | [5 empty] | 338 |  |  | 323 |  | 297 |  |  | 272 |  |  | 247 |  |  | 351 |  | 337 |  | 310 | 285 |  | 269 |  |  |  | 362 |  | 346 |  | 320 | 294 |  | 285 |  | 370 | 353 | 326 |  | 302 |  | 299
115 | SHC kW BF | [5 empty] | 138 34.1 0.00 |  |  | 160 33.9 0.14 |  | 193 33.7 0.07 |  |  | 225 33.9 0.06 |  |  | 246 34.8 0.12 |  |  | 148 34.5 0.20 |  | 173 34.4 0.11 |  | 214 34.1 0.08 | 253 34.1 0.07 |  | 269 34.5 0.23 |  |  |  | 156 35.0 0.15 |  | 186 34.7 0.11 |  | 233 34.3 0.10 | 278 34.5 0.10 |  | 285 34.4 0.32 |  | 164 35.3 0.14 | 197 35.0 0.12 | 251 34.5 0.11 |  | 295 34.5 0.15 |  | 299 34.5 0.39
48/50 030 (30 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 12000 | [13 empty] | 13500 | [10 empty] | 15000
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC | [5 empty] | 437 |  |  | 417 |  | 385 |  |  | 356 |  |  | 350 |  |  | 444 |  | 423 |  | 391 | 361 |  | 360 |  |  |  | 449 |  | 428 |  | 396 | 370 |  | 369
75 | SHC kW BF | [5 empty] | 191 24.2 0.18 |  |  | 229 23.6 0.14 |  | 289 22.7 0.13 |  |  | 343 21.9 0.14 |  |  | 350 21.8 0.37 |  |  | 199 24.3 0.18 |  | 240 23.8 0.15 |  | 306 22.9 0.14 | 358 22.1 0.19 |  | 360 22.1 0.43 |  |  |  | 206 24.5 0.18 |  | 250 23.9 0.15 |  | 323 23.0 0.15 | 370 22.3 0.24 |  | 369 22.3 0.47
| TC | [5 empty] | 421 |  |  | 402 |  | 373 |  |  | 348 |  |  | 343 |  |  | 427 |  | 407 |  | 378 | 353 |  | 353 |  |  |  | 432 |  | 412 |  | 382 | 362 |  | 361
85 | SHC kW BF | [5 empty] | 186 26.4 0.17 |  |  | 223 25.8 0.14 |  | 284 25.0 0.12 |  |  | 338 24.3 0.15 |  |  | 343 24.2 0.39 |  |  | 193 26.5 0.17 |  | 234 26.0 0.14 |  | 301 25.1 0.14 | 351 24.4 0.20 |  | 353 24.4 0.44 |  |  |  | 200 26.6 0.17 |  | 245 26.1 0.15 |  | 318 25.2 0.15 | 362 24.7 0.26 |  | 361 24.7 0.48
| TC | [5 empty] | 406 |  |  | 389 |  | 362 |  |  | 337 |  |  | 334 |  |  | 411 |  | 395 |  | 367 | 344 |  | 344 |  |  |  | 416 |  | 399 |  | 370 | 352 |  | 352
95 | SHC kW BF | [5 empty] | 181 28.9 0.16 |  |  | 219 28.4 0.13 |  | 280 27.7 0.12 |  |  | 331 27.1 0.16 |  |  | 334 27.0 0.40 |  |  | 188 29.0 0.16 |  | 230 28.6 0.14 |  | 297 27.8 0.13 | 344 27.3 0.22 |  | 344 27.3 0.45 |  |  |  | 195 29.2 0.17 |  | 240 28.7 0.16 |  | 313 27.9 0.14 | 352 27.5 0.28 |  | 352 27.5 0.50
| TC | [5 empty] | 392 |  |  | 376 |  | 348 |  |  | 324 |  |  | 323 |  |  | 397 |  | 380 |  | 353 | 333 |  | 332 |  |  |  | 402 |  | 384 |  | 356 | 340 |  | 340
105 | SHC kW BF | [5 empty] | 177 31.9 0.15 |  |  | 214 31.5 0.13 |  | 275 30.9 0.12 |  |  | 321 30.4 0.18 |  |  | 323 30.5 0.42 |  |  | 184 32.1 0.16 |  | 225 31.7 0.14 |  | 292 31.0 0.13 | 329 30.6 0.26 |  | 332 30.7 0.47 |  |  |  | 191 32.3 0.16 |  | 235 31.8 0.16 |  | 308 31.2 0.15 | 340 30.9 0.30 |  | 340 30.9 0.51
| TC | [5 empty] | 375 |  |  | 359 |  | 331 |  |  | 311 |  |  | 309 |  |  | 380 |  | 363 |  | 335 | 318 |  | 318 |  |  |  | 384 |  | 366 |  | 338 | 325 |  | 325
115 | SHC kW BF | [5 empty] | 172 35.5 0.15 |  |  | 209 35.2 0.13 |  | 268 34.6 0.12 |  |  | 304 34.3 0.23 |  |  | 309 34.5 0.45 |  |  | 179 35.7 0.15 |  | 219 35.3 0.14 |  | 285 34.8 0.13 | 318 34.7 0.27 |  | 318 34.6 0.49 |  |  |  | 185 35.9 0.16 |  | 229 35.5 0.15 |  | 301 34.9 0.15 | 325 34.8 0.33 |  | 325 34.7 0.53
Performance data (cont)
Cooling Capacities (cont) 48/50 035 (35 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 7000 | [13 empty] | 8750 | [10 empty] | 9625 | [8 empty] | 10500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 437 |  |  | 419 |  | 387 |  |  | 358 |  |  | 332 |  |  | 459 |  | 439 |  | 407 | 377 |  | 352 |  |  |  | 466 |  | 446 |  | 414 | 384 |  | 361 |  | 472 | 453 | 420 |  | 389 |  | 370
75 | SHC kW BF | [5 empty] | 177 27.0 0.00 |  |  | 200 26.3 0.00 |  | 242 25.3 0.11 |  |  | 281 24.4 0.08 |  |  | 318 23.8 0.08 |  |  | 183 27.7 0.00 |  | 216 27.0 0.18 |  | 266 25.9 0.11 | 313 24.9 0.10 |  | 343 24.2 0.18 |  |  |  | 190 27.9 0.00 |  | 224 27.2 0.16 |  | 277 26.1 0.12 | 328 25.1 0.10 |  | 361 24.5 0.20 |  | 195 28.1 0.14 | 231 27.4 0.16 | 288 26.3 0.12 |  | 343 25.3 0.11 |  | 370 24.7 0.24
| TC | [5 empty] | 424 |  |  | 406 |  | 377 |  |  | 350 |  |  | 323 |  |  | 444 |  | 424 |  | 395 | 368 |  | 344 |  |  |  | 450 |  | 432 |  | 402 | 375 |  | 353 |  | 456 | 438 | 408 |  | 380 |  | 363
85 | SHC kW BF | [5 empty] | 172 29.5 0.00 |  |  | 196 28.8 0.00 |  | 237 27.8 0.10 |  |  | 277 27.0 0.08 |  |  | 313 26.6 0.08 |  |  | 180 30.1 0.00 |  | 211 29.4 0.16 |  | 261 28.4 0.11 | 309 27.5 0.09 |  | 339 26.9 0.18 |  |  |  | 185 30.4 0.00 |  | 218 29.7 0.15 |  | 272 28.6 0.12 | 325 27.7 0.10 |  | 353 27.2 0.21 |  | 190 30.6 0.25 | 225 29.9 0.15 | 283 28.8 0.12 |  | 339 27.9 0.11 |  | 363 27.4 0.26
| TC | [5 empty] | 409 |  |  | 394 |  | 368 |  |  | 340 |  |  | 311 |  |  | 427 |  | 411 |  | 384 | 357 |  | 333 |  |  |  | 433 |  | 418 |  | 391 | 363 |  | 344 |  | 438 | 423 | 397 |  | 369 |  | 353
95 | SHC kW BF | [5 empty] | 166 32.3 0.00 |  |  | 191 31.7 0.10 |  | 233 30.9 0.10 |  |  | 272 30.3 0.08 |  |  | 304 30.0 0.09 |  |  | 175 32.9 0.00 |  | 206 32.3 0.15 |  | 256 31.4 0.10 | 304 30.7 0.09 |  | 333 30.4 0.18 |  |  |  | 179 33.2 0.27 |  | 214 32.5 0.14 |  | 267 31.6 0.11 | 319 30.9 0.10 |  | 344 30.6 0.23 |  | 184 33.4 0.21 | 220 32.7 0.14 | 278 31.8 0.12 |  | 334 31.1 0.11 |  | 353 30.8 0.28
| TC | [5 empty] | 398 |  |  | 382 |  | 355 |  |  | 327 |  |  | 298 |  |  | 413 |  | 399 |  | 371 | 343 |  | 321 |  |  |  | 419 |  | 405 |  | 377 | 349 |  | 332 |  | 425 | 410 | 382 |  | 354 |  | 341
105 | SHC kW BF | [5 empty] | 161 35.7 0.00 |  |  | 187 35.2 0.18 |  | 228 34.6 0.09 |  |  | 265 34.2 0.08 |  |  | 295 34.4 0.11 |  |  | 170 36.3 0.14 |  | 202 35.8 0.14 |  | 251 35.1 0.10 | 297 34.6 0.09 |  | 321 34.4 0.21 |  |  |  | 175 36.5 0.21 |  | 209 36.0 0.13 |  | 262 35.3 0.11 | 313 34.8 0.10 |  | 332 34.6 0.26 |  | 180 36.7 0.19 | 216 36.2 0.13 | 272 35.4 0.12 |  | 326 35.1 0.11 |  | 341 34.8 0.30
| TC | [5 empty] | 383 |  |  | 367 |  | 339 |  |  | 311 |  |  | 284 |  |  | 397 |  | 382 |  | 354 | 326 |  | 308 |  |  |  | 403 |  | 388 |  | 359 | 332 |  | 318 |  | 408 | 393 | 364 |  | 336 |  | 327
115 | SHC kW BF | [5 empty] | 154 39.6 0.00 |  |  | 181 39.3 0.15 |  | 221 38.9 0.09 |  |  | 258 39.1 0.07 |  |  | 283 39.9 0.14 |  |  | 165 40.2 0.22 |  | 196 39.9 0.13 |  | 243 39.4 0.10 | 290 39.3 0.09 |  | 308 39.7 0.24 |  |  |  | 170 40.5 0.18 |  | 203 40.1 0.13 |  | 254 39.6 0.11 | 304 39.5 0.10 |  | 318 39.6 0.29 |  | 175 40.7 0.17 | 210 40.3 0.13 | 265 39.7 0.11 |  | 318 39.8 0.11 |  | 327 39.7 0.33
48/50 035 (35 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 12225 | [13 empty] | 14000 | [10 empty] | 15000
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC | [5 empty] | 482 |  |  | 463 |  | 430 |  |  | 400 |  |  | 386 |  |  | 491 |  | 471 |  | 438 | 406 |  | 400 |  |  |  | 496 |  | 475 |  | 442 | 411 |  | 406
75 | SHC kW BF | [5 empty] | 204 28.5 0.22 |  |  | 244 27.8 0.16 |  | 309 26.6 0.13 |  |  | 371 25.6 0.13 |  |  | 386 25.2 0.32 |  |  | 213 28.8 0.20 |  | 257 28.0 0.16 |  | 329 26.9 0.14 | 391 25.8 0.16 |  | 400 25.6 0.39 |  |  |  | 218 28.9 0.20 |  | 264 28.2 0.16 |  | 340 27.0 0.15 | 400 26.0 0.19 |  | 406 25.8 0.42
| TC | [5 empty] | 466 |  |  | 447 |  | 417 |  |  | 390 |  |  | 379 |  |  | 475 |  | 455 |  | 424 | 397 |  | 392 |  |  |  | 478 |  | 458 |  | 427 | 400 |  | 398
85 | SHC kW BF | [5 empty] | 199 30.9 0.20 |  |  | 239 30.2 0.15 |  | 303 29.1 0.13 |  |  | 366 28.2 0.13 |  |  | 379 27.9 0.34 |  |  | 208 31.2 0.19 |  | 252 30.5 0.16 |  | 323 29.3 0.14 | 386 28.4 0.17 |  | 392 28.3 0.40 |  |  |  | 212 31.4 0.19 |  | 259 30.6 0.16 |  | 334 29.4 0.15 | 395 28.5 0.20 |  | 398 28.5 0.43
| TC | [5 empty] | 449 |  |  | 433 |  | 405 |  |  | 378 |  |  | 369 |  |  | 456 |  | 439 |  | 412 | 385 |  | 382 |  |  |  | 460 |  | 442 |  | 415 | 389 |  | 388
95 | SHC kW BF | [5 empty] | 193 33.7 0.18 |  |  | 234 33.1 0.14 |  | 299 32.1 0.13 |  |  | 360 31.4 0.13 |  |  | 369 31.1 0.35 |  |  | 202 34.0 0.18 |  | 246 33.3 0.15 |  | 319 32.3 0.14 | 377 31.6 0.17 |  | 382 31.5 0.42 |  |  |  | 206 34.1 0.18 |  | 253 33.4 0.16 |  | 330 32.4 0.15 | 381 31.6 0.23 |  | 388 31.6 0.45
| TC | [5 empty] | 435 |  |  | 418 |  | 390 |  |  | 362 |  |  | 356 |  |  | 441 |  | 425 |  | 396 | 370 |  | 369 |  |  |  | 444 |  | 428 |  | 399 | 376 |  | 375
105 | SHC kW BF | [5 empty] | 189 37.1 0.17 |  |  | 229 36.5 0.14 |  | 293 35.7 0.13 |  |  | 348 35.2 0.15 |  |  | 356 35.1 0.38 |  |  | 197 37.4 0.17 |  | 241 36.8 0.15 |  | 313 35.9 0.14 | 363 35.3 0.21 |  | 369 35.3 0.44 |  |  |  | 202 37.5 0.17 |  | 249 36.9 0.15 |  | 324 36.0 0.15 | 368 35.4 0.26 |  | 375 35.5 0.46
| TC | [5 empty] | 417 |  |  | 400 |  | 371 |  |  | 345 |  |  | 341 |  |  | 423 |  | 406 |  | 377 | 355 |  | 353 |  |  |  | 425 |  | 409 |  | 380 | 359 |  | 359
115 | SHC kW BF | [5 empty] | 183 41.1 0.16 |  |  | 223 40.6 0.14 |  | 286 39.9 0.13 |  |  | 337 39.8 0.17 |  |  | 341 39.8 0.40 |  |  | 192 41.4 0.16 |  | 235 40.9 0.14 |  | 305 40.1 0.14 | 347 39.6 0.25 |  | 353 39.9 0.46 |  |  |  | 196 41.5 0.17 |  | 242 41.0 0.15 |  | 317 40.2 0.15 | 359 40.0 0.26 |  | 359 40.0 0.49
Performance data (cont)
Cooling Capacities (cont) 48/50 040 (40 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 8000 | [13 empty] | 10000 | [10 empty] | 12000 | [8 empty] | 14000
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 477 |  |  | 458 |  | 420 |  |  | 383 |  |  | 348 |  |  | 501 |  | 483 |  | 443 | 405 |  | 367 |  |  |  | 519 |  | 497 |  | 458 | 420 |  | 383 |  | 533 | 508 | 469 |  | 431 |  | 397
75 | SHC kW BF | [5 empty] | 195 24.8 0.00 |  |  | 210 24.5 0.00 |  | 246 24.0 0.00 |  |  | 282 23.6 0.33 |  |  | 317 23.3 0.26 |  |  | 206 25.3 0.00 |  | 220 24.9 0.00 |  | 271 24.3 0.39 | 313 23.9 0.31 |  | 348 23.5 0.31 |  |  |  | 207 25.7 0.00 |  | 237 25.2 0.00 |  | 290 24.6 0.36 | 339 24.1 0.32 |  | 371 23.5 0.37 |  | 210 26.0 0.00 | 249 25.5 0.22 | 307 24.8 0.36 |  | 364 24.2 0.33 |  | 397 23.9 0.39
| TC | [5 empty] | 467 |  |  | 447 |  | 409 |  |  | 371 |  |  | 338 |  |  | 490 |  | 471 |  | 431 | 393 |  | 356 |  |  |  | 507 |  | 485 |  | 446 | 407 |  | 370 |  | 520 | 497 | 457 |  | 419 |  | 388
85 | SHC kW BF | [5 empty] | 191 27.5 0.00 |  |  | 206 27.3 0.00 |  | 241 26.9 0.00 |  |  | 277 26.6 0.31 |  |  | 311 26.3 0.26 |  |  | 202 28.0 0.00 |  | 218 27.7 0.00 |  | 266 27.1 0.36 | 308 26.8 0.30 |  | 340 26.5 0.31 |  |  |  | 203 28.3 0.00 |  | 233 27.9 0.00 |  | 286 27.4 0.35 | 334 27.0 0.31 |  | 367 26.6 0.35 |  | 205 28.6 0.00 | 246 28.2 0.44 | 302 27.6 0.36 |  | 358 27.1 0.33 |  | 387 26.8 0.41
| TC | [5 empty] | 455 |  |  | 435 |  | 397 |  |  | 359 |  |  | 326 |  |  | 479 |  | 457 |  | 418 | 379 |  | 341 |  |  |  | 494 |  | 470 |  | 431 | 393 |  | 360 |  | 504 | 482 | 441 |  | 404 |  | 377
95 | SHC kW BF | [5 empty] | 186 30.7 0.00 |  |  | 199 30.6 0.00 |  | 237 30.2 0.00 |  |  | 271 30.0 0.30 |  |  | 304 29.8 0.26 |  |  | 190 31.2 0.00 |  | 214 30.9 0.00 |  | 261 30.5 0.34 | 302 30.2 0.29 |  | 334 29.9 0.30 |  |  |  | 194 31.5 0.00 |  | 229 31.1 0.00 |  | 280 30.7 0.34 | 328 30.4 0.31 |  | 356 30.0 0.37 |  | 203 31.7 0.00 | 241 31.3 0.42 | 296 30.9 0.35 |  | 352 30.5 0.32 |  | 377 30.3 0.42
| TC | [5 empty] | 440 |  |  | 420 |  | 382 |  |  | 346 |  |  | 312 |  |  | 463 |  | 440 |  | 401 | 364 |  | 330 |  |  |  | 477 |  | 453 |  | 413 | 377 |  | 347 |  | 486 | 464 | 424 |  | 387 |  | 364
105 | SHC kW BF | [5 empty] | 180 34.4 0.00 |  |  | 192 34.4 0.00 |  | 231 34.1 0.42 |  |  | 265 34.2 0.29 |  |  | 295 34.5 0.27 |  |  | 184 34.9 0.00 |  | 209 34.7 0.00 |  | 254 34.4 0.32 | 295 34.2 0.29 |  | 321 34.3 0.33 |  |  |  | 189 35.1 0.00 |  | 223 34.9 0.44 |  | 269 34.6 0.33 | 321 34.3 0.30 |  | 347 34.4 0.38 |  | 199 35.3 0.00 | 235 35.1 0.39 | 289 34.8 0.35 |  | 345 34.3 0.32 |  | 364 34.4 0.44
| TC | [5 empty] | 422 |  |  | 406 |  | 365 |  |  | 330 |  |  | 297 |  |  | 443 |  | 420 |  | 383 | 347 |  | 315 |  |  |  | 456 |  | 434 |  | 395 | 359 |  | 334 |  | 466 | 443 | 404 |  | 368 |  | 350
115 | SHC kW BF | [5 empty] | 174 38.7 0.00 |  |  | 187 38.4 0.00 |  | 224 38.9 0.34 |  |  | 257 39.4 0.28 |  |  | 283 40.3 0.29 |  |  | 178 39.1 0.00 |  | 203 39.0 0.00 |  | 247 38.9 0.31 | 288 39.2 0.28 |  | 312 39.8 0.34 |  |  |  | 183 39.3 0.00 |  | 217 39.2 0.39 |  | 265 39.1 0.32 | 314 39.1 0.29 |  | 334 39.6 0.40 |  | 193 39.5 0.00 | 229 39.4 0.37 | 282 39.1 0.34 |  | 336 39.2 0.32 |  | 350 39.4 0.46
48/50 040 (40 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 16000 | [13 empty] | 18000 | [10 empty] | 20000
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC | [5 empty] | 542 |  |  | 518 |  | 478 |  |  | 440 |  |  | 413 |  |  | 549 |  | 525 |  | 486 | 447 |  | 426 |  |  |  | 557 |  | 531 |  | 491 | 453 |  | 438
75 | SHC kW BF | [5 empty] | 220 26.2 0.00 |  |  | 261 25.7 0.43 |  | 324 24.9 0.37 |  |  | 386 24.4 0.35 |  |  | 413 24.0 0.45 |  |  | 228 26.4 0.00 |  | 272 25.8 0.41 |  | 339 25.1 0.38 | 406 24.5 0.37 |  | 426 24.2 0.49 |  |  |  | 237 26.5 0.49 |  | 282 25.9 0.41 |  | 354 25.2 0.39 | 424 24.6 0.39 |  | 438 24.4 0.53
| TC | [5 empty] | 527 |  |  | 505 |  | 465 |  |  | 427 |  |  | 402 |  |  | 535 |  | 512 |  | 472 | 434 |  | 416 |  |  |  | 541 |  | 518 |  | 478 | 440 |  | 427
85 | SHC kW BF | [5 empty] | 216 28.8 0.00 |  |  | 257 28.3 0.41 |  | 319 27.7 0.37 |  |  | 380 27.3 0.35 |  |  | 402 27.0 0.46 |  |  | 223 29.0 0.26 |  | 268 28.5 0.41 |  | 334 27.8 0.38 | 401 27.3 0.36 |  | 416 27.1 0.50 |  |  |  | 232 29.1 0.48 |  | 277 28.6 0.41 |  | 350 27.9 0.39 | 415 27.5 0.39 |  | 427 27.3 0.54
| TC | [5 empty] | 512 |  |  | 490 |  | 450 |  |  | 412 |  |  | 391 |  |  | 520 |  | 496 |  | 456 | 419 |  | 404 |  |  |  | 527 |  | 502 |  | 462 | 423 |  | 415
95 | SHC kW BF | [5 empty] | 212 31.8 0.00 |  |  | 252 31.5 0.40 |  | 313 31.0 0.36 |  |  | 373 30.6 0.35 |  |  | 391 30.4 0.47 |  |  | 219 32.1 0.53 |  | 263 31.6 0.40 |  | 329 31.1 0.37 | 391 30.7 0.37 |  | 404 30.5 0.52 |  |  |  | 227 32.2 0.46 |  | 272 31.8 0.40 |  | 344 31.2 0.38 | 402 30.8 0.39 |  | 415 30.7 0.55
| TC | [5 empty] | 494 |  |  | 471 |  | 432 |  |  | 394 |  |  | 378 |  |  | 502 |  | 477 |  | 438 | 401 |  | 391 |  |  |  | 507 |  | 483 |  | 443 | 405 |  | 400
105 | SHC kW BF | [5 empty] | 208 35.4 0.50 |  |  | 246 35.2 0.38 |  | 306 34.8 0.35 |  |  | 365 34.5 0.35 |  |  | 378 34.4 0.49 |  |  | 215 35.7 0.46 |  | 258 35.2 0.37 |  | 322 34.9 0.37 | 378 34.5 0.38 |  | 391 34.4 0.53 |  |  |  | 222 35.8 0.44 |  | 267 35.5 0.39 |  | 337 35.0 0.38 | 395 34.6 0.40 |  | 400 34.6 0.57
| TC | [5 empty] | 473 |  |  | 450 |  | 411 |  |  | 375 |  |  | 365 |  |  | 480 |  | 456 |  | 417 | 382 |  | 375 |  |  |  | 484 |  | 461 |  | 421 | 389 |  | 384
115 | SHC kW BF | [5 empty] | 201 39.7 0.47 |  |  | 240 39.6 0.37 |  | 299 39.1 0.35 |  |  | 354 39.3 0.35 |  |  | 365 39.0 0.51 |  |  | 209 39.9 0.42 |  | 250 39.7 0.37 |  | 314 39.2 0.36 | 363 39.3 0.40 |  | 375 39.3 0.55 |  |  |  | 215 40.0 0.42 |  | 260 39.7 0.38 |  | 330 39.2 0.37 | 373 39.0 0.45 |  | 384 39.3 0.59
Performance data (cont)
Cooling Capacities (cont) 48/50 040 (40 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 8000 | [14 empty] | 10000 | [10 empty] | 12000 | [8 empty] | 14000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC |  |  |  |  | 502 |  |  |  | 480 |  | 439 |  |  | 404 |  |  | 369 |  |  | 531 |  | 504 |  | 464 | 427 |  | 395 |  |  |  | 550 |  | 523 |  | 480 | 443 |  | 417 |  | 565 | 537 | 493 |  | 456 |  | 436
75 | SHC kW BF |  |  |  |  | 207 25.5 0.00 |  |  |  | 227 25.0 0.00 |  | 273 24.2 0.15 |  |  | 315 23.5 0.11 |  |  | 352 23.1 0.12 |  |  | 217 26.1 0.00 |  | 249 25.5 0.22 |  | 301 24.6 0.14 | 353 24.0 0.12 |  | 389 23.5 0.18 |  |  |  | 228 26.4 0.15 |  | 266 25.9 0.19 |  | 326 25.0 0.15 | 387 24.2 0.13 |  | 417 23.8 0.25 |  | 239 26.7 0.12 | 282 26.1 0.18 | 349 25.2 0.16 |  | 417 24.5 0.16 |  | 436 24.2 0.33
| TC |  |  |  |  | 490 |  |  |  | 469 |  | 432 |  |  | 397 |  |  | 360 |  |  | 518 |  | 493 |  | 456 | 419 |  | 386 |  |  |  | 536 |  | 511 |  | 472 | 435 |  | 410 |  | 551 | 523 | 484 |  | 447 |  | 429
85 | SHC kW BF |  |  |  |  | 202 28.0 0.00 |  |  |  | 224 27.6 0.00 |  | 270 26.9 0.15 |  |  | 312 26.4 0.11 |  |  | 346 26.1 0.12 |  |  | 211 28.6 0.00 |  | 245 28.1 0.21 |  | 297 27.3 0.14 | 349 26.8 0.12 |  | 382 26.3 0.19 |  |  |  | 223 29.0 0.13 |  | 262 28.4 0.18 |  | 322 27.6 0.15 | 383 27.0 0.13 |  | 410 26.7 0.27 |  | 235 29.3 0.26 | 277 28.6 0.17 | 346 27.9 0.16 |  | 412 27.3 0.16 |  | 429 27.0 0.34
| TC |  |  |  |  | 480 |  |  |  | 461 |  | 423 |  |  | 387 |  |  | 350 |  |  | 507 |  | 484 |  | 445 | 408 |  | 375 |  |  |  | 526 |  | 501 |  | 461 | 423 |  | 400 |  | 539 | 514 | 472 |  | 434 |  | 419
95 | SHC kW BF |  |  |  |  | 197 31.1 0.00 |  |  |  | 221 30.7 0.00 |  | 265 30.3 0.15 |  |  | 307 30.0 0.11 |  |  | 339 29.9 0.13 |  |  | 208 31.7 0.00 |  | 242 31.2 0.20 |  | 293 30.6 0.14 | 344 30.3 0.12 |  | 375 30.1 0.19 |  |  |  | 220 32.1 0.12 |  | 258 31.6 0.17 |  | 318 31.0 0.15 | 377 30.6 0.13 |  | 400 30.3 0.28 |  | 231 32.4 0.24 | 273 31.9 0.18 | 341 31.2 0.16 |  | 404 30.8 0.16 |  | 419 30.6 0.36
| TC |  |  |  |  | 470 |  |  |  | 448 |  | 409 |  |  | 372 |  |  | 336 |  |  | 495 |  | 471 |  | 431 | 393 |  | 363 |  |  |  | 512 |  | 485 |  | 445 | 406 |  | 387 |  | 524 | 498 | 455 |  | 416 |  | 406
105 | SHC kW BF |  |  |  |  | 193 34.8 0.00 |  |  |  | 217 34.6 0.12 |  | 259 34.5 0.14 |  |  | 300 34.5 0.10 |  |  | 329 35.7 0.14 |  |  | 203 35.5 0.00 |  | 237 35.2 0.18 |  | 287 34.8 0.13 | 337 34.7 0.11 |  | 363 35.0 0.22 |  |  |  | 216 36.0 0.11 |  | 253 35.5 0.16 |  | 312 35.1 0.14 | 369 35.0 0.13 |  | 387 35.0 0.31 |  | 226 36.4 0.22 | 267 36.0 0.18 | 336 35.2 0.15 |  | 393 35.2 0.17 |  | 406 35.1 0.38
| TC |  |  |  |  | 454 |  |  |  | 431 |  | 392 |  |  | 355 |  |  | 319 |  |  | 478 |  | 452 |  | 412 | 373 |  | 349 |  |  |  | 491 |  | 466 |  | 425 | 386 |  | 372 |  | 502 | 476 | 433 |  | 397 |  | 390
115 | SHC kW BF |  |  |  |  | 186 39.5 0.00 |  |  |  | 211 39.6 0.09 |  | 252 40.1 0.13 |  |  | 291 41.4 0.10 |  |  | 318 44.0 0.15 |  |  | 198 40.4 0.14 |  | 230 40.1 0.16 |  | 279 40.3 0.13 | 328 41.3 0.11 |  | 349 42.6 0.25 |  |  |  | 209 40.8 0.23 |  | 245 40.6 0.16 |  | 304 40.5 0.14 | 358 41.8 0.14 |  | 372 41.8 0.34 |  | 219 41.3 0.21 | 260 41.0 0.17 | 328 40.5 0.14 |  | 378 41.7 0.20 |  | 390 40.9 0.40
48/50 040 (40 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 16000 | [14 empty] | 18000 | [10 empty] | 20000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC |  |  |  |  | 577 |  |  |  | 548 |  | 503 |  |  | 463 |  |  | 453 |  |  | 585 |  | 556 |  | 511 | 474 |  | 466 |  |  |  | 593 |  | 563 |  | 517 | 481 |  | 479
75 | SHC kW BF |  |  |  |  | 250 27.0 0.24 |  |  |  | 296 26.4 0.19 |  | 372 25.4 0.17 |  |  | 438 24.7 0.19 |  |  | 453 24.5 0.39 |  |  | 259 27.2 0.23 |  | 309 26.5 0.21 |  | 393 25.6 0.19 | 458 24.9 0.23 |  | 466 24.7 0.44 |  |  |  | 268 27.3 0.23 |  | 322 26.7 0.22 |  | 413 25.7 0.20 | 475 25.0 0.27 |  | 479 25.0 0.49
| TC |  |  |  |  | 563 |  |  |  | 536 |  | 493 |  |  | 455 |  |  | 446 |  |  | 571 |  | 544 |  | 501 | 465 |  | 459 |  |  |  | 579 |  | 551 |  | 507 | 472 |  | 471
85 | SHC kW BF |  |  |  |  | 245 29.5 0.23 |  |  |  | 291 29.0 0.20 |  | 368 28.1 0.17 |  |  | 433 27.4 0.20 |  |  | 446 27.3 0.40 |  |  | 255 29.7 0.22 |  | 304 29.1 0.21 |  | 389 28.3 0.19 | 452 27.7 0.24 |  | 459 27.5 0.45 |  |  |  | 264 29.9 0.22 |  | 317 29.3 0.22 |  | 410 28.4 0.20 | 472 27.7 0.27 |  | 471 27.7 0.49
| TC |  |  |  |  | 550 |  |  |  | 524 |  | 481 |  |  | 444 |  |  | 436 |  |  | 559 |  | 532 |  | 487 | 453 |  | 449 |  |  |  | 566 |  | 538 |  | 494 | 461 |  | 461
95 | SHC kW BF |  |  |  |  | 241 32.7 0.22 |  |  |  | 287 32.2 0.19 |  | 363 31.4 0.17 |  |  | 421 31.0 0.22 |  |  | 436 30.8 0.42 |  |  | 251 32.9 0.22 |  | 300 32.4 0.20 |  | 388 31.4 0.16 | 441 31.1 0.26 |  | 449 31.0 0.46 |  |  |  | 260 33.1 0.22 |  | 313 32.5 0.21 |  | 404 31.7 0.20 | 461 31.2 0.29 |  | 461 31.2 0.51
| TC |  |  |  |  | 533 |  |  |  | 507 |  | 462 |  |  | 427 |  |  | 422 |  |  | 541 |  | 514 |  | 470 | 437 |  | 435 |  |  |  | 547 |  | 520 |  | 476 | 447 |  | 446
105 | SHC kW BF |  |  |  |  | 236 36.7 0.21 |  |  |  | 281 36.3 0.19 |  | 360 35.3 0.15 |  |  | 414 35.4 0.22 |  |  | 422 35.0 0.43 |  |  | 245 37.0 0.21 |  | 294 36.5 0.20 |  | 380 35.6 0.17 | 431 35.2 0.27 |  | 435 35.3 0.48 |  |  |  | 254 37.2 0.21 |  | 307 36.6 0.21 |  | 396 35.9 0.20 | 446 35.5 0.31 |  | 446 35.5 0.52
| TC |  |  |  |  | 511 |  |  |  | 484 |  | 441 |  |  | 407 |  |  | 405 |  |  | 517 |  | 491 |  | 447 | 418 |  | 417 |  |  |  | 523 |  | 496 |  | 452 | 428 |  | 428
115 | SHC kW BF |  |  |  |  | 229 41.8 0.20 |  |  |  | 273 41.4 0.19 |  | 350 40.7 0.16 |  |  | 401 41.6 0.23 |  |  | 405 41.4 0.46 |  |  | 238 42.1 0.20 |  | 286 41.6 0.20 |  | 371 41.0 0.17 | 416 41.2 0.29 |  | 417 41.3 0.50 |  |  |  | 245 42.7 0.22 |  | 299 41.8 0.21 |  | 392 41.0 0.18 | 428 41.3 0.34 |  | 428 41.3 0.54
Performance data (cont)
Cooling Capacities (cont) 48/50 050 (50 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 10000 | [13 empty] | 12500 | [10 empty] | 15000 | [8 empty] | 17500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 633 |  |  | 606 |  | 558 |  |  | 512 |  |  | 466 |  |  | 665 |  | 635 |  | 587 | 541 |  | 494 |  |  |  | 690 |  | 656 |  | 607 | 561 |  | 520 |  | 707 | 672 | 622 |  | 576 |  | 541
75 | SHC kW BF | [5 empty] | 260 33.8 0.00 |  |  | 281 33.3 0.00 |  | 338 32.5 0.09 |  |  | 389 32.1 0.18 |  |  | 436 31.9 0.15 |  |  | 273 34.3 0.00 |  | 303 33.8 0.00 |  | 369 33.0 0.23 | 431 32.5 0.19 |  | 480 32.2 0.21 |  |  |  | 277 34.7 0.00 |  | 323 34.2 0.13 |  | 398 33.3 0.23 | 470 32.8 0.20 |  | 518 32.4 0.28 |  | 288 35.0 0.00 | 341 34.4 0.30 | 423 33.6 0.24 |  | 506 33.0 0.21 |  | 541 32.6 0.33
| TC | [5 empty] | 614 |  |  | 592 |  | 543 |  |  | 495 |  |  | 450 |  |  | 646 |  | 618 |  | 571 | 523 |  | 477 |  |  |  | 667 |  | 637 |  | 590 | 542 |  | 501 |  | 681 | 650 | 605 |  | 557 |  | 526
85 | SHC kW BF | [5 empty] | 251 37.4 0.00 |  |  | 273 37.0 0.00 |  | 331 36.4 0.26 |  |  | 381 36.2 0.17 |  |  | 427 36.0 0.15 |  |  | 257 38.0 0.00 |  | 297 37.5 0.00 |  | 363 36.8 0.22 | 423 36.5 0.18 |  | 461 36.0 0.24 |  |  |  | 268 38.4 0.00 |  | 316 37.8 0.32 |  | 391 37.1 0.22 | 461 36.7 0.20 |  | 500 36.5 0.29 |  | 282 38.7 0.20 | 333 38.1 0.28 | 417 37.4 0.23 |  | 497 36.9 0.21 |  | 526 36.7 0.35
| TC | [5 empty] | 598 |  |  | 573 |  | 525 |  |  | 476 |  |  | 428 |  |  | 628 |  | 600 |  | 551 | 502 |  | 458 |  |  |  | 646 |  | 618 |  | 570 | 520 |  | 484 |  | 658 | 632 | 583 |  | 534 |  | 508
95 | SHC kW BF | [5 empty] | 245 41.8 0.00 |  |  | 268 41.4 0.00 |  | 323 41.2 0.23 |  |  | 371 41.1 0.16 |  |  | 413 41.2 0.16 |  |  | 251 42.4 0.00 |  | 291 42.0 0.14 |  | 355 41.5 0.21 | 413 41.4 0.18 |  | 458 41.3 0.24 |  |  |  | 262 42.7 0.00 |  | 310 42.3 0.29 |  | 383 41.8 0.21 | 452 41.6 0.19 |  | 484 41.4 0.31 |  | 275 43.0 0.17 | 327 42.6 0.27 | 408 42.1 0.23 |  | 487 41.8 0.21 |  | 508 41.7 0.38
| TC | [5 empty] | 578 |  |  | 552 |  | 502 |  |  | 454 |  |  | 408 |  |  | 606 |  | 577 |  | 527 | 478 |  | 436 |  |  |  | 623 |  | 594 |  | 544 | 495 |  | 465 |  | 635 | 608 | 557 |  | 508 |  | 488
105 | SHC kW BF | [5 empty] | 237 47.1 0.00 |  |  | 261 46.9 0.00 |  | 314 46.8 0.20 |  |  | 360 47.2 0.16 |  |  | 398 48.7 0.17 |  |  | 243 47.6 0.00 |  | 283 47.4 0.12 |  | 345 47.2 0.20 | 402 47.3 0.17 |  | 436 48.2 0.25 |  |  |  | 256 47.9 0.00 |  | 302 47.6 0.27 |  | 372 47.5 0.21 | 441 47.3 0.19 |  | 465 47.8 0.33 |  | 268 48.1 0.14 | 319 47.9 0.26 | 398 47.7 0.22 |  | 474 47.5 0.22 |  | 488 47.6 0.40
| TC | [5 empty] | 553 |  |  | 526 |  | 477 |  |  | 429 |  |  | 382 |  |  | 580 |  | 549 |  | 500 | 451 |  | 416 |  |  |  | 595 |  | 566 |  | 516 | 467 |  | 443 |  | 607 | 578 | 528 |  | 479 |  | 466
115 | SHC kW BF | [5 empty] | 227 53.2 0.00 |  |  | 253 53.3 0.00 |  | 303 53.8 0.18 |  |  | 349 55.5 0.15 |  |  | 379 58.0 0.20 |  |  | 234 53.7 0.00 |  | 273 53.6 0.27 |  | 334 53.9 0.19 | 390 55.3 0.17 |  | 416 56.9 0.28 |  |  |  | 248 53.9 0.16 |  | 292 53.9 0.25 |  | 361 54.1 0.20 | 428 55.3 0.19 |  | 443 56.0 0.36 |  | 259 54.1 0.33 | 309 54.1 0.24 | 387 54.1 0.22 |  | 455 55.0 0.23 |  | 466 55.5 0.43
48/50 050 (50 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
20,000 Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57
| TC | [5 empty] | 719 |  |  | 685 |  | 633 |  |  | 587 |  |  | 562
75 | SHC kW BF | [5 empty] | 301 35.2 0.17 |  |  | 357 34.7 0.29 |  | 448 33.8 0.25 |  |  | 539 33.2 0.23 |  |  | 562 32.9 0.40
| TC | [5 empty] | 693 |  |  | 662 |  | 616 |  |  | 568 |  |  | 547
85 | SHC kW BF | [5 empty] | 293 38.9 0.15 |  |  | 350 38.3 0.28 |  | 441 37.6 0.24 |  |  | 529 37.1 0.24 |  |  | 547 36.9 0.41
| TC | [5 empty] | 668 |  |  | 643 |  | 594 |  |  | 543 |  |  | 528
95 | SHC kW BF | [5 empty] | 286 43.2 0.35 |  |  | 343 42.8 0.27 |  | 433 42.2 0.24 |  |  | 515 41.9 0.24 |  |  | 528 41.8 0.43
| TC | [5 empty] | 645 |  |  | 618 |  | 568 |  |  | 519 |  |  | 507
105 | SHC kW BF | [5 empty] | 279 48.3 0.32 |  |  | 335 48.1 0.26 |  | 423 47.8 0.24 |  |  | 498 47.5 0.26 |  |  | 507 47.5 0.45
| TC | [5 empty] | 615 |  |  | 587 |  | 537 |  |  | 491 |  |  | 484
115 | SHC kW BF | [5 empty] | 270 54.2 0.30 |  |  | 325 54.3 0.25 |  | 412 54.1 0.23 |  |  | 480 55.0 0.28 |  |  | 484 55.1 0.48
Performance data (cont)
Cooling Capacities (cont) 48/50 050 (50 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 10000 | [12 empty] | 12500 | [10 empty] | 15000 | [9 empty] | 17500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  | 75 |  |  | 72 |  | 67 | 62 |  | 57 |  |  | 75 |  |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 638 |  |  | 609 |  | 560 |  |  | 517 |  |  | 476 |  | 673 |  |  | 643 |  | 590 | 546 |  | 503 |  |  | 698 |  |  | 665 |  | 611 | 566 |  | 527 |  | 715 | 677 | 627 |  | 581 |  | 552
75 | SHC kW BF | [5 empty] | 264 33.7 0.00 |  |  | 289 33.3 0.00 |  | 343 32.4 0.20 |  |  | 397 31.7 0.14 |  |  | 446 31.3 0.13 |  | 274 34.3 0.00 |  |  | 312 33.8 0.13 |  | 376 32.9 0.19 | 441 32.2 0.15 |  | 490 31.6 0.18 |  |  | 284 34.8 0.00 |  |  | 332 34.2 0.25 |  | 406 33.3 0.19 | 481 32.5 0.17 |  | 526 31.9 0.25 |  | 298 35.1 0.16 | 351 34.5 0.22 | 434 33.5 0.20 |  | 518 32.8 0.18 |  | 552 32.3 0.32
| TC | [5 empty] | 622 |  |  | 595 |  | 549 |  |  | 505 |  |  | 461 |  | 654 |  |  | 624 |  | 578 | 533 |  | 489 |  |  | 678 |  |  | 646 |  | 598 | 552 |  | 515 |  | 695 | 661 | 613 |  | 567 |  | 540
85 | SHC kW BF | [5 empty] | 256 37.4 0.00 |  |  | 280 36.9 0.00 |  | 338 36.1 0.19 |  |  | 391 35.5 0.14 |  |  | 437 35.4 0.13 |  | 266 38.0 0.00 |  |  | 305 37.4 0.12 |  | 371 36.6 0.18 | 435 36.0 0.15 |  | 481 35.6 0.19 |  |  | 277 38.4 0.00 |  |  | 326 37.8 0.23 |  | 400 37.0 0.19 | 475 36.3 0.16 |  | 515 35.9 0.26 |  | 292 38.8 0.14 | 345 38.1 0.22 | 428 37.2 0.20 |  | 511 36.6 0.19 |  | 540 36.2 0.34
| TC | [5 empty] | 606 |  |  | 582 |  | 535 |  |  | 488 |  |  | 440 |  | 638 |  |  | 610 |  | 562 | 515 |  | 472 |  |  | 658 |  |  | 630 |  | 582 | 534 |  | 500 |  | 677 | 646 | 596 |  | 548 |  | 525
95 | SHC kW BF | [5 empty] | 248 41.6 0.00 |  |  | 277 41.3 0.00 |  | 332 40.7 0.18 |  |  | 383 40.5 0.13 |  |  | 424 40.4 0.13 |  | 257 42.3 0.00 |  |  | 300 41.9 0.11 |  | 364 41.3 0.17 | 426 40.9 0.15 |  | 465 40.5 0.22 |  |  | 273 42.7 0.00 |  |  | 320 42.3 0.23 |  | 394 41.6 0.18 | 466 41.3 0.16 |  | 500 41.0 0.28 |  | 287 43.2 0.31 | 339 42.7 0.21 | 421 41.9 0.19 |  | 502 41.6 0.19 |  | 525 41.2 0.36
| TC | [5 empty] | 591 |  |  | 564 |  | 515 |  |  | 467 |  |  | 423 |  | 621 |  |  | 591 |  | 541 | 492 |  | 452 |  |  | 641 |  |  | 611 |  | 560 | 510 |  | 481 |  | 656 | 625 | 573 |  | 523 |  | 505
105 | SHC kW BF | [5 empty] | 242 46.9 0.00 |  |  | 271 46.8 0.00 |  | 323 46.6 0.16 |  |  | 372 46.6 0.13 |  |  | 407 47.6 0.17 |  | 253 47.7 0.00 |  |  | 294 47.5 0.23 |  | 355 47.1 0.17 | 416 46.9 0.14 |  | 451 47.4 0.23 |  |  | 267 48.3 0.16 |  |  | 313 48.0 0.21 |  | 384 47.5 0.18 | 455 47.2 0.16 |  | 481 47.3 0.31 |  | 280 48.7 0.28 | 331 48.3 0.21 | 412 47.7 0.19 |  | 488 47.5 0.19 |  | 505 47.3 0.38
| TC | [5 empty] | 569 |  |  | 540 |  | 490 |  |  | 443 |  |  | 400 |  | 596 |  |  | 565 |  | 514 | 466 |  | 431 |  |  | 614 |  |  | 583 |  | 531 | 479 |  | 459 |  | 627 | 595 | 542 |  | 493 |  | 483
115 | SHC kW BF | [5 empty] | 234 53.4 0.00 |  |  | 262 53.5 0.12 |  | 312 54.2 0.15 |  |  | 360 55.9 0.12 |  |  | 394 59.3 0.17 |  | 244 54.2 0.00 |  |  | 284 54.1 0.21 |  | 344 54.4 0.16 | 403 55.9 0.14 |  | 431 57.2 0.26 |  |  | 259 54.9 0.13 |  |  | 304 54.6 0.20 |  | 374 54.7 0.17 | 442 55.7 0.16 |  | 459 56.4 0.34 |  | 271 55.4 0.25 | 321 55.1 0.21 | 402 54.6 0.18 |  | 470 55.8 0.20 |  | 483 56.0 0.41
48/50 050 (50 TON) HIGH- CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm 20,000 Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57
| TC | [5 empty] | 730 |  |  | 695 |  | 639 |  |  | 593 |  |  | 572
75 | SHC kW BF | [5 empty] | 311 35.3 0.31 |  |  | 368 34.7 0.24 |  | 460 33.8 0.21 |  |  | 549 33.0 0.21 |  |  | 572 32.6 0.39
| TC | [5 empty] | 707 |  |  | 675 |  | 624 |  |  | 578 |  |  | 561
85 | SHC kW BF | [5 empty] | 305 39.0 0.28 |  |  | 361 38.4 0.23 |  | 454 37.5 0.21 |  |  | 541 36.8 0.22 |  |  | 561 36.5 0.40
| TC | [5 empty] | 690 |  |  | 658 |  | 606 |  |  | 558 |  |  | 545
Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
95 | SHC kW BF | [5 empty] | 299 43.5 0.27 |  |  | 356 42.9 0.23 |  | 450 42.1 0.20 |  |  | 524 41.5 0.23 |  |  | 545 41.4 0.42
| TC | [5 empty] | 668 |  |  | 635 |  | 582 |  |  | 534 |  |  | 525
105 | SHC kW BF | [5 empty] | 292 49.1 0.25 |  |  | 348 48.6 0.22 |  | 440 47.8 0.20 |  |  | 514 47.7 0.23 |  |  | 525 47.4 0.44
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
| TC | [5 empty] | 638 |  |  | 606 |  | 553 |  |  | 507 |  |  | 502
Correction Factor
115 | SHC kW BF | [5 empty] | 283 55.8 0.24 |  |  | 337 55.4 0.22 |  | 428 55.2 0.20 |  |  | 496 56.0 0.25 |  |  | 502 55.7 0.46
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 055 (55 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 11000 | [13 empty] | 13750 | [10 empty] | 16500 | [8 empty] | 19250
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 685 |  |  | 654 |  | 604 |  |  | 558 |  |  | 510 |  |  | 722 |  | 686 |  | 636 | 588 |  | 538 |  |  |  | 744 |  | 709 |  | 656 | 609 |  | 572 |  | 761 | 726 | 672 |  | 625 |  | 598
75 | SHC kW BF | [5 empty] | 281 37.2 0.00 |  |  | 311 36.5 0.00 |  | 375 35.5 0.15 |  |  | 434 34.8 0.11 |  |  | 486 34.6 0.11 |  |  | 292 37.9 0.00 |  | 338 37.2 0.24 |  | 412 36.1 0.14 | 485 35.3 0.12 |  | 525 34.6 0.18 |  |  |  | 307 38.4 0.00 |  | 361 37.6 0.19 |  | 446 36.5 0.15 | 531 35.7 0.13 |  | 572 35.2 0.25 |  | 322 38.8 0.29 | 381 38.0 0.19 | 477 36.9 0.16 |  | 572 36.1 0.15 |  | 598 35.6 0.33
| TC | [5 empty] | 663 |  |  | 636 |  | 588 |  |  | 540 |  |  | 491 |  |  | 697 |  | 665 |  | 618 | 570 |  | 519 |  |  |  | 717 |  | 687 |  | 638 | 589 |  | 556 |  | 732 | 702 | 653 |  | 604 |  | 582
85 | SHC kW BF | [5 empty] | 271 41.0 0.00 |  |  | 304 40.5 0.00 |  | 368 39.7 0.15 |  |  | 425 39.3 0.11 |  |  | 474 39.2 0.11 |  |  | 281 41.8 0.00 |  | 330 41.1 0.21 |  | 405 40.3 0.14 | 476 39.8 0.12 |  | 506 39.1 0.19 |  |  |  | 299 42.3 0.13 |  | 352 41.6 0.19 |  | 438 40.7 0.15 | 522 40.1 0.13 |  | 556 39.7 0.28 |  | 313 42.6 0.26 | 373 41.9 0.18 | 470 41.0 0.16 |  | 562 40.5 0.16 |  | 582 40.0 0.35
| TC | [5 empty] | 646 |  |  | 619 |  | 570 |  |  | 520 |  |  | 466 |  |  | 676 |  | 647 |  | 598 | 547 |  | 504 |  |  |  | 694 |  | 667 |  | 617 | 566 |  | 537 |  | 708 | 681 | 631 |  | 580 |  | 563
95 | SHC kW BF | [5 empty] | 264 45.7 0.00 |  |  | 298 45.3 0.00 |  | 359 44.9 0.14 |  |  | 415 44.7 0.11 |  |  | 451 45.6 0.12 |  |  | 276 46.4 0.00 |  | 323 45.9 0.19 |  | 396 45.4 0.13 | 466 45.2 0.11 |  | 504 45.2 0.21 |  |  |  | 292 46.8 0.11 |  | 346 46.4 0.18 |  | 430 45.8 0.14 | 505 45.5 0.13 |  | 537 45.2 0.30 |  | 306 47.1 0.23 | 366 46.7 0.18 | 461 46.1 0.16 |  | 549 45.9 0.16 |  | 563 45.4 0.37
| TC | [5 empty] | 626 |  |  | 597 |  | 546 |  |  | 495 |  |  | 443 |  |  | 654 |  | 624 |  | 572 | 522 |  | 485 |  |  |  | 671 |  | 642 |  | 590 | 539 |  | 516 |  | 686 | 655 | 604 |  | 552 |  | 542
105 | SHC kW BF | [5 empty] | 256 51.3 0.00 |  |  | 290 51.2 0.10 |  | 349 51.1 0.13 |  |  | 404 52.1 0.10 |  |  | 443 54.4 0.13 |  |  | 269 51.9 0.00 |  | 315 51.7 0.18 |  | 386 51.6 0.13 | 454 52.0 0.11 |  | 485 53.0 0.24 |  |  |  | 284 52.4 0.26 |  | 337 52.2 0.17 |  | 419 51.9 0.14 | 497 52.5 0.14 |  | 516 52.5 0.33 |  | 299 52.8 0.22 | 357 52.5 0.17 | 451 52.2 0.15 |  | 533 52.5 0.17 |  | 542 51.9 0.39
| TC | [5 empty] | 602 |  |  | 570 |  | 519 |  |  | 468 |  |  | — |  |  | 626 |  | 595 |  | 544 | 492 |  | — |  |  |  | 643 |  | 612 |  | 561 | 508 |  | 494 |  | 657 | 625 | 573 |  | 521 |  | 517
115 | SHC kW BF | [5 empty] | 243 58.1 0.00 |  |  | 280 58.2 0.22 |  | 337 59.6 0.12 |  |  | 390 62.5 0.10 |  |  | — — — |  |  | 261 58.5 0.12 |  | 305 58.6 0.16 |  | 374 59.7 0.12 | 440 62.3 0.11 |  | — — — |  |  |  | 275 58.9 0.23 |  | 326 59.0 0.16 |  | 407 59.8 0.14 | 481 62.2 0.14 |  | 494 61.0 0.36 |  | 289 59.5 0.20 | 347 59.3 0.16 | 439 59.9 0.15 |  | 513 61.3 0.19 |  | 517 61.1 0.42
48/50 055 (55 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 22000 | [13 empty] | 24750
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC | [5 empty] | 773 |  |  | 738 |  | 684 |  |  | 636 |  |  | 620 |  |  | 785 |  | 748 |  | 693 | 642 |  | 638
75 | SHC kW BF | [5 empty] | 335 39.1 0.25 |  |  | 401 38.3 0.19 |  | 508 37.1 0.17 |  |  | 607 36.3 0.18 |  |  | 620 35.9 0.39 |  |  | 348 39.3 0.24 |  | 419 38.5 0.20 |  | 536 37.3 0.18 | 627 36.3 0.23 |  | 638 36.3 0.45
| TC | [5 empty] | 745 |  |  | 712 |  | 664 |  |  | 615 |  |  | 604 |  |  | 755 |  | 721 |  | 673 | 623 |  | 621
85 | SHC kW BF | [5 empty] | 326 42.9 0.23 |  |  | 392 42.2 0.19 |  | 500 41.3 0.17 |  |  | 594 40.6 0.19 |  |  | 604 40.2 0.41 |  |  | 339 43.2 0.23 |  | 411 42.3 0.19 |  | 529 41.5 0.18 | 614 40.6 0.23 |  | 621 40.6 0.46
| TC | [5 empty] | 722 |  |  | 691 |  | 642 |  |  | 592 |  |  | 585 |  |  | 732 |  | 701 |  | 650 | 602 |  | 602
95 | SHC kW BF | [5 empty] | 319 47.5 0.22 |  |  | 385 46.9 0.18 |  | 491 46.3 0.17 |  |  | 579 45.9 0.20 |  |  | 585 45.6 0.43 |  |  | 331 47.8 0.22 |  | 402 47.2 0.20 |  | 520 46.5 0.18 | 595 45.8 0.25 |  | 602 45.9 0.48
| TC | [5 empty] | 697 |  |  | 664 |  | 614 |  |  | 565 |  |  | 562 |  |  | 706 |  | 674 |  | 622 | 578 |  | 578
105 | SHC kW BF | [5 empty] | 311 53.1 0.21 |  |  | 377 52.6 0.17 |  | 481 52.4 0.17 |  |  | 555 51.9 0.23 |  |  | 562 52.0 0.45 |  |  | 324 53.4 0.21 |  | 393 53.0 0.19 |  | 509 52.6 0.18 | 572 52.1 0.28 |  | 578 52.1 0.50
| TC | [5 empty] | 666 |  |  | 633 |  | 582 |  |  | 539 |  |  | 536 |  |  | 674 |  | 640 |  | 590 | 554 |  | 553
115 | SHC kW BF | [5 empty] | 302 59.8 0.20 |  |  | 365 59.1 0.17 |  | 469 59.9 0.16 |  |  | 532 60.4 0.26 |  |  | 536 60.8 0.48 |  |  | 314 60.0 0.20 |  | 383 59.2 0.18 |  | 497 60.0 0.18 | 550 60.4 0.32 |  | 553 60.5 0.52
LEGEND | [28 empty] | 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm Wet-bulb temperature corresponding to enthalpy of air leaving evaporator coil (hlwb).
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
Interpolation is permissible.
hlwb |  |  |  |  | – total capacity (Btuh) 4.5 x cfm | [11 empty] | Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor
fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 055 (55 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 11000 | [13 empty] | 13750 | [10 empty] | 16500 | [8 empty] | 19250
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 693 |  |  | 657 |  | 606 |  |  | 556 |  |  | 513 |  |  | 731 |  | 694 |  | 639 | 586 |  | 542 |  |  |  | 757 |  | 719 |  | 661 | 609 |  | 575 |  | 776 | 737 | 678 |  | 625 |  | 602
75 | SHC kW BF | [5 empty] | 285 37.2 0.00 |  |  | 318 36.5 0.08 |  | 379 35.4 0.12 |  |  | 438 34.4 0.09 |  |  | 494 33.6 0.09 |  |  | 299 38.0 0.00 |  | 346 37.2 0.15 |  | 419 36.1 0.11 | 490 35.0 0.09 |  | 542 34.2 0.15 |  |  |  | 318 38.5 0.08 |  | 369 37.7 0.15 |  | 454 36.5 0.12 | 539 35.5 0.11 |  | 575 34.9 0.25 |  | 334 38.8 0.18 | 390 38.1 0.16 | 488 36.9 0.13 |  | 581 35.8 0.13 |  | 602 35.4 0.33
| TC | [5 empty] | 675 |  |  | 641 |  | 591 |  |  | 544 |  |  | 501 |  |  | 709 |  | 674 |  | 623 | 573 |  | 532 |  |  |  | 735 |  | 699 |  | 645 | 596 |  | 565 |  | 757 | 717 | 661 |  | 609 |  | 591
85 | SHC kW BF | [5 empty] | 277 41.1 0.00 |  |  | 312 40.4 0.08 |  | 372 39.3 0.11 |  |  | 432 38.5 0.08 |  |  | 486 37.9 0.09 |  |  | 292 41.9 0.00 |  | 339 41.1 0.14 |  | 412 40.0 0.11 | 484 39.0 0.09 |  | 532 38.3 0.17 |  |  |  | 311 42.4 0.21 |  | 361 41.6 0.15 |  | 447 40.5 0.12 | 532 39.6 0.11 |  | 565 38.9 0.27 |  | 327 42.9 0.17 | 383 42.0 0.15 | 481 40.9 0.13 |  | 575 39.8 0.13 |  | 591 39.5 0.34
| TC | [5 empty] | 659 |  |  | 627 |  | 578 |  |  | 530 |  |  | 487 |  |  | 692 |  | 659 |  | 608 | 558 |  | 519 |  |  |  | 719 |  | 682 |  | 628 | 576 |  | 551 |  | 737 | 699 | 644 |  | 592 |  | 577
95 | SHC kW BF | [5 empty] | 271 45.7 0.00 |  |  | 306 45.1 0.06 |  | 367 44.3 0.11 |  |  | 425 43.5 0.08 |  |  | 480 43.4 0.11 |  |  | 287 46.5 0.11 |  | 333 45.9 0.13 |  | 405 44.9 0.11 | 476 44.1 0.10 |  | 519 43.5 0.19 |  |  |  | 305 47.4 0.19 |  | 355 46.5 0.14 |  | 440 45.5 0.12 | 525 44.5 0.10 |  | 551 44.1 0.28 |  | 321 48.0 0.17 | 376 47.0 0.15 | 474 45.9 0.13 |  | 561 44.9 0.15 |  | 577 44.6 0.36
| TC | [5 empty] | 641 |  |  | 610 |  | 558 |  |  | 507 |  |  | 463 |  |  | 674 |  | 639 |  | 586 | 534 |  | 503 |  |  |  | 696 |  | 659 |  | 605 | 555 |  | 533 |  | 711 | 674 | 619 |  | 568 |  | 558
105 | SHC kW BF | [5 empty] | 264 51.6 0.00 |  |  | 299 51.1 0.18 |  | 358 50.6 0.10 |  |  | 415 49.7 0.07 |  |  | 458 50.7 0.12 |  |  | 281 52.9 0.09 |  | 325 51.9 0.12 |  | 396 51.3 0.10 | 467 50.2 0.08 |  | 503 49.3 0.21 |  |  |  | 298 54.0 0.17 |  | 347 52.9 0.14 |  | 431 51.9 0.11 | 509 51.2 0.12 |  | 533 50.7 0.31 |  | 312 54.8 0.15 | 367 53.5 0.15 | 464 52.3 0.13 |  | 548 51.4 0.15 |  | 558 51.1 0.38
| TC | [5 empty] | 615 |  |  | 581 |  | 528 |  |  | 476 |  |  | 436 |  |  | 644 |  | 609 |  | 554 | 502 |  | 475 |  |  |  | 663 |  | 627 |  | 572 | 519 |  | 505 |  | — | 641 | 585 |  | 537 |  | 529
115 | SHC kW BF | [5 empty] | 252 60.1 0.00 |  |  | 289 59.8 0.14 |  | 345 59.8 0.09 |  |  | 400 58.7 0.07 |  |  | 433 60.6 0.16 |  |  | 271 62.3 0.20 |  | 314 61.0 0.12 |  | 383 60.6 0.10 | 450 61.0 0.09 |  | 475 60.4 0.26 |  |  |  | 287 64.3 0.15 |  | 335 62.2 0.13 |  | 418 61.4 0.11 | 494 61.3 0.12 |  | 505 60.6 0.34 |  | — — — | 356 63.6 0.14 | 451 61.9 0.13 |  | 523 60.8 0.18 |  | 529 61.1 0.41
48/50 055 (55 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 22000 | [13 empty] | 24750
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC | [5 empty] | 791 |  |  | 751 |  | 691 |  |  | 637 |  |  | 625 |  |  | 805 |  | 762 |  | 702 | 650 |  | 644
75 | SHC kW BF | [5 empty] | 348 39.1 0.17 |  |  | 410 38.3 0.16 |  | 520 37.2 0.14 |  |  | 614 36.1 0.17 |  |  | 625 35.8 0.39 |  |  | 359 39.4 0.20 |  | 429 38.6 0.17 |  | 550 37.4 0.15 | 639 36.4 0.22 |  | 644 36.2 0.44
| TC | [5 empty] | 771 |  |  | 730 |  | 673 |  |  | 621 |  |  | 612 |  |  | 787 |  | 743 |  | 684 | 634 |  | 632
85 | SHC kW BF | [5 empty] | 341 43.2 0.17 |  |  | 403 42.4 0.16 |  | 512 41.2 0.14 |  |  | 606 40.1 0.17 |  |  | 612 39.9 0.40 |  |  | 354 43.7 0.19 |  | 422 42.7 0.18 |  | 543 41.4 0.15 | 620 40.4 0.24 |  | 632 40.3 0.45
| TC | [5 empty] | 753 |  |  | 713 |  | 655 |  |  | 606 |  |  | 598 |  |  | 764 |  | 723 |  | 665 | 617 |  | 616
95 | SHC kW BF | [5 empty] | 333 48.8 0.18 |  |  | 396 47.6 0.17 |  | 505 46.2 0.14 |  |  | 589 45.2 0.20 |  |  | 598 45.0 0.42 |  |  | 346 49.3 0.19 |  | 416 47.8 0.17 |  | 536 46.5 0.15 | 610 45.3 0.25 |  | 616 45.4 0.47
| TC | [5 empty] | 724 |  |  | 686 |  | 630 |  |  | 584 |  |  | 578 |  |  | 733 |  | 696 |  | 638 | 596 |  | 596
105 | SHC kW BF | [5 empty] | 324 56.4 0.18 |  |  | 387 54.1 0.16 |  | 495 52.7 0.14 |  |  | 570 51.4 0.22 |  |  | 578 51.6 0.44 |  |  | 336 57.1 0.18 |  | 406 54.8 0.17 |  | 525 52.9 0.15 | 596 52.0 0.26 |  | 596 51.9 0.48
| TC | [5 empty] | — |  |  | 652 |  | 595 |  |  | 551 |  |  | 550 |  |  | — |  | — |  | 603 | 570 |  | 567
115 | SHC kW BF | [5 empty] | — — — |  |  | 375 65.0 0.16 |  | 482 62.3 0.14 |  |  | 548 61.3 0.24 |  |  | 550 61.4 0.46 |  |  | — — — |  | — — — |  | 511 63.1 0.16 | 561 61.2 0.31 |  | 567 61.7 0.51
LEGEND | [28 empty] | 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible.
hlwb |  |  |  |  | – total capacity (Btuh) 4.5 x cfm | [11 empty] | Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor
fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 060 (60 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 12000 | [14 empty] | 15000 | [10 empty] | 18000 | [8 empty] | 21000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  | 62 |  |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC |  |  |  |  | 751 |  |  |  | 718 |  | 664 |  | 611 |  |  |  | 558 |  |  | 791 |  | 752 |  | 698 | 644 |  | 589 |  |  |  | 816 |  | 777 |  | 721 | 667 |  | 624 |  | 834 | 796 | 739 |  | 684 |  | 653
75 | SHC kW BF |  |  |  |  | 308 43.7 0.00 |  |  |  | 339 42.9 0.00 |  | 410 41.6 0.17 |  | 474 40.7 0.12 |  |  |  | 530 40.4 0.11 |  |  | 318 44.7 0.00 |  | 368 43.7 0.10 |  | 449 42.4 0.16 | 528 41.4 0.13 |  | 575 40.5 0.18 |  |  |  | 335 45.4 0.00 |  | 393 44.4 0.22 |  | 485 43.0 0.16 | 577 41.9 0.14 |  | 624 41.2 0.26 |  | 351 45.9 0.12 | 415 44.8 0.21 | 520 43.4 0.17 |  | 621 42.4 0.17 |  | 653 41.7 0.33
| TC |  |  |  |  | 730 |  |  |  | 701 |  | 647 |  | 593 |  |  |  | 539 |  |  | 765 |  | 733 |  | 679 | 625 |  | 573 |  |  |  | 787 |  | 756 |  | 701 | 647 |  | 607 |  | 803 | 773 | 718 |  | 663 |  | 636
85 | SHC kW BF |  |  |  |  | 298 48.1 0.00 |  |  |  | 334 47.4 0.00 |  | 403 46.4 0.16 |  | 465 46.0 0.12 |  |  |  | 518 46.0 0.12 |  |  | 306 49.1 0.00 |  | 361 48.2 0.25 |  | 442 47.3 0.15 | 519 46.6 0.13 |  | 558 45.7 0.21 |  |  |  | 326 49.7 0.00 |  | 385 48.9 0.20 |  | 478 47.8 0.16 | 568 47.0 0.14 |  | 607 46.6 0.27 |  | 341 50.1 0.29 | 407 49.3 0.20 | 511 48.2 0.17 |  | 611 47.5 0.17 |  | 636 47.0 0.35
| TC |  |  |  |  | 711 |  |  |  | 681 |  | 626 |  | 572 |  |  |  | 515 |  |  | 744 |  | 711 |  | 656 | 601 |  | 554 |  |  |  | 764 |  | 733 |  | 677 | 622 |  | 587 |  | 779 | 748 | 692 |  | 636 |  | 616
95 | SHC kW BF |  |  |  |  | 291 53.5 0.00 |  |  |  | 327 53.0 0.00 |  | 393 52.5 0.14 |  | 454 52.3 0.11 |  |  |  | 498 53.8 0.14 |  |  | 300 54.4 0.00 |  | 353 53.8 0.22 |  | 432 53.3 0.15 | 507 52.7 0.12 |  | 553 53.2 0.21 |  |  |  | 319 54.9 0.13 |  | 377 54.4 0.19 |  | 468 53.7 0.16 | 556 53.3 0.14 |  | 587 53.2 0.30 |  | 334 55.4 0.26 | 399 54.8 0.19 | 501 54.1 0.17 |  | 598 53.6 0.17 |  | 616 53.1 0.37
| TC |  |  |  |  | 686 |  |  |  | 655 |  | 600 |  | 546 |  |  |  | 489 |  |  | 716 |  | 683 |  | 627 | 573 |  | 531 |  |  |  | 735 |  | 703 |  | 647 | 591 |  | 564 |  | 748 | 717 | 661 |  | 605 |  | 591
105 | SHC kW BF |  |  |  |  | 281 60.0 0.00 |  |  |  | 317 59.8 0.12 |  | 382 59.8 0.13 |  | 442 61.6 0.11 |  |  |  | 484 64.9 0.14 |  |  | 293 60.8 0.00 |  | 343 60.5 0.20 |  | 420 60.5 0.14 | 495 61.6 0.12 |  | 531 63.0 0.24 |  |  |  | 310 61.3 0.30 |  | 367 61.1 0.18 |  | 456 60.8 0.15 | 541 62.3 0.15 |  | 564 62.4 0.33 |  | 324 61.6 0.23 | 388 61.4 0.19 | 489 61.1 0.17 |  | 576 62.2 0.17 |  | 591 61.8 0.39
| TC |  |  |  |  | 657 |  |  |  | 624 |  | 569 |  | — |  |  |  | — |  |  | 682 |  | 650 |  | 594 | — |  | — |  |  |  | 700 |  | 668 |  | 612 | 554 |  | — |  | 714 | 681 | 625 |  | 570 |  | 562
115 | SHC kW BF |  |  |  |  | 265 67.5 0.00 |  |  |  | 306 68.0 0.25 |  | 369 69.8 0.12 |  | — — — |  |  |  | — — — |  |  | 283 68.1 0.00 |  | 332 68.7 0.18 |  | 407 70.2 0.14 | — — — |  | — — — |  |  |  | 299 68.8 0.24 |  | 354 69.1 0.17 |  | 442 70.3 0.15 | 522 73.7 0.15 |  | — — — |  | 313 69.4 0.22 | 376 69.5 0.18 | 476 70.4 0.16 |  | 556 72.7 0.20 |  | 562 72.3 0.42
48/50 060 (60 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 24000 | [14 empty] | 27000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  | 62 |  |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC |  |  |  |  | 848 |  |  |  | 809 |  | 752 |  | 697 |  |  |  | 677 |  |  | 861 |  | 820 |  | 762 | 707 |  | 698
75 | SHC kW BF |  |  |  |  | 365 46.2 0.28 |  |  |  | 436 45.2 0.21 |  | 552 43.7 0.19 |  | 660 42.7 0.19 |  |  |  | 677 42.2 0.39 |  |  | 379 46.6 0.26 |  | 456 45.5 0.21 |  | 583 44.0 0.20 | 690 42.8 0.23 |  | 698 42.5 0.44
| TC |  |  |  |  | 816 |  |  |  | 785 |  | 730 |  | 675 |  |  |  | 660 |  |  | 829 |  | 794 |  | 740 | 686 |  | 680
85 | SHC kW BF |  |  |  |  | 356 50.4 0.25 |  |  |  | 428 49.7 0.20 |  | 544 48.5 0.18 |  | 648 47.8 0.20 |  |  |  | 660 47.2 0.41 |  |  | 369 50.8 0.25 |  | 447 49.9 0.21 |  | 575 48.8 0.19 | 669 47.7 0.25 |  | 680 47.7 0.46
| TC |  |  |  |  | 793 |  |  |  | 759 |  | 704 |  | 648 |  |  |  | 638 |  |  | 803 |  | 768 |  | 713 | 660 |  | 658
95 | SHC kW BF |  |  |  |  | 348 55.8 0.24 |  |  |  | 419 55.1 0.20 |  | 534 54.4 0.18 |  | 630 53.8 0.21 |  |  |  | 638 53.5 0.43 |  |  | 361 56.1 0.24 |  | 439 55.3 0.21 |  | 565 54.6 0.19 | 652 53.7 0.26 |  | 658 53.8 0.48
| TC |  |  |  |  | 762 |  |  |  | 728 |  | 671 |  | 620 |  |  |  | 614 |  |  | 771 |  | 736 |  | 680 | 632 |  | 632
105 | SHC kW BF |  |  |  |  | 338 62.2 0.23 |  |  |  | 408 61.7 0.20 |  | 521 61.3 0.18 |  | 605 61.2 0.24 |  |  |  | 614 61.4 0.45 |  |  | 352 62.6 0.23 |  | 427 62.1 0.21 |  | 552 61.5 0.19 | 625 61.2 0.28 |  | 632 61.5 0.50
| TC |  |  |  |  | 724 |  |  |  | 691 |  | 635 |  | 586 |  |  |  | 584 |  |  | 732 |  | 697 |  | 643 | 602 |  | 602
115 | SHC kW BF |  |  |  |  | 327 69.8 0.22 |  |  |  | 396 69.5 0.19 |  | 508 70.3 0.18 |  | 581 71.2 0.26 |  |  |  | 584 71.7 0.48 |  |  | 340 70.1 0.22 |  | 415 69.2 0.20 |  | 538 70.4 0.19 | 602 71.3 0.31 |  | 602 71.3 0.52
LEGEND | [28 empty] | Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80).
hlwb = hewb – | [5 empty] | 4.5 x cfm | [7 empty] | 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 060 (60 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 12000 | [14 empty] | 15000 | [10 empty] | 18000 | [8 empty] | 21000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
75 | TC SHC kW BF |  |  |  |  | 761 313 43.9 0.00 |  |  |  | 725 349 43.0 0.00 |  | 664 415 41.4 0.12 |  |  | 610 479 40.1 0.09 |  |  | 561 539 39.0 0.08 |  |  | 802 328 44.9 0.00 |  | 762 378 43.9 0.17 |  | 700 457 42.3 0.12 | 643 534 40.9 0.10 |  | 594 594 39.8 0.15 |  |  |  | 830 347 45.5 0.10 |  | 789 404 44.5 0.16 |  | 725 495 42.9 0.13 | 666 588 41.4 0.11 |  | 628 628 40.7 0.25 |  | 851 364 46.0 0.21 | 809 426 45.0 0.17 | 744 531 43.4 0.14 |  | 685 629 42.0 0.15 |  | 659 659 41.3 0.33
85 | TC SHC kW BF |  |  |  |  | 741 304 48.2 0.00 |  |  |  | 705 342 47.3 0.09 |  | 651 408 45.9 0.12 |  |  | 599 473 44.8 0.09 |  |  | 549 525 44.1 0.09 |  |  | 779 319 49.2 0.00 |  | 741 370 48.2 0.16 |  | 685 450 46.8 0.12 | 631 528 45.5 0.10 |  | 584 584 44.6 0.16 |  |  |  | 808 340 49.9 0.25 |  | 768 396 48.9 0.15 |  | 709 488 47.5 0.13 | 656 580 46.3 0.12 |  | 619 619 45.3 0.26 |  | 831 358 50.5 0.19 | 788 418 49.4 0.17 | 727 524 48.0 0.14 |  | 672 625 46.7 0.14 |  | 647 647 46.0 0.34
95 | TC SHC kW BF |  |  |  |  | 725 298 53.5 0.00 |  |  |  | 690 336 52.6 0.07 |  | 636 401 51.5 0.12 |  |  | 584 465 50.6 0.09 |  |  | 534 520 50.3 0.11 |  |  | 761 313 54.6 0.00 |  | 724 364 53.7 0.15 |  | 668 443 52.5 0.12 | 615 521 51.6 0.10 |  | 571 570 50.7 0.19 |  |  |  | 787 333 55.5 0.21 |  | 749 388 54.5 0.16 |  | 691 481 53.2 0.13 | 637 571 52.3 0.12 |  | 605 605 51.3 0.28 |  | 808 350 56.4 0.18 | 766 410 55.1 0.16 | 707 516 53.7 0.14 |  | 652 613 52.7 0.15 |  | 633 633 52.0 0.35
105 | TC SHC kW BF |  |  |  |  | 703 290 60.2 0.00 |  |  |  | 669 328 59.4 0.06 |  | 614 392 58.7 0.11 |  |  | 560 455 57.7 0.07 |  |  | 508 498 59.7 0.11 |  |  | 736 306 61.6 0.10 |  | 700 355 60.6 0.14 |  | 643 432 59.7 0.11 | 588 510 58.5 0.09 |  | 554 554 57.0 0.21 |  |  |  | 760 324 63.1 0.19 |  | 721 378 61.7 0.15 |  | 664 470 60.4 0.12 | 610 556 60.2 0.13 |  | 584 584 59.0 0.30 |  | 775 339 64.1 0.17 | 736 400 62.4 0.16 | 679 505 61.0 0.14 |  | 624 598 60.2 0.16 |  | 611 611 59.6 0.38
| TC |  |  |  |  | 675 |  |  |  | 639 |  | 582 |  |  | 527 |  |  | 482 |  |  | 706 |  | 668 |  | 610 | 554 |  | 523 |  |  |  | — |  | 688 |  | 630 | 574 |  | 555 |  | — | — | 644 |  | 590 |  | 582
115 | SHC kW BF |  |  |  |  | 276 70.1 0.00 |  |  |  | 316 69.7 0.15 |  | 378 69.6 0.10 |  |  | 440 68.0 0.07 |  |  | 476 71.2 0.16 |  |  | 296 72.8 0.07 |  | 343 70.9 0.13 |  | 419 70.6 0.11 | 493 71.2 0.10 |  | 523 70.6 0.25 |  |  |  | — — — |  | 366 72.6 0.15 |  | 456 71.6 0.12 | 540 71.7 0.13 |  | 555 70.8 0.34 |  | — — — | — — — | 491 72.2 0.14 |  | 573 71.6 0.18 |  | 582 71.3 0.41
48/50 060 (60 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 24000 | [14 empty] | 27000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC |  |  |  |  | 868 |  |  |  | 824 |  | 759 |  |  | 700 |  |  | 684 |  |  | 882 |  | 836 |  | 770 | 714 |  | 705
75 | SHC kW BF |  |  |  |  | 380 46.4 0.19 |  |  |  | 448 45.4 0.18 |  | 565 43.8 0.15 |  |  | 669 42.3 0.18 |  |  | 684 42.0 0.39 |  |  | 393 46.7 0.20 |  | 468 45.7 0.19 |  | 598 44.1 0.17 | 689 42.7 0.22 |  | 705 42.5 0.44
| TC |  |  |  |  | 847 |  |  |  | 803 |  | 741 |  |  | 685 |  |  | 671 |  |  | 861 |  | 814 |  | 752 | 698 |  | 692
85 | SHC kW BF |  |  |  |  | 373 51.0 0.18 |  |  |  | 440 49.9 0.17 |  | 558 48.3 0.15 |  |  | 653 47.0 0.20 |  |  | 671 46.6 0.40 |  |  | 387 51.5 0.19 |  | 460 50.2 0.18 |  | 591 48.7 0.17 | 688 47.3 0.23 |  | 692 47.2 0.45
| TC |  |  |  |  | 822 |  |  |  | 780 |  | 720 |  |  | 666 |  |  | 656 |  |  | 835 |  | 792 |  | 730 | 679 |  | 675
95 | SHC kW BF |  |  |  |  | 364 57.1 0.19 |  |  |  | 432 55.6 0.17 |  | 550 54.1 0.15 |  |  | 641 52.9 0.20 |  |  | 656 52.5 0.41 |  |  | 377 57.9 0.20 |  | 453 56.2 0.18 |  | 582 54.5 0.17 | 664 52.9 0.26 |  | 675 53.1 0.46
| TC |  |  |  |  | 789 |  |  |  | 749 |  | 690 |  |  | 639 |  |  | 633 |  |  | 798 |  | 757 |  | 699 | 653 |  | 652
105 | SHC kW BF |  |  |  |  | 353 65.4 0.18 |  |  |  | 421 63.2 0.17 |  | 538 61.4 0.15 |  |  | 628 60.4 0.21 |  |  | 633 60.1 0.43 |  |  | 365 66.8 0.19 |  | 442 63.5 0.17 |  | 570 61.7 0.16 | 648 60.5 0.27 |  | 652 60.5 0.48
| TC |  |  |  |  | — |  |  |  | — |  | 655 |  |  | 606 |  |  | 603 |  |  | — |  | — |  | 663 | 622 |  | 622
115 | SHC kW BF |  |  |  |  | — — — |  |  |  | — — — |  | 524 72.8 0.15 |  |  | 599 71.0 0.24 |  |  | 603 71.9 0.46 |  |  | — — — |  | — — — |  | 556 72.8 0.16 | 622 72.1 0.29 |  | 622 72.0 0.51
LEGEND | [28 empty] | Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80).
hlwb = hewb – | [5 empty] | 4.5 x cfm | [7 empty] | 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 070 (70 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 14000 | [13 empty] | 17500 | [10 empty] | 21000 | [8 empty] | 24500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 843 |  |  | 802 |  | 744 |  |  | 685 |  |  | 629 |  |  | 880 |  | 839 |  | 779 | 720 |  | 675 |  |  |  | 905 |  | 863 |  | 803 | 744 |  | 710 |  | 924 | 882 | 820 |  | 761 |  | 741
75 | SHC kW BF | [5 empty] | 345 46.7 0.00 |  |  | 392 45.7 0.19 |  | 472 44.2 0.09 |  |  | 549 42.9 0.07 |  |  | 604 41.9 0.11 |  |  | 363 47.7 0.00 |  | 423 46.6 0.14 |  | 520 45.0 0.10 | 614 43.7 0.08 |  | 663 42.7 0.20 |  |  |  | 384 48.4 0.21 |  | 453 47.3 0.12 |  | 564 45.6 0.11 | 672 44.3 0.10 |  | 710 43.5 0.27 |  | 402 48.9 0.17 | 479 47.7 0.13 | 606 46.1 0.12 |  | 722 44.7 0.13 |  | 741 44.2 0.35
| TC | [5 empty] | 822 |  |  | 783 |  | 726 |  |  | 667 |  |  | 612 |  |  | 857 |  | 819 |  | 759 | 700 |  | 655 |  |  |  | 880 |  | 839 |  | 782 | 722 |  | 694 |  | 900 | 860 | 798 |  | 739 |  | 724
85 | SHC kW BF | [5 empty] | 334 51.3 0.00 |  |  | 384 50.2 0.17 |  | 464 48.9 0.09 |  |  | 540 47.7 0.07 |  |  | 599 46.8 0.11 |  |  | 356 52.2 0.00 |  | 416 51.2 0.13 |  | 511 49.7 0.10 | 604 48.5 0.08 |  | 655 47.6 0.20 |  |  |  | 376 52.9 0.19 |  | 444 51.8 0.12 |  | 555 50.3 0.11 | 660 49.1 0.11 |  | 694 48.3 0.29 |  | 394 53.4 0.16 | 471 52.3 0.13 | 597 50.8 0.12 |  | 709 49.5 0.14 |  | 724 49.0 0.36
| TC | [5 empty] | 799 |  |  | 763 |  | 703 |  |  | 645 |  |  | 588 |  |  | 830 |  | 791 |  | 734 | 674 |  | 635 |  |  |  | 854 |  | 816 |  | 755 | 695 |  | 673 |  | 871 | 832 | 771 |  | 711 |  | 702
95 | SHC kW BF | [5 empty] | 326 56.7 0.00 |  |  | 376 55.8 0.15 |  | 454 54.6 0.09 |  |  | 531 53.2 0.06 |  |  | 584 52.7 0.11 |  |  | 347 57.6 0.27 |  | 406 56.5 0.11 |  | 501 55.4 0.09 | 591 54.3 0.08 |  | 635 53.4 0.22 |  |  |  | 367 58.3 0.17 |  | 435 57.4 0.12 |  | 545 55.9 0.10 | 647 54.8 0.11 |  | 673 54.1 0.31 |  | 385 58.9 0.16 | 461 57.9 0.13 | 586 56.4 0.12 |  | 688 55.1 0.15 |  | 702 54.8 0.38
| TC | [5 empty] | 771 |  |  | 734 |  | 674 |  |  | 618 |  |  | 569 |  |  | 799 |  | 764 |  | 703 | 644 |  | 612 |  |  |  | 821 |  | 784 |  | 722 | 664 |  | 648 |  | 836 | 798 | 737 |  | 679 |  | 676
105 | SHC kW BF | [5 empty] | 313 63.1 0.00 |  |  | 365 62.3 0.13 |  | 442 61.1 0.07 |  |  | 517 60.4 0.06 |  |  | 561 60.1 0.15 |  |  | 337 64.0 0.20 |  | 395 63.2 0.11 |  | 488 62.0 0.09 | 577 61.8 0.08 |  | 612 61.1 0.25 |  |  |  | 356 64.8 0.15 |  | 424 63.8 0.11 |  | 531 62.5 0.10 | 631 62.0 0.11 |  | 648 61.4 0.34 |  | 374 65.3 0.15 | 449 64.4 0.13 | 573 62.9 0.11 |  | 672 62.0 0.16 |  | 676 61.8 0.41
| TC | [5 empty] | 736 |  |  | 699 |  | 642 |  |  | 587 |  |  | 541 |  |  | 763 |  | 728 |  | 669 | 610 |  | 587 |  |  |  | 782 |  | 747 |  | 687 | 629 |  | 620 |  | 796 | 760 | 700 |  | 650 |  | 646
115 | SHC kW BF | [5 empty] | 304 70.7 0.00 |  |  | 353 69.4 0.10 |  | 427 70.3 0.08 |  |  | 503 69.2 0.05 |  |  | 541 71.0 0.17 |  |  | 325 71.7 0.16 |  | 383 71.3 0.10 |  | 474 70.8 0.09 | 560 71.4 0.09 |  | 587 70.3 0.28 |  |  |  | 344 72.5 0.14 |  | 411 72.1 0.11 |  | 517 71.4 0.10 | 602 71.1 0.14 |  | 620 71.0 0.37 |  | 361 73.0 0.14 | 435 72.4 0.13 | 559 71.7 0.11 |  | 641 70.8 0.20 |  | 646 71.1 0.43
48/50 070 (70 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 28000 | [13 empty] | 30000
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC | [5 empty] | 938 |  |  | 897 |  | 834 |  |  | 774 |  |  | 767 |  |  | 945 |  | 903 |  | 840 | 782 |  | 779
75 | SHC kW BF | [5 empty] | 419 49.3 0.17 |  |  | 504 48.1 0.15 |  | 646 46.4 0.13 |  |  | 758 45.0 0.18 |  |  | 767 44.8 0.41 |  |  | 428 49.5 0.17 |  | 518 48.3 0.15 |  | 668 46.6 0.14 | 776 45.1 0.21 |  | 779 45.1 0.44
| TC | [5 empty] | 913 |  |  | 874 |  | 811 |  |  | 751 |  |  | 749 |  |  | 919 |  | 880 |  | 816 | 763 |  | 761
85 | SHC kW BF | [5 empty] | 411 53.8 0.16 |  |  | 496 52.8 0.14 |  | 637 51.1 0.13 |  |  | 745 49.7 0.18 |  |  | 749 49.6 0.43 |  |  | 420 54.0 0.16 |  | 510 52.9 0.15 |  | 659 51.3 0.14 | 756 50.0 0.23 |  | 761 49.9 0.45
| TC | [5 empty] | 883 |  |  | 845 |  | 782 |  |  | 728 |  |  | 726 |  |  | 889 |  | 850 |  | 788 | 741 |  | 738
95 | SHC kW BF | [5 empty] | 401 59.3 0.16 |  |  | 486 58.3 0.14 |  | 626 56.7 0.13 |  |  | 723 55.4 0.21 |  |  | 726 55.4 0.44 |  |  | 411 59.5 0.16 |  | 500 58.4 0.15 |  | 648 56.9 0.14 | 727 55.7 0.27 |  | 738 55.7 0.47
| TC | [5 empty] | 847 |  |  | 809 |  | 747 |  |  | 701 |  |  | 698 |  |  | 853 |  | 815 |  | 753 | 710 |  | 710
105 | SHC kW BF | [5 empty] | 390 65.7 0.15 |  |  | 474 64.7 0.14 |  | 615 63.1 0.12 |  |  | 692 62.1 0.24 |  |  | 698 62.2 0.46 |  |  | 400 65.9 0.15 |  | 488 64.9 0.14 |  | 635 63.4 0.14 | 710 62.4 0.27 |  | 710 62.4 0.49
| TC | [5 empty] | 806 |  |  | 770 |  | 710 |  |  | 673 |  |  | 668 |  |  | 811 |  | 774 |  | 714 | 680 |  | 679
115 | SHC kW BF | [5 empty] | 378 73.5 0.14 |  |  | 460 72.8 0.14 |  | 598 71.9 0.13 |  |  | 655 71.1 0.29 |  |  | 668 71.2 0.49 |  |  | 387 73.7 0.15 |  | 474 72.9 0.14 |  | 619 72.2 0.14 | 680 71.3 0.30 |  | 679 71.4 0.51
LEGEND | [28 empty] | Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm Wet-bulb temperature corresponding to enthalpy of air leaving evaporator coil (hlwb). h = h – total capacity (Btuh) 4.5 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 070 (70 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 14000 | [14 empty] | 17500 | [10 empty] | 21000 | [8 empty] | 24500
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC |  |  |  |  | 863 |  |  |  | 814 |  | 754 |  |  | 690 |  |  | 636 |  |  | 905 |  | 862 |  | 793 | 728 |  | 686 |  |  |  | 934 |  | 889 |  | 820 | 753 |  | 729 |  | 956 | 911 | 839 |  | 771 |  | 764
75 | SHC kW BF |  |  |  |  | 353 47.8 0.00 |  |  |  | 404 46.6 0.05 |  | 485 44.8 0.03 |  |  | 563 43.2 0.01 |  |  | 630 42.0 0.05 |  |  | 380 48.8 0.12 |  | 441 47.6 0.05 |  | 539 45.7 0.03 | 635 44.1 0.02 |  | 686 43.1 0.16 |  |  |  | 403 49.6 0.08 |  | 473 48.3 0.05 |  | 589 46.4 0.04 | 700 44.7 0.04 |  | 729 44.2 0.25 |  | 423 50.2 0.07 | 504 48.9 0.05 | 639 46.9 0.04 |  | 757 45.3 0.06 |  | 764 45.1 0.33
| TC |  |  |  |  | 838 |  |  |  | 797 |  | 729 |  |  | 678 |  |  | 623 |  |  | 876 |  | 834 |  | 772 | 715 |  | 673 |  |  |  | 903 |  | 861 |  | 798 | 734 |  | 714 |  | 926 | 882 | 817 |  | 753 |  | 746
85 | SHC kW BF |  |  |  |  | 345 52.1 0.00 |  |  |  | 396 50.9 0.06 |  | 475 49.1 0.02 |  |  | 556 47.7 0.02 |  |  | 621 46.4 0.05 |  |  | 370 53.2 0.10 |  | 430 51.9 0.05 |  | 530 50.1 0.03 | 628 48.7 0.03 |  | 673 47.7 0.17 |  |  |  | 392 53.9 0.07 |  | 463 52.7 0.05 |  | 581 50.9 0.03 | 692 49.2 0.04 |  | 714 48.7 0.27 |  | 413 54.5 0.07 | 494 53.3 0.05 | 630 51.4 0.04 |  | 742 49.7 0.08 |  | 746 49.6 0.35
| TC |  |  |  |  | 814 |  |  |  | 777 |  | 711 |  |  | 662 |  |  | 611 |  |  | 853 |  | 813 |  | 753 | 693 |  | 660 |  |  |  | 879 |  | 841 |  | 777 | 718 |  | 699 |  | 902 | 860 | 795 |  | 734 |  | 730
95 | SHC kW BF |  |  |  |  | 337 57.3 0.00 |  |  |  | 388 56.2 0.05 |  | 467 54.4 0.02 |  |  | 548 53.2 0.02 |  |  | 608 51.9 0.07 |  |  | 362 58.4 0.08 |  | 422 57.3 0.05 |  | 522 55.6 0.03 | 618 54.1 0.02 |  | 660 53.1 0.19 |  |  |  | 384 59.3 0.06 |  | 455 58.1 0.05 |  | 572 56.3 0.03 | 683 54.8 0.04 |  | 699 54.2 0.29 |  | 405 60.0 0.07 | 486 58.7 0.05 | 621 56.9 0.04 |  | 730 55.2 0.09 |  | 730 55.1 0.36
| TC |  |  |  |  | 791 |  |  |  | 755 |  | 691 |  |  | 640 |  |  | 593 |  |  | 828 |  | 788 |  | 728 | 667 |  | 642 |  |  |  | 852 |  | 813 |  | 750 | 691 |  | 680 |  | 871 | 831 | 766 |  | 711 |  | 709
105 | SHC kW BF |  |  |  |  | 330 63.6 0.00 |  |  |  | 379 62.6 0.05 |  | 458 60.7 0.02 |  |  | 537 59.9 0.02 |  |  | 593 58.6 0.09 |  |  | 354 64.9 0.07 |  | 413 63.7 0.04 |  | 512 62.1 0.03 | 607 60.4 0.02 |  | 642 59.8 0.21 |  |  |  | 375 65.8 0.06 |  | 445 64.7 0.04 |  | 561 63.0 0.03 | 668 61.3 0.05 |  | 680 60.8 0.31 |  | 395 66.6 0.06 | 476 65.4 0.05 | 610 63.5 0.04 |  | 702 61.6 0.13 |  | 709 61.6 0.38
| TC |  |  |  |  | 761 |  |  |  | 725 |  | 664 |  |  | 611 |  |  | 571 |  |  | 794 |  | 758 |  | 697 | 639 |  | 618 |  |  |  | 817 |  | 779 |  | 717 | 659 |  | 654 |  | 834 | 795 | 731 |  | 682 |  | 682
115 | SHC kW BF |  |  |  |  | 319 71.2 0.12 |  |  |  | 367 70.3 0.04 |  | 446 68.2 0.02 |  |  | 523 69.1 0.02 |  |  | 571 67.5 0.13 |  |  | 341 72.7 0.06 |  | 401 71.9 0.04 |  | 498 70.5 0.03 | 591 69.9 0.03 |  | 618 68.5 0.24 |  |  |  | 363 73.9 0.06 |  | 433 73.0 0.04 |  | 548 71.5 0.03 | 646 69.6 0.07 |  | 654 69.2 0.33 |  | 382 75.0 0.06 | 463 73.8 0.05 | 595 72.0 0.04 |  | 682 69.2 0.14 |  | 682 70.0 0.40
48/50 070 (70 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 28000 | [14 empty] | 30000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC |  |  |  |  | 973 |  |  |  | 926 |  | 853 |  |  | 795 |  |  | 792 |  |  | 980 |  | 934 |  | 860 | 809 |  | 806
75 | SHC kW BF |  |  |  |  | 442 50.6 0.07 |  |  |  | 534 49.3 0.06 |  | 685 47.4 0.05 |  |  | 787 45.9 0.14 |  |  | 792 45.9 0.39 |  |  | 453 50.8 0.07 |  | 551 49.5 0.06 |  | 711 47.5 0.05 | 802 46.3 0.18 |  | 806 46.2 0.42
| TC |  |  |  |  | 942 |  |  |  | 898 |  | 830 |  |  | 773 |  |  | 772 |  |  | 950 |  | 905 |  | 839 | 783 |  | 785
85 | SHC kW BF |  |  |  |  | 432 55.0 0.07 |  |  |  | 524 53.7 0.05 |  | 676 51.8 0.05 |  |  | 769 50.4 0.16 |  |  | 772 50.3 0.41 |  |  | 443 55.2 0.07 |  | 541 54.0 0.06 |  | 701 52.0 0.05 | 783 50.7 0.20 |  | 785 50.7 0.44
| TC |  |  |  |  | 918 |  |  |  | 874 |  | 808 |  |  | 753 |  |  | 756 |  |  | 924 |  | 881 |  | 815 | 766 |  | 768
95 | SHC kW BF |  |  |  |  | 424 60.5 0.07 |  |  |  | 516 59.2 0.05 |  | 667 57.3 0.05 |  |  | 753 55.7 0.17 |  |  | 756 55.8 0.42 |  |  | 435 60.7 0.07 |  | 532 59.5 0.06 |  | 692 57.6 0.05 | 766 56.1 0.21 |  | 768 56.2 0.45
| TC |  |  |  |  | 885 |  |  |  | 843 |  | 779 |  |  | 732 |  |  | 734 |  |  | 891 |  | 850 |  | 784 | 746 |  | 746
105 | SHC kW BF |  |  |  |  | 414 67.1 0.07 |  |  |  | 505 65.9 0.05 |  | 654 64.0 0.05 |  |  | 732 62.2 0.20 |  |  | 734 62.4 0.44 |  |  | 424 67.4 0.07 |  | 522 66.1 0.06 |  | 679 64.2 0.06 | 746 62.8 0.23 |  | 746 62.8 0.47
| TC |  |  |  |  | 847 |  |  |  | 806 |  | 742 |  |  | 706 |  |  | 706 |  |  | 853 |  | 812 |  | 747 | 718 |  | 717
115 | SHC kW BF |  |  |  |  | 401 75.8 0.06 |  |  |  | 492 74.5 0.05 |  | 640 72.8 0.05 |  |  | 706 70.6 0.22 |  |  | 706 70.7 0.46 |  |  | 412 76.1 0.07 |  | 509 74.9 0.05 |  | 664 72.9 0.06 | 718 71.0 0.26 |  | 717 71.0 0.49
LEGEND | [28 empty] | Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80).
hlwb = hewb – | [5 empty] | 4.5 x cfm | [6 empty] | 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 075 (75 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 14000 | [14 empty] | 17500 | [10 empty] | 21000 | [8 empty] | 24500
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC |  |  |  |  | 889 |  |  |  | 852 |  | 787 |  |  | 724 |  |  | 663 |  |  | 933 |  | 893 |  | 826 | 763 |  | 705 |  |  |  | 960 |  | 917 |  | 854 | 789 |  | 745 |  | 981 | 937 | 874 |  | 809 |  | 780
75 | SHC kW BF |  |  |  |  | 365 50.7 0.00 |  |  |  | 410 49.6 0.00 |  | 491 48.1 0.10 |  |  | 568 46.7 0.07 |  |  | 635 45.8 0.08 |  |  | 377 51.8 0.00 |  | 443 50.7 0.16 |  | 540 49.0 0.10 | 634 47.7 0.09 |  | 695 46.5 0.16 |  |  |  | 402 52.6 0.30 |  | 472 51.4 0.14 |  | 585 49.7 0.11 | 693 48.3 0.10 |  | 745 47.3 0.24 |  | 420 53.3 0.20 | 499 52.0 0.14 | 627 50.3 0.12 |  | 747 48.8 0.12 |  | 780 48.0 0.32
| TC |  |  |  |  | 869 |  |  |  | 831 |  | 766 |  |  | 703 |  |  | 641 |  |  | 909 |  | 870 |  | 803 | 740 |  | 686 |  |  |  | 935 |  | 892 |  | 829 | 765 |  | 726 |  | 957 | 910 | 848 |  | 783 |  | 760
85 | SHC kW BF |  |  |  |  | 357 55.8 0.00 |  |  |  | 402 54.9 0.00 |  | 482 53.4 0.10 |  |  | 558 52.1 0.07 |  |  | 619 51.2 0.09 |  |  | 372 57.0 0.00 |  | 435 55.9 0.15 |  | 530 54.4 0.10 | 623 53.1 0.08 |  | 679 52.0 0.18 |  |  |  | 394 57.7 0.24 |  | 463 56.5 0.13 |  | 575 55.1 0.11 | 682 53.8 0.10 |  | 726 52.9 0.26 |  | 413 58.4 0.18 | 490 57.1 0.13 | 617 55.6 0.12 |  | 734 54.2 0.13 |  | 760 53.5 0.33
| TC |  |  |  |  | 844 |  |  |  | 803 |  | 740 |  |  | 679 |  |  | 615 |  |  | 880 |  | 841 |  | 775 | 711 |  | 662 |  |  |  | 906 |  | 864 |  | 799 | 735 |  | 704 |  | 925 | 884 | 817 |  | 752 |  | 735
95 | SHC kW BF |  |  |  |  | 346 62.0 0.00 |  |  |  | 392 60.8 0.19 |  | 470 59.8 0.09 |  |  | 547 58.3 0.06 |  |  | 602 58.6 0.10 |  |  | 364 63.0 0.00 |  | 424 62.1 0.14 |  | 518 60.7 0.10 | 609 59.5 0.08 |  | 662 58.9 0.19 |  |  |  | 384 63.9 0.20 |  | 453 62.7 0.12 |  | 563 61.4 0.11 | 667 60.2 0.10 |  | 704 59.1 0.28 |  | 403 64.6 0.17 | 480 63.5 0.13 | 605 61.9 0.12 |  | 716 60.5 0.13 |  | 735 60.1 0.36
| TC |  |  |  |  | 813 |  |  |  | 773 |  | 709 |  |  | 649 |  |  | 592 |  |  | 846 |  | 806 |  | 742 | 679 |  | 637 |  |  |  | 869 |  | 828 |  | 765 | 701 |  | 678 |  | 886 | 846 | 781 |  | 717 |  | 708
105 | SHC kW BF |  |  |  |  | 331 69.2 0.00 |  |  |  | 380 68.3 0.16 |  | 457 67.4 0.08 |  |  | 532 67.1 0.06 |  |  | 582 67.2 0.13 |  |  | 353 70.3 0.00 |  | 412 69.1 0.12 |  | 504 68.6 0.09 | 593 68.7 0.08 |  | 637 68.2 0.22 |  |  |  | 372 71.1 0.17 |  | 440 69.7 0.11 |  | 549 69.1 0.10 | 650 69.2 0.11 |  | 678 68.0 0.31 |  | 390 71.8 0.16 | 467 70.7 0.13 | 591 69.6 0.12 |  | 693 69.1 0.15 |  | 708 68.7 0.38
| TC |  |  |  |  | 779 |  |  |  | 739 |  | 676 |  |  | 616 |  |  | 562 |  |  | 808 |  | 770 |  | 706 | 643 |  | 610 |  |  |  | 830 |  | 791 |  | 726 | 664 |  | 647 |  | 845 | 806 | 742 |  | 683 |  | 677
115 | SHC kW BF |  |  |  |  | 316 78.2 0.00 |  |  |  | 367 78.6 0.14 |  | 443 77.5 0.08 |  |  | 516 78.0 0.06 |  |  | 560 79.9 0.14 |  |  | 340 79.3 0.20 |  | 398 78.4 0.11 |  | 489 78.9 0.09 | 576 79.8 0.08 |  | 610 79.5 0.25 |  |  |  | 360 80.3 0.15 |  | 427 79.9 0.11 |  | 533 79.3 0.10 | 631 79.9 0.11 |  | 647 79.4 0.34 |  | 377 81.0 0.15 | 452 80.3 0.13 | 574 79.6 0.12 |  | 669 78.5 0.17 |  | 677 79.4 0.41
48/50 075 (75 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 28000 | [14 empty] | 30000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC |  |  |  |  | 1000 |  |  |  | 955 |  | 889 |  |  | 823 |  |  | 808 |  |  | 1007 |  | 964 |  | 896 | 830 |  | 822
75 | SHC kW BF |  |  |  |  | 439 53.7 0.18 |  |  |  | 525 52.5 0.15 |  | 668 50.7 0.13 |  |  | 791 49.1 0.16 |  |  | 808 48.7 0.38 |  |  | 448 53.9 0.18 |  | 539 52.7 0.15 |  | 690 50.9 0.14 | 811 49.3 0.18 |  | 822 49.1 0.41
| TC |  |  |  |  | 972 |  |  |  | 930 |  | 862 |  |  | 798 |  |  | 787 |  |  | 979 |  | 937 |  | 869 | 804 |  | 801
85 | SHC kW BF |  |  |  |  | 430 58.9 0.17 |  |  |  | 516 57.7 0.14 |  | 658 56.0 0.13 |  |  | 773 54.5 0.17 |  |  | 787 54.2 0.40 |  |  | 439 59.1 0.17 |  | 530 57.9 0.15 |  | 680 56.2 0.14 | 797 54.6 0.19 |  | 801 54.5 0.43
| TC |  |  |  |  | 939 |  |  |  | 898 |  | 831 |  |  | 766 |  |  | 762 |  |  | 946 |  | 904 |  | 837 | 777 |  | 775
95 | SHC kW BF |  |  |  |  | 420 65.0 0.16 |  |  |  | 505 64.0 0.14 |  | 645 62.3 0.13 |  |  | 757 60.8 0.17 |  |  | 762 60.6 0.42 |  |  | 429 65.2 0.16 |  | 519 64.2 0.15 |  | 667 62.4 0.14 | 771 61.0 0.21 |  | 775 61.0 0.44
| TC |  |  |  |  | 899 |  |  |  | 859 |  | 793 |  |  | 736 |  |  | 733 |  |  | 905 |  | 864 |  | 800 | 748 |  | 746
105 | SHC kW BF |  |  |  |  | 407 72.2 0.16 |  |  |  | 491 71.2 0.14 |  | 631 69.9 0.13 |  |  | 725 68.9 0.21 |  |  | 733 69.0 0.44 |  |  | 416 72.4 0.16 |  | 505 71.4 0.15 |  | 653 70.2 0.13 | 739 69.0 0.25 |  | 746 69.2 0.47
| TC |  |  |  |  | 857 |  |  |  | 818 |  | 753 |  |  | 705 |  |  | 701 |  |  | 863 |  | 823 |  | 759 | 717 |  | 713
115 | SHC kW BF |  |  |  |  | 393 81.3 0.15 |  |  |  | 477 80.8 0.14 |  | 615 80.2 0.13 |  |  | 692 79.2 0.25 |  |  | 701 79.5 0.46 |  |  | 403 81.6 0.15 |  | 491 81.0 0.14 |  | 637 80.2 0.13 | 702 79.3 0.29 |  | 713 79.5 0.49
LEGEND | [28 empty] | Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80).
hlwb = hewb – | [5 empty] | 4.5 x cfm | [6 empty] | 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 075 (75 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 14000 | [14 empty] | 17500 | [10 empty] | 21000 | [8 empty] | 24500
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC |  |  |  |  | 912 |  |  |  | 868 |  | 796 |  |  | 732 |  |  | 674 |  |  | 960 |  | 913 |  | 841 | 773 |  | 721 |  |  |  | 992 |  | 944 |  | 871 | 803 |  | 767 |  | 1016 | 967 | 892 |  | 823 |  | 805
75 | SHC kW BF |  |  |  |  | 376 51.6 0.00 |  |  |  | 425 50.4 0.09 |  | 505 48.4 0.02 |  |  | 584 46.7 0.02 |  |  | 657 45.3 0.02 |  |  | 400 52.9 0.00 |  | 461 51.5 0.06 |  | 560 49.5 0.03 | 658 47.8 0.02 |  | 721 46.5 0.12 |  |  |  | 423 53.8 0.10 |  | 493 52.4 0.05 |  | 611 50.3 0.04 | 724 48.5 0.04 |  | 767 47.7 0.22 |  | 444 54.4 0.07 | 525 53.0 0.05 | 659 50.9 0.04 |  | 785 49.1 0.05 |  | 805 48.7 0.30
| TC |  |  |  |  | 885 |  |  |  | 837 |  | 776 |  |  | 714 |  |  | 660 |  |  | 928 |  | 884 |  | 819 | 752 |  | 708 |  |  |  | 958 |  | 913 |  | 847 | 786 |  | 752 |  | 980 | 938 | 869 |  | 802 |  | 787
85 | SHC kW BF |  |  |  |  | 363 56.5 0.00 |  |  |  | 413 55.2 0.05 |  | 495 53.3 0.03 |  |  | 575 51.7 0.01 |  |  | 649 50.4 0.03 |  |  | 389 57.7 0.14 |  | 449 56.4 0.05 |  | 550 54.4 0.03 | 649 52.6 0.02 |  | 708 51.6 0.13 |  |  |  | 411 58.6 0.08 |  | 482 57.2 0.05 |  | 601 55.3 0.03 | 716 53.6 0.04 |  | 752 52.7 0.23 |  | 431 59.3 0.07 | 514 57.9 0.05 | 650 55.9 0.04 |  | 774 54.1 0.06 |  | 787 53.7 0.31
| TC |  |  |  |  | 858 |  |  |  | 809 |  | 759 |  |  | 698 |  |  | 643 |  |  | 901 |  | 861 |  | 793 | 735 |  | 693 |  |  |  | 931 |  | 889 |  | 825 | 763 |  | 735 |  | 954 | 913 | 845 |  | 777 |  | 769
95 | SHC kW BF |  |  |  |  | 352 62.2 0.00 |  |  |  | 402 60.8 0.04 |  | 487 59.3 0.03 |  |  | 567 57.7 0.02 |  |  | 636 56.5 0.04 |  |  | 379 63.5 0.11 |  | 441 62.3 0.05 |  | 540 60.3 0.03 | 643 58.8 0.01 |  | 693 57.7 0.15 |  |  |  | 402 64.5 0.07 |  | 474 63.2 0.05 |  | 592 61.3 0.03 | 705 59.7 0.04 |  | 735 58.8 0.25 |  | 423 65.3 0.07 | 505 64.0 0.05 | 641 62.0 0.04 |  | 760 60.0 0.06 |  | 769 59.8 0.33
| TC |  |  |  |  | 835 |  |  |  | 795 |  | 730 |  |  | 676 |  |  | 623 |  |  | 875 |  | 834 |  | 767 | 709 |  | 673 |  |  |  | 903 |  | 862 |  | 796 | 733 |  | 714 |  | 922 | 881 | 813 |  | 751 |  | 746
105 | SHC kW BF |  |  |  |  | 344 69.2 0.00 |  |  |  | 396 68.0 0.05 |  | 476 66.1 0.02 |  |  | 555 65.2 0.02 |  |  | 614 63.6 0.08 |  |  | 370 70.7 0.09 |  | 430 69.5 0.05 |  | 529 67.4 0.02 | 626 66.2 0.02 |  | 673 65.0 0.17 |  |  |  | 392 71.8 0.07 |  | 463 70.6 0.05 |  | 580 68.7 0.03 | 690 67.0 0.04 |  | 714 66.1 0.27 |  | 412 72.6 0.06 | 493 71.3 0.05 | 628 69.3 0.04 |  | 744 67.3 0.07 |  | 746 67.1 0.35
| TC |  |  |  |  | 804 |  |  |  | 766 |  | 701 |  |  | 645 |  |  | 596 |  |  | 840 |  | 799 |  | 735 | 677 |  | 648 |  |  |  | 865 |  | 826 |  | 760 | 699 |  | 687 |  | 884 | 843 | 777 |  | 719 |  | 718
115 | SHC kW BF |  |  |  |  | 334 77.7 0.00 |  |  |  | 384 76.8 0.05 |  | 463 74.5 0.02 |  |  | 540 75.6 0.02 |  |  | 596 74.1 0.09 |  |  | 358 79.5 0.07 |  | 418 78.3 0.04 |  | 515 76.4 0.02 | 611 75.8 0.02 |  | 648 74.9 0.21 |  |  |  | 379 80.7 0.06 |  | 450 79.8 0.04 |  | 565 78.3 0.03 | 673 76.7 0.04 |  | 687 75.8 0.30 |  | 399 82.1 0.06 | 480 80.8 0.05 | 614 79.0 0.04 |  | 709 75.3 0.12 |  | 718 76.5 0.37
48/50 075 (75 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [5 empty] | Evaporator Air Quantity — Cfm
[6 empty] | 28000 | [14 empty] | 30000
Evaporator Air — Ewb (F)
[6 empty] | 75 |  |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57
| TC |  |  |  |  | 1034 |  |  |  | 985 |  | 909 |  |  | 839 |  |  | 836 |  |  | 1042 |  | 993 |  | 916 | 853 |  | 851
75 | SHC kW BF |  |  |  |  | 463 54.9 0.08 |  |  |  | 555 53.5 0.06 |  | 707 51.4 0.05 |  |  | 833 49.6 0.09 |  |  | 836 49.5 0.36 |  |  | 473 55.2 0.08 |  | 571 53.8 0.06 |  | 733 51.6 0.05 | 849 50.0 0.13 |  | 851 49.9 0.39
| TC |  |  |  |  | 1001 |  |  |  | 955 |  | 885 |  |  | 817 |  |  | 816 |  |  | 1009 |  | 963 |  | 892 | 831 |  | 829
85 | SHC kW BF |  |  |  |  | 452 59.8 0.07 |  |  |  | 544 58.5 0.06 |  | 698 56.4 0.05 |  |  | 817 54.5 0.10 |  |  | 816 54.5 0.38 |  |  | 463 60.1 0.08 |  | 561 58.7 0.06 |  | 724 56.6 0.05 | 820 55.0 0.17 |  | 829 54.9 0.41
| TC |  |  |  |  | 973 |  |  |  | 929 |  | 859 |  |  | 799 |  |  | 797 |  |  | 981 |  | 936 |  | 867 | 812 |  | 810
95 | SHC kW BF |  |  |  |  | 443 65.9 0.07 |  |  |  | 535 64.6 0.06 |  | 687 62.5 0.05 |  |  | 796 60.6 0.13 |  |  | 797 60.6 0.39 |  |  | 453 66.2 0.07 |  | 552 64.8 0.06 |  | 713 62.8 0.05 | 806 61.0 0.18 |  | 810 61.0 0.42
| TC |  |  |  |  | 938 |  |  |  | 895 |  | 827 |  |  | 772 |  |  | 772 |  |  | 945 |  | 901 |  | 833 | 784 |  | 785
105 | SHC kW BF |  |  |  |  | 431 73.3 0.07 |  |  |  | 523 71.9 0.05 |  | 674 69.9 0.05 |  |  | 767 67.6 0.16 |  |  | 772 67.9 0.41 |  |  | 442 73.6 0.07 |  | 539 72.2 0.06 |  | 699 70.2 0.05 | 784 68.1 0.20 |  | 785 68.3 0.44
| TC |  |  |  |  | 898 |  |  |  | 856 |  | 789 |  |  | 742 |  |  | 743 |  |  | 905 |  | 862 |  | 794 | 756 |  | 755
115 | SHC kW BF |  |  |  |  | 418 83.0 0.07 |  |  |  | 510 81.6 0.05 |  | 659 80.0 0.05 |  |  | 742 76.5 0.18 |  |  | 743 77.3 0.43 |  |  | 429 83.4 0.07 |  | 526 82.0 0.06 |  | 684 80.0 0.05 | 756 77.6 0.22 |  | 755 77.7 0.46
LEGEND | [28 empty] | Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80).
hlwb = hewb – | [5 empty] | 4.5 x cfm | [6 empty] | 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 090 (90 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 18000 | [13 empty] | 22500 | [9 empty] | 27000 | [9 empty] | 31500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  | 67 | 62 |  | 57 |  |  | 75 |  |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 1118 |  |  | 1070 |  | 985 |  |  | 903 |  |  | 822 |  |  | 1173 |  | 1118 |  | 1032 | 950 |  | 884 |  |  | 1204 |  |  | 1152 |  | 1066 | 981 |  | 922 |  | 1231 | 1175 | 1090 |  | 1005 |  | 970
75 | SHC kW BF | [5 empty] | 460 61.5 0.00 |  |  | 513 60.5 0.00 |  | 614 59.0 0.13 |  |  | 709 57.8 0.10 |  |  | 790 56.7 0.11 |  |  | 474 62.6 0.00 |  | 553 61.5 0.21 |  | 674 59.9 0.13 | 790 58.6 0.11 |  | 858 57.4 0.21 |  |  | 501 63.3 0.00 |  |  | 590 62.2 0.18 |  | 729 60.6 0.14 | 863 59.2 0.13 |  | 922 58.2 0.25 |  | 525 63.9 0.25 | 624 62.8 0.17 | 781 61.1 0.15 |  | 928 59.6 0.15 |  | 970 58.9 0.34
| TC | [5 empty] | 1086 |  |  | 1037 |  | 954 |  |  | 873 |  |  | 791 |  |  | 1135 |  | 1083 |  | 998 | 917 |  | 847 |  |  | 1165 |  |  | 1112 |  | 1030 | 947 |  | 899 |  | 1187 | 1137 | 1052 |  | 970 |  | 942
85 | SHC kW BF | [5 empty] | 444 68.1 0.00 |  |  | 501 67.1 0.00 |  | 600 65.8 0.13 |  |  | 694 64.6 0.10 |  |  | 759 63.3 0.10 |  |  | 461 69.1 0.00 |  | 540 68.1 0.19 |  | 659 66.6 0.13 | 775 65.4 0.11 |  | 847 64.2 0.19 |  |  | 489 69.8 0.30 |  |  | 576 68.7 0.16 |  | 714 67.2 0.14 | 846 66.0 0.13 |  | 899 65.1 0.28 |  | 512 70.3 0.22 | 609 69.3 0.17 | 766 67.7 0.15 |  | 911 66.4 0.16 |  | 942 65.8 0.36
| TC | [5 empty] | 1050 |  |  | 1001 |  | 920 |  |  | 841 |  |  | 763 |  |  | 1093 |  | 1044 |  | 961 | 882 |  | 827 |  |  | 1122 |  |  | 1073 |  | 990 | 909 |  | 873 |  | 1144 | 1093 | 1011 |  | 930 |  | 910
95 | SHC kW BF | [5 empty] | 430 75.7 0.00 |  |  | 488 74.7 0.26 |  | 585 73.6 0.12 |  |  | 678 72.3 0.09 |  |  | 748 71.3 0.12 |  |  | 450 76.7 0.00 |  | 526 75.8 0.17 |  | 644 74.4 0.12 | 758 73.1 0.11 |  | 810 72.1 0.25 |  |  | 475 77.4 0.24 |  |  | 561 76.5 0.16 |  | 699 75.0 0.13 | 828 73.7 0.13 |  | 873 72.9 0.30 |  | 498 77.9 0.21 | 594 76.9 0.16 | 750 75.4 0.15 |  | 888 74.1 0.16 |  | 910 73.7 0.38
| TC | [5 empty] | 1010 |  |  | 961 |  | 881 |  |  | 806 |  |  | 734 |  |  | 1048 |  | 1000 |  | 919 | 842 |  | 791 |  |  | 1075 |  |  | 1026 |  | 946 | 867 |  | 839 |  | 1095 | 1046 | 965 |  | 886 |  | 874
105 | SHC kW BF | [5 empty] | 411 84.5 0.00 |  |  | 472 83.7 0.20 |  | 568 82.4 0.11 |  |  | 663 81.3 0.08 |  |  | 729 81.1 0.14 |  |  | 436 85.4 0.00 |  | 510 84.6 0.15 |  | 626 83.2 0.12 | 739 82.2 0.11 |  | 791 81.8 0.24 |  |  | 460 86.1 0.21 |  |  | 546 85.1 0.15 |  | 681 83.8 0.13 | 807 82.8 0.13 |  | 839 82.0 0.33 |  | 482 86.6 0.19 | 578 85.7 0.16 | 732 84.2 0.14 |  | 859 82.9 0.18 |  | 874 82.6 0.40
| TC | [5 empty] | 963 |  |  | 914 |  | 838 |  |  | 768 |  |  | 713 |  |  | 997 |  | 950 |  | 872 | 797 |  | 758 |  |  | 1021 |  |  | 974 |  | 896 | 821 |  | 802 |  | 1039 | 992 | 914 |  | 839 |  | 837
115 | SHC kW BF | [5 empty] | 391 94.5 0.00 |  |  | 454 93.7 0.16 |  | 550 93.5 0.10 |  |  | 647 92.2 0.08 |  |  | 693 92.2 0.20 |  |  | 420 95.3 0.24 |  | 492 94.5 0.14 |  | 607 93.9 0.11 | 718 94.0 0.11 |  | 758 93.5 0.28 |  |  | 443 96.0 0.18 |  |  | 527 95.2 0.14 |  | 661 94.2 0.13 | 784 94.2 0.14 |  | 802 93.8 0.36 |  | 465 96.5 0.18 | 560 95.6 0.15 | 712 94.5 0.14 |  | 833 94.1 0.19 |  | 837 94.0 0.43
LEGEND
48/50 VAV units only.
48/50 090 (90 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm 36,000 Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57
| TC | [5 empty] | 1251 |  |  | 1195 |  | 1109 |  |  | 1023 |  |  | 1004
75 | SHC kW BF | [5 empty] | 547 64.3 0.22 |  |  | 656 63.2 0.17 |  | 831 61.4 0.16 |  |  | 983 59.9 0.18 |  |  | 1004 59.6 0.40
[29 empty] | tlwb |  | Wet-bulb temperature corresponding to enthalpy of air leaving evaporator coil (hlwb).
| TC | [5 empty] | 1208 |  |  | 1153 |  | 1070 |  |  | 986 |  |  | 974
85 | SHC kW BF | [5 empty] | 534 70.7 0.21 |  |  | 641 69.6 0.17 |  | 816 68.1 0.16 |  |  | 962 66.7 0.19 |  |  | 974 66.4 0.42 | [10 empty] | hlwb |  | = hewb |  |  |  | – total capacity (Btuh) 4.5 x cfm
| TC | [5 empty] | 1161 |  |  | 1110 |  | 1027 |  |  | 948 |  |  | 942
Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
95 | SHC kW BF | [5 empty] | 519 78.3 0.20 |  |  | 626 77.3 0.17 |  | 800 75.8 0.16 |  |  | 929 74.4 0.22 |  |  | 942 74.3 0.44
| TC | [5 empty] | 1110 |  |  | 1061 |  | 980 |  |  | 908 |  |  | 905
105 | SHC kW BF | [5 empty] | 503 87.0 0.19 |  |  | 609 86.1 0.17 |  | 781 84.6 0.16 |  |  | 899 83.2 0.24 |  |  | 905 83.2 0.46
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
| TC | [5 empty] | 1052 |  |  | 1005 |  | 927 |  |  | 867 |  |  | 864
Correction Factor
115 | SHC kW BF | [5 empty] | 485 96.8 0.18 |  |  | 589 96.0 0.17 |  | 762 94.8 0.16 |  |  | 860 94.2 0.27 |  |  | 864 94.3 0.48
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 090 (90 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm
[7 empty] | 18000 | [12 empty] | 22500 | [10 empty] | 27000 | [9 empty] | 31500
Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57 |  | 75 |  |  | 72 |  | 67 | 62 |  | 57 |  |  | 75 |  |  | 72 |  | 67 | 62 |  | 57 |  | 75 | 72 | 67 |  | 62 |  | 57
| TC | [5 empty] | 1177 |  |  | 1117 |  | 1025 |  |  | 946 |  |  | 870 |  | 1238 |  |  | 1176 |  | 1081 | 999 |  | 929 |  |  | 1279 |  |  | 1214 |  | 1119 | 1036 |  | 984 |  | 1309 | 1246 | 1147 |  | 1061 |  | 1031
75 | SHC kW BF | [5 empty] | 486 63.2 0.00 |  |  | 546 62.0 0.13 |  | 648 60.0 0.04 |  |  | 750 58.4 0.03 |  |  | 843 57.0 0.04 |  | 512 64.6 0.00 |  |  | 591 63.2 0.08 |  | 717 61.2 0.04 | 843 59.5 0.04 |  | 921 58.1 0.13 |  |  | 542 65.4 0.13 |  |  | 633 64.1 0.06 |  | 781 62.0 0.05 | 927 60.2 0.05 |  | 984 59.2 0.22 |  | 569 66.1 0.10 | 672 64.7 0.07 | 842 62.6 0.06 |  | 1004 60.8 0.07 |  | 1031 60.2 0.30
| TC | [5 empty] | 1138 |  |  | 1081 |  | 1000 |  |  | 922 |  |  | 846 |  | 1191 |  |  | 1133 |  | 1051 | 971 |  | 908 |  |  | 1228 |  |  | 1167 |  | 1087 | 1005 |  | 962 |  | 1255 | 1198 | 1113 |  | 1028 |  | 1006
85 | SHC kW BF | [5 empty] | 465 69.7 0.00 |  |  | 531 68.4 0.10 |  | 636 66.6 0.04 |  |  | 738 65.1 0.03 |  |  | 828 63.8 0.04 |  | 496 70.9 0.00 |  |  | 575 69.6 0.07 |  | 704 67.8 0.04 | 830 66.2 0.03 |  | 908 64.9 0.13 |  |  | 525 71.7 0.11 |  |  | 616 70.4 0.06 |  | 768 68.6 0.05 | 912 66.9 0.05 |  | 962 65.9 0.24 |  | 551 72.3 0.09 | 655 71.0 0.07 | 829 69.2 0.06 |  | 986 67.4 0.07 |  | 1006 66.9 0.31
| TC | [5 empty] | 1100 |  |  | 1050 |  | 971 |  |  | 894 |  |  | 819 |  | 1151 |  |  | 1092 |  | 1018 | 940 |  | 883 |  |  | 1185 |  |  | 1134 |  | 1051 | 971 |  | 936 |  | 1208 | 1153 | 1075 |  | 994 |  | 979
95 | SHC kW BF | [5 empty] | 450 77.1 0.00 |  |  | 518 76.0 0.08 |  | 623 74.4 0.04 |  |  | 723 73.1 0.03 |  |  | 810 71.5 0.05 |  | 483 78.3 0.17 |  |  | 560 77.0 0.06 |  | 690 75.5 0.04 | 814 74.1 0.03 |  | 883 72.7 0.16 |  |  | 510 79.2 0.10 |  |  | 602 78.0 0.06 |  | 754 76.3 0.05 | 895 74.8 0.05 |  | 936 73.8 0.26 |  | 535 79.8 0.09 | 640 78.5 0.06 | 813 76.9 0.05 |  | 968 75.2 0.08 |  | 979 74.8 0.33
| TC | [5 empty] | 1064 |  |  | 1014 |  | 936 |  |  | 858 |  |  | 792 |  | 1110 |  |  | 1060 |  | 980 | 900 |  | 854 |  |  | 1140 |  |  | 1091 |  | 1009 | 930 |  | 905 |  | 1161 | 1104 | 1031 |  | 952 |  | 946
105 | SHC kW BF | [5 empty] | 434 85.9 0.00 |  |  | 504 84.9 0.07 |  | 607 83.5 0.04 |  |  | 706 82.3 0.02 |  |  | 780 80.5 0.09 |  | 469 87.2 0.13 |  |  | 547 86.1 0.06 |  | 674 84.6 0.04 | 794 83.3 0.04 |  | 854 82.0 0.19 |  |  | 495 88.0 0.09 |  |  | 586 86.9 0.06 |  | 736 85.4 0.05 | 875 83.9 0.05 |  | 905 83.1 0.28 |  | 520 88.5 0.08 | 623 87.1 0.06 | 797 86.0 0.05 |  | 941 84.2 0.09 |  | 946 83.9 0.36
| TC | [5 empty] | 1019 |  |  | 967 |  | 893 |  |  | 816 |  |  | 756 |  | 1061 |  |  | 1012 |  | 932 | 855 |  | 820 |  |  | 1087 |  |  | 1039 |  | 960 | 882 |  | 868 |  | 1108 | 1059 | 979 |  | 910 |  | 906
115 | SHC kW BF | [5 empty] | 422 96.1 0.00 |  |  | 486 94.7 0.05 |  | 588 94.2 0.03 |  |  | 685 94.4 0.03 |  |  | 756 92.7 0.10 |  | 452 97.4 0.10 |  |  | 528 96.4 0.06 |  | 654 95.3 0.04 | 773 95.2 0.04 |  | 820 93.4 0.22 |  |  | 477 98.2 0.08 |  |  | 568 97.2 0.06 |  | 716 96.1 0.05 | 852 94.4 0.06 |  | 868 94.2 0.31 |  | 502 98.8 0.08 | 605 97.8 0.06 | 776 96.7 0.05 |  | 899 95.0 0.13 |  | 906 94.8 0.38
LEGEND
48/50 VAV units only.
48/50 090 (90 TON) HIGH- CAPACITY COIL — STANDARD MODE (cont)
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
Temp (F) Air Entering Condenser (Edb) | [6 empty] | Evaporator Air Quantity — Cfm 36,000 Evaporator Air — Ewb (F)
[7 empty] | 75 |  |  | 72 |  | 67 |  |  | 62 |  |  | 57
| TC | [5 empty] | 1331 |  |  | 1267 |  | 1169 |  |  | 1081 |  |  | 1069
75 | SHC kW BF | [5 empty] | 593 66.6 0.10 |  |  | 711 65.2 0.07 |  | 903 63.0 0.06 |  |  | 1066 61.2 0.10 |  |  | 1069 61.1 0.36
[29 empty] | tlwb |  | Wet-bulb temperature corresponding to enthalpy of air leaving evaporator coil (hlwb).
| TC | [5 empty] | 1276 |  |  | 1218 |  | 1133 |  |  | 1048 |  |  | 1043
85 | SHC kW BF | [5 empty] | 575 72.8 0.09 |  |  | 692 71.5 0.07 |  | 889 69.6 0.06 |  |  | 1042 67.8 0.11 |  |  | 1043 67.7 0.38 | [10 empty] | hlwb |  | = hewb |  |  |  | – total capacity (Btuh) 4.5 x cfm
| TC | [5 empty] | 1231 |  |  | 1177 |  | 1093 |  |  | 1017 |  |  | 1014
Where: hewb = Enthalpy of air entering evaporator coil. 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
95 | SHC kW BF | [5 empty] | 560 80.3 0.09 |  |  | 678 79.1 0.07 |  | 873 77.4 0.06 |  |  | 1007 75.6 0.15 |  |  | 1014 75.6 0.40
| TC | [5 empty] | 1182 |  |  | 1129 |  | 1047 |  |  | 983 |  |  | 979
105 | SHC kW BF | [5 empty] | 544 89.1 0.09 |  |  | 661 88.0 0.07 |  | 855 86.4 0.06 |  |  | 968 84.8 0.18 |  |  | 979 84.7 0.42
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
| TC | [5 empty] | 1126 |  |  | 1073 |  | 993 |  |  | 938 |  |  | 937
Correction Factor
115 | SHC kW BF | [5 empty] | 526 99.5 0.08 |  |  | 642 98.3 0.07 |  | 832 97.4 0.06 |  |  | 938 95.3 0.20 |  |  | 937 95.3 0.44
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50P2,P3,P4,P5100 (100 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [8 empty] | Evaporator Air Quantity — Cfm
[9 empty] | 20000 | [15 empty] | 25000 | [12 empty] | 30000
Evaporator Air — Ewb (F)
[9 empty] | 75 |  |  | 72 |  |  |  | 67 |  |  | 62 |  |  |  | 57 |  | 75 |  | 72 |  |  |  | 67 |  |  | 62 |  | 57 |  | 75 |  | 72 |  | 67 |  | 62 |  | 57
|  | TC | [6 empty] | 1198 |  |  | 1147 |  |  |  | 1057 |  |  | 970 |  |  |  | 883 |  | 1251 |  | 1194 |  |  |  | 1104 |  |  | 1017 |  | 944 |  | 1285 |  | 1228 |  | 1138 |  | 1050 |  | 991
75 |  | SHC kW BF | [6 empty] | 489 68.6 0.00 |  |  | 549 67.4 0.00 |  |  |  | 663 65.6 0.14 |  |  | 768 64.1 0.11 |  |  |  | 854 62.7 0.13 |  | 509 69.9 0.00 |  | 593 68.5 0.23 |  |  |  | 727 66.6 0.14 |  |  | 856 65.0 0.12 |  | 928 63.7 0.22 |  | 535 70.8 0.12 |  | 632 69.3 0.19 |  | 786 67.4 0.15 |  | 935 65.7 0.14 |  | 991 64.7 0.28
|  | TC | [6 empty] | 1161 |  |  | 1111 |  |  |  | 1023 |  |  | 938 |  |  |  | 855 |  | 1209 |  | 1155 |  |  |  | 1068 |  |  | 982 |  | 923 |  | 1238 |  | 1186 |  | 1099 |  | 1012 |  | 975
85 |  | SHC kW BF | [6 empty] | 475 75.7 0.00 |  |  | 536 74.6 0.10 |  |  |  | 648 72.9 0.14 |  |  | 752 71.5 0.10 |  |  |  | 833 70.2 0.14 |  | 490 77.0 0.00 |  | 579 75.7 0.20 |  |  |  | 711 73.9 0.14 |  |  | 840 72.4 0.12 |  | 892 71.2 0.27 |  | 521 77.8 0.10 |  | 617 76.5 0.18 |  | 771 74.6 0.15 |  | 917 73.0 0.14 |  | 947 72.2 0.35
|  | TC | [6 empty] | 1121 |  |  | 1071 |  |  |  | 985 |  |  | 902 |  |  |  | 825 |  | 1164 |  | 1113 |  |  |  | 1027 |  |  | 942 |  | 893 |  | 1191 |  | 1141 |  | 1056 |  | 970 |  | 933
95 |  | SHC kW BF | [6 empty] | 457 84.1 0.00 |  |  | 522 83.0 0.08 |  |  |  | 632 81.4 0.13 |  |  | 735 80.0 0.10 |  |  |  | 811 79.3 0.15 |  | 480 85.2 0.14 |  | 564 84.1 0.18 |  |  |  | 695 82.4 0.13 |  |  | 821 80.8 0.12 |  | 870 79.7 0.28 |  | 506 86.0 0.28 |  | 602 84.8 0.17 |  | 754 83.1 0.14 |  | 896 81.5 0.14 |  | 933 80.8 0.33
|  | TC | [6 empty] | 1077 |  |  | 1026 |  |  |  | 942 |  |  | 861 |  |  |  | 796 |  | 1113 |  | 1064 |  |  |  | 981 |  |  | 899 |  | 849 |  | 1139 |  | 1090 |  | 1007 |  | 924 |  | 897
105 |  | SHC kW BF | [6 empty] | 436 93.7 0.00 |  |  | 506 92.7 0.07 |  |  |  | 613 91.4 0.12 |  |  | 716 90.5 0.10 |  |  |  | 775 89.8 0.20 |  | 464 94.7 0.10 |  | 547 93.7 0.17 |  |  |  | 676 92.1 0.13 |  |  | 800 91.3 0.12 |  | 848 90.9 0.27 |  | 490 95.4 0.23 |  | 585 94.3 0.16 |  | 735 92.7 0.14 |  | 872 91.9 0.15 |  | 897 91.4 0.36
|  | TC | [6 empty] | 1025 |  |  | 976 |  |  |  | 895 |  |  | 817 |  |  |  | 759 |  | 1057 |  | 1010 |  |  |  | 930 |  |  | 851 |  | 812 |  | 1080 |  | 1034 |  | 954 |  | 875 |  | 858
115 |  | SHC kW BF | [6 empty] | 417 104.6 0.00 |  |  | 487 103.9 0.18 |  |  |  | 593 103.4 0.11 |  |  | 695 103.4 0.09 |  |  |  | 747 103.1 0.21 |  | 447 105.4 0.08 |  | 528 104.6 0.15 |  |  |  | 656 103.9 0.12 |  |  | 778 103.9 0.12 |  | 812 103.8 0.30 |  | 471 106.1 0.20 |  | 565 105.3 0.16 |  | 715 104.3 0.14 |  | 841 104.1 0.17 |  | 858 104.0 0.39
48/50P2,P3,P4,P5100 (100 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [8 empty] | Evaporator Air Quantity — Cfm
[9 empty] | 35000 | [15 empty] | 40000
Evaporator Air — Ewb (F)
[9 empty] | 75 |  |  | 72 |  |  |  | 67 |  |  | 62 |  |  |  | 57 |  | 75 |  | 72 |  |  |  | 67 |  |  | 62 |  | 57
|  | TC | [6 empty] | 1310 |  |  | 1252 |  |  |  | 1162 |  |  | 1073 |  |  |  | 1038 |  | 1329 |  | 1273 |  |  |  | 1181 |  |  | 1092 |  | 1074
75 |  | SHC kW BF | [6 empty] | 561 71.4 0.27 |  |  | 669 70.0 0.19 |  |  |  | 843 68.0 0.16 |  |  | 1005 66.2 0.17 |  |  |  | 1038 65.5 0.36 |  | 584 71.9 0.24 |  | 705 70.5 0.19 |  |  |  | 898 68.4 0.17 |  |  | 1059 66.6 0.21 |  | 1074 66.2 0.42
|  | TC | [6 empty] | 1260 |  |  | 1206 |  |  |  | 1121 |  |  | 1034 |  |  |  | 1007 |  | 1278 |  | 1224 |  |  |  | 1139 |  |  | 1054 |  | 1044
85 |  | SHC kW BF | [6 empty] | 545 78.4 0.25 |  |  | 654 77.1 0.18 |  |  |  | 828 75.2 0.16 |  |  | 980 73.5 0.18 |  |  |  | 1007 72.9 0.38 |  | 568 78.9 0.23 |  | 688 77.5 0.18 |  |  |  | 882 75.6 0.17 |  |  | 1032 73.9 0.22 |  | 1044 73.6 0.44
|  | TC | [6 empty] | 1212 |  |  | 1160 |  |  |  | 1077 |  |  | 992 |  |  |  | 973 |  | 1228 |  | 1177 |  |  |  | 1093 |  |  | 1014 |  | 1006
95 |  | SHC kW BF | [6 empty] | 530 86.6 0.23 |  |  | 638 85.3 0.17 |  |  |  | 810 83.6 0.16 |  |  | 951 81.9 0.19 |  |  |  | 973 81.5 0.40 |  | 553 87.0 0.22 |  | 671 85.8 0.18 |  |  |  | 865 84.0 0.17 |  |  | 992 82.3 0.25 |  | 1006 82.2 0.46
|  | TC | [6 empty] | 1158 |  |  | 1108 |  |  |  | 1026 |  |  | 947 |  |  |  | 937 |  | 1173 |  | 1123 |  |  |  | 1041 |  |  | 970 |  | 967
105 |  | SHC kW BF | [6 empty] | 513 95.9 0.21 |  |  | 620 94.8 0.17 |  |  |  | 791 93.2 0.15 |  |  | 926 92.2 0.20 |  |  |  | 937 91.7 0.43 |  | 536 96.4 0.21 |  | 653 95.3 0.18 |  |  |  | 845 93.6 0.17 |  |  | 960 92.5 0.27 |  | 967 92.4 0.48
|  | TC | [6 empty] | 1098 |  |  | 1050 |  |  |  | 972 |  |  | 901 |  |  |  | 894 |  | 1110 |  | 1063 |  |  |  | 985 |  |  | 923 |  | 922
115 |  | SHC kW BF | [6 empty] | 495 106.6 0.19 |  |  | 600 105.7 0.16 |  |  |  | 770 104.7 0.15 |  |  | 882 104.0 0.24 |  |  |  | 894 104.2 0.45 |  | 517 107.0 0.20 |  | 633 106.1 0.17 |  |  |  | 824 104.9 0.17 |  |  | 923 104.4 0.29 |  | 922 104.5 0.51
LEGEND | [28 empty] | 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tlwb
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80).
hlwb = hewb – | [5 empty] | 4.5 x cfm | [7 empty] | 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50P2,P3,P4,P5100 (100 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) | [7 empty] | Evaporator Air Quantity — Cfm
[8 empty] | 20000 | [16 empty] | 25000 | [12 empty] | 30000
Evaporator Air — Ewb (F)
[8 empty] | 75 |  |  | 72 |  |  |  |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  |  | 67 |  |  |  | 62 |  | 57 |  | 75 |  | 72 |  | 67 |  | 62 |  | 57
|  | TC | [5 empty] | 1269 |  |  | 1208 |  |  |  |  | 1114 |  |  | 1026 |  |  | 941 |  |  | 1332 |  | 1267 |  |  | 1171 |  |  |  | 1081 |  | 1010 |  | 1373 |  | 1308 |  | 1210 |  | 1118 |  | 1069
75 |  | SHC kW BF | [5 empty] | 524 71.2 0.00 |  |  | 591 69.7 0.05 |  |  |  |  | 707 67.3 0.05 |  |  | 820 65.4 0.03 |  |  | 910 63.7 0.06 |  |  | 552 72.9 0.10 |  | 640 71.1 0.08 |  |  | 782 68.7 0.05 |  |  |  | 920 66.6 0.04 |  | 1002 65.0 0.15 |  | 585 73.9 0.14 |  | 685 72.2 0.08 |  | 852 69.7 0.06 |  | 1010 67.5 0.06 |  | 1069 66.4 0.24
|  | TC | [5 empty] | 1231 |  |  | 1172 |  |  |  |  | 1084 |  |  | 998 |  |  | 916 |  |  | 1285 |  | 1227 |  |  | 1136 |  |  |  | 1048 |  | 987 |  | 1324 |  | 1265 |  | 1173 |  | 1083 |  | 1043
85 |  | SHC kW BF | [5 empty] | 505 78.3 0.00 |  |  | 577 76.7 0.11 |  |  |  |  | 694 74.6 0.05 |  |  | 805 72.8 0.03 |  |  | 891 71.1 0.07 |  |  | 537 79.7 0.07 |  | 626 78.3 0.07 |  |  | 767 75.9 0.05 |  |  |  | 904 74.1 0.04 |  | 977 72.5 0.17 |  | 568 80.8 0.12 |  | 670 79.2 0.07 |  | 836 76.9 0.05 |  | 993 74.9 0.06 |  | 1043 73.8 0.25
|  | TC | [5 empty] | 1189 |  |  | 1136 |  |  |  |  | 1049 |  |  | 963 |  |  | 887 |  |  | 1241 |  | 1183 |  |  | 1097 |  |  |  | 1010 |  | 955 |  | 1275 |  | 1221 |  | 1131 |  | 1041 |  | 1012
95 |  | SHC kW BF | [5 empty] | 488 86.5 0.00 |  |  | 563 85.1 0.10 |  |  |  |  | 678 83.2 0.04 |  |  | 788 81.5 0.03 |  |  | 871 80.1 0.08 |  |  | 522 88.0 0.06 |  | 609 86.5 0.07 |  |  | 751 84.5 0.05 |  |  |  | 885 82.7 0.04 |  | 955 81.3 0.18 |  | 552 89.0 0.10 |  | 653 87.6 0.07 |  | 819 85.5 0.05 |  | 971 83.4 0.06 |  | 1012 82.5 0.28
|  | TC | [5 empty] | 1147 |  |  | 1090 |  |  |  |  | 1007 |  |  | 923 |  |  | 853 |  |  | 1193 |  | 1139 |  |  | 1051 |  |  |  | 965 |  | 921 |  | 1224 |  | 1170 |  | 1082 |  | 995 |  | 975
105 |  | SHC kW BF | [5 empty] | 473 96.1 0.00 |  |  | 545 94.7 0.07 |  |  |  |  | 659 93.3 0.04 |  |  | 768 92.4 0.03 |  |  | 849 90.6 0.09 |  |  | 506 97.6 0.13 |  | 592 96.3 0.07 |  |  | 731 94.6 0.04 |  |  |  | 863 93.4 0.04 |  | 921 92.2 0.21 |  | 535 98.6 0.09 |  | 635 97.3 0.07 |  | 800 95.5 0.05 |  | 945 94.0 0.07 |  | 975 93.0 0.30
|  | TC | [5 empty] | 1095 |  |  | 1043 |  |  |  |  | 959 |  |  | 877 |  |  | 817 |  |  | 1137 |  | 1085 |  |  | 999 |  |  |  | 915 |  | 883 |  | 1166 |  | 1113 |  | 1027 |  | 945 |  | 933
115 |  | SHC kW BF | [5 empty] | 455 107.2 0.08 |  |  | 526 106.4 0.07 |  |  |  |  | 638 105.6 0.04 |  |  | 746 105.4 0.03 |  |  | 816 104.0 0.12 |  |  | 487 108.8 0.10 |  | 572 107.9 0.06 |  |  | 710 106.7 0.04 |  |  |  | 839 106.4 0.05 |  | 883 104.6 0.24 |  | 516 109.9 0.08 |  | 614 108.8 0.06 |  | 778 107.6 0.05 |  | 912 106.5 0.09 |  | 933 105.5 0.33
48/50P2,P3,P4,P5100 (100 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) | [7 empty] | Evaporator Air Quantity — Cfm
[8 empty] | 35000 | [16 empty] | 40000
Evaporator Air — Ewb (F)
[8 empty] | 75 |  |  | 72 |  |  |  |  | 67 |  |  | 62 |  |  | 57 |  |  | 75 |  | 72 |  |  | 67 |  |  |  | 62 |  | 57
|  | TC | [5 empty] | 1402 |  |  | 1337 |  |  |  |  | 1239 |  |  | 1144 |  |  | 1118 |  |  | 1426 |  | 1360 |  |  | 1260 |  |  |  | 1170 |  | 1159
75 |  | SHC kW BF | [5 empty] | 613 74.7 0.11 |  |  | 729 73.0 0.07 |  |  |  |  | 919 70.4 0.06 |  |  | 1086 68.2 0.09 |  |  | 1118 67.6 0.31 |  |  | 640 75.3 0.10 |  | 769 73.6 0.08 |  |  | 984 71.0 0.07 |  |  |  | 1149 68.8 0.13 |  | 1159 68.6 0.38
|  | TC | [5 empty] | 1351 |  |  | 1292 |  |  |  |  | 1199 |  |  | 1107 |  |  | 1090 |  |  | 1373 |  | 1313 |  |  | 1219 |  |  |  | 1135 |  | 1128
85 |  | SHC kW BF | [5 empty] | 596 81.6 0.10 |  |  | 712 80.0 0.08 |  |  |  |  | 903 77.6 0.06 |  |  | 1064 75.5 0.09 |  |  | 1090 74.9 0.33 |  |  | 623 82.2 0.10 |  | 753 80.6 0.08 |  |  | 967 78.2 0.07 |  |  |  | 1121 76.1 0.15 |  | 1128 75.9 0.40
|  | TC | [5 empty] | 1302 |  |  | 1246 |  |  |  |  | 1155 |  |  | 1069 |  |  | 1057 |  |  | 1322 |  | 1264 |  |  | 1173 |  |  |  | 1097 |  | 1093
95 |  | SHC kW BF | [5 empty] | 580 89.8 0.09 |  |  | 695 88.3 0.07 |  |  |  |  | 886 86.2 0.06 |  |  | 1038 84.1 0.11 |  |  | 1057 83.7 0.35 |  |  | 606 90.4 0.09 |  | 736 88.9 0.08 |  |  | 949 86.8 0.07 |  |  |  | 1083 84.7 0.18 |  | 1093 84.6 0.41
|  | TC | [5 empty] | 1249 |  |  | 1192 |  |  |  |  | 1104 |  |  | 1026 |  |  | 1018 |  |  | 1266 |  | 1209 |  |  | 1120 |  |  |  | 1054 |  | 1052
105 |  | SHC kW BF | [5 empty] | 562 99.4 0.09 |  |  | 677 98.0 0.07 |  |  |  |  | 865 96.2 0.06 |  |  | 1004 94.4 0.13 |  |  | 1018 94.0 0.38 |  |  | 588 100.0 0.09 |  | 717 98.6 0.08 |  |  | 928 96.8 0.07 |  |  |  | 1048 94.6 0.20 |  | 1052 94.7 0.44
|  | TC | [5 empty] | 1187 |  |  | 1133 |  |  |  |  | 1046 |  |  | 976 |  |  | 973 |  |  | 1204 |  | 1149 |  |  | 1061 |  |  |  | 1009 |  | 1006
115 |  | SHC kW BF | [5 empty] | 542 110.6 0.08 |  |  | 656 109.5 0.07 |  |  |  |  | 842 108.3 0.06 |  |  | 971 105.9 0.15 |  |  | 973 106.2 0.40 |  |  | 568 111.5 0.09 |  | 696 110.2 0.07 |  |  | 904 108.6 0.07 |  |  |  | 999 106.8 0.24 |  | 1006 106.9 0.46
LEGEND | [28 empty] | 3. SHC is based on 80°F edb temperature of air entering evaporator coil. Below 80°F edb, subtract (corr factor x cfm) from SHC. Above 80°F edb, add (corr factor x cfm) to SHC.
48/50 VAV units only.
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used:
[29 empty] | BF |  |  |  |  | ENTERING AIR DRY-BULB TEMP (F)
[34 empty] | 79 |  | 78 |  | 77 |  | 76 |  | 75 |  | under 75
[34 empty] | 81 |  | 82 |  | 83 |  | 84 |  | 85 |  | over 85
Correction Factor
[29 empty] | .05 .10 .20 |  |  |  |  | 1.04 0.99 0.88 |  | 2.09 1.98 1.76 |  | 3.14 2.97 2.64 |  | 4.18 3.96 3.52 |  | 5.22 4.95 4.40 |  | Use formula shown below
tldb |  |  |  | – sensible capacity (Btuh) 1.10 x cfm
Wet-bulb temperature corresponding to enthalpy of air leaving evaporator coil (hlwb). h = h – total capacity (Btuh) 4.5 x cfm Where: hewb = Enthalpy of air entering evaporator coil.
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
tlwb =
ldb edb
=
lwb ewb
=
lwb ewb
ldb edb
=
lwb ewb
ldb edb
=
lwb ewb
ldb edb
=
tlwb =
ldb edb
ldb edb
=
ldb edb
=
ldb edb
=
tlwb =
ldb edb
lwb ewb
ldb edb
=
ldb edb
=
ldb edb
=
ldb edb
=
ldb edb
=
ldb edb
=
tlwb =
lwb ewb

## Sheet1
Performance data
Cooling Capacities 48/50 030 (30 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 6000 |  |  |  |  | 7500 |  |  |  |  | 9000 |  |  |  |  | 10500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 378 | 362 | 334 | 308 | 282 | 399 | 379 | 351 | 325 | 297 | 412 | 392 | 363 | 336 | 312 | 421 | 401 | 372 | 345 | 327
| SHC | 155 | 167 | 204 | 236 | 265 | 159 | 183 | 224 | 262 | 292 | 166 | 195 | 241 | 285 | 312 | 175 | 206 | 256 | 307 | 327
| kW | 22.5 | 22.1 | 21.3 | 20.8 | 20.5 | 23 | 22.5 | 21.7 | 21.2 | 20.7 | 23.4 | 22.8 | 22.1 | 21.4 | 21 | 23.6 | 23.1 | 22.3 | 21.6 | 21.3
| BF | 0 | 0 | 0.22 | 0.16 | 0.14 | 0 | 0 | 0.19 | 0.16 | 0.19 | 0 | 0.27 | 0.2 | 0.18 | 0.26 | 0 | 0.25 | 0.21 | 0.19 | 0.33
85 | TC | 367 | 353 | 326 | 300 | 273 | 384 | 369 | 342 | 316 | 290 | 396 | 380 | 353 | 327 | 305 | 404 | 389 | 361 | 335 | 319
| SHC | 150 | 165 | 201 | 231 | 259 | 155 | 180 | 220 | 257 | 281 | 162 | 191 | 236 | 281 | 305 | 170 | 202 | 252 | 303 | 319
| kW | 24.7 | 24.4 | 23.7 | 23.4 | 23.2 | 25.2 | 24.8 | 24.1 | 23.7 | 23.1 | 25.6 | 25.1 | 24.4 | 23.9 | 23.6 | 25.8 | 25.3 | 24.7 | 24.1 | 23.8
| BF | 0 | 0 | 0.21 | 0.15 | 0.14 | 0 | 0.16 | 0.18 | 0.16 | 0.23 | 0 | 0.25 | 0.2 | 0.18 | 0.27 | 0.36 | 0.24 | 0.21 | 0.19 | 0.35
95 | TC | 357 | 343 | 316 | 289 | 264 | 373 | 357 | 331 | 304 | 281 | 383 | 368 | 341 | 315 | 295 | 391 | 376 | 349 | 322 | 309
| SHC | 146 | 162 | 196 | 226 | 253 | 150 | 176 | 215 | 252 | 272 | 159 | 187 | 232 | 275 | 295 | 166 | 198 | 248 | 296 | 309
| kW | 27.4 | 27.1 | 26.6 | 26.4 | 26.1 | 27.9 | 27.5 | 27 | 26.6 | 26.1 | 28.2 | 27.8 | 27.3 | 26.9 | 26.6 | 28.4 | 28 | 27.5 | 27.1 | 26.8
| BF | 0 | 0 | 0.19 | 0.15 | 0.14 | 0 | 0.28 | 0.18 | 0.16 | 0.26 | 0 | 0.24 | 0.19 | 0.17 | 0.3 | 0.31 | 0.23 | 0.21 | 0.2 | 0.37
105 | TC | 344 | 330 | 304 | 277 | 251 | 360 | 344 | 318 | 291 | 268 | 369 | 354 | 327 | 301 | 284 | 377 | 361 | 334 | 308 | 297
| SHC | 141 | 158 | 191 | 220 | 244 | 145 | 171 | 210 | 246 | 268 | 154 | 182 | 226 | 269 | 284 | 162 | 193 | 242 | 288 | 297
| kW | 30.5 | 30.3 | 30 | 29.8 | 30.2 | 31 | 30.7 | 30.3 | 30 | 29.9 | 31.2 | 31 | 30.6 | 30.2 | 30.1 | 31.5 | 31.2 | 30.7 | 30.5 | 30.2
| BF | 0 | 0 | 0.17 | 0.14 | 0.16 | 0 | 0.25 | 0.17 | 0.15 | 0.23 | 0.18 | 0.22 | 0.19 | 0.17 | 0.32 | 0.28 | 0.22 | 0.2 | 0.2 | 0.39
115 | TC | 330 | 315 | 289 | 263 | 237 | 344 | 328 | 302 | 276 | 256 | 352 | 337 | 310 | 285 | 272 | 360 | 344 | 317 | 291 | 285
| SHC | 135 | 153 | 185 | 214 | 234 | 141 | 166 | 203 | 239 | 256 | 149 | 177 | 219 | 261 | 272 | 156 | 187 | 235 | 279 | 285
| kW | 34 | 33.9 | 33.9 | 34.2 | 34.6 | 34.4 | 34.3 | 34.1 | 34.3 | 34.6 | 34.7 | 34.6 | 34.3 | 34.4 | 34.5 | 35.1 | 34.8 | 34.4 | 34.5 | 34.4
| BF | 0 | 0 | 0.16 | 0.14 | 0.18 | 0 | 0.22 | 0.17 | 0.15 | 0.27 | 0.29 | 0.21 | 0.18 | 0.17 | 0.35 | 0.26 | 0.21 | 0.2 | 0.21 | 0.42
48/50 030 (30 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 13500 |  |  |  |  | 15000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 428 | 408 | 378 | 352 | 339 | 434 | 414 | 383 | 357 | 349 | 439 | 418 | 388 | 360 | 357
| SHC | 182 | 216 | 272 | 326 | 339 | 189 | 226 | 286 | 341 | 349 | 195 | 235 | 300 | 354 | 357
| kW | 23.8 | 23.3 | 22.5 | 21.8 | 21.5 | 24 | 23.4 | 22.6 | 21.9 | 21.8 | 24.1 | 23.6 | 22.7 | 22 | 22
| BF | 0.33 | 0.25 | 0.22 | 0.22 | 0.39 | 0.31 | 0.25 | 0.24 | 0.25 | 0.45 | 0.3 | 0.26 | 0.25 | 0.28 | 0.49
85 | TC | 411 | 395 | 368 | 341 | 330 | 417 | 400 | 373 | 346 | 340 | 422 | 404 | 376 | 349 | 348
| SHC | 177 | 212 | 268 | 321 | 330 | 183 | 221 | 282 | 334 | 340 | 190 | 230 | 296 | 348 | 348
| kW | 26 | 25.5 | 24.8 | 24.3 | 24 | 26.2 | 25.7 | 25 | 24.4 | 24.2 | 26.3 | 25.8 | 25.1 | 24.4 | 24.4
| BF | 0.3 | 0.24 | 0.22 | 0.22 | 0.41 | 0.29 | 0.25 | 0.23 | 0.26 | 0.46 | 0.29 | 0.25 | 0.25 | 0.29 | 0.5
95 | TC | 398 | 382 | 355 | 328 | 320 | 404 | 387 | 359 | 332 | 330 | 408 | 391 | 363 | 339 | 338
| SHC | 173 | 207 | 263 | 313 | 320 | 179 | 217 | 277 | 327 | 330 | 185 | 226 | 291 | 334 | 338
| kW | 28.6 | 28.2 | 27.6 | 27.2 | 27 | 28.8 | 28.3 | 27.7 | 27.3 | 27.2 | 28.9 | 28.5 | 27.8 | 27.3 | 27.3
| BF | 0.29 | 0.23 | 0.22 | 0.23 | 0.43 | 0.28 | 0.24 | 0.23 | 0.26 | 0.48 | 0.28 | 0.25 | 0.24 | 0.32 | 0.52
105 | TC | 383 | 367 | 340 | 313 | 308 | 388 | 371 | 344 | 320 | 317 | 392 | 375 | 347 | 326 | 325
| SHC | 168 | 202 | 257 | 303 | 308 | 175 | 212 | 271 | 309 | 317 | 180 | 221 | 285 | 321 | 325
| kW | 31.7 | 31.4 | 30.9 | 30.5 | 30.4 | 31.9 | 31.5 | 31 | 30.4 | 30.6 | 32 | 31.6 | 31 | 30.7 | 30.7
| BF | 0.27 | 0.23 | 0.22 | 0.24 | 0.45 | 0.26 | 0.24 | 0.23 | 0.32 | 0.5 | 0.27 | 0.25 | 0.24 | 0.35 | 0.54
115 | TC | 365 | 349 | 322 | 296 | 295 | 369 | 353 | 326 | 303 | 303 | 372 | 356 | 329 | 311 | 310
| SHC | 163 | 196 | 250 | 292 | 295 | 169 | 206 | 264 | 303 | 303 | 175 | 214 | 278 | 310 | 310
| kW | 35.3 | 35 | 34.5 | 34.4 | 34.5 | 35.4 | 35.1 | 34.6 | 34.5 | 34.5 | 35.5 | 35.2 | 34.6 | 34.5 | 34.5
| BF | 0.25 | 0.22 | 0.21 | 0.26 | 0.47 | 0.25 | 0.23 | 0.23 | 0.31 | 0.52 | 0.26 | 0.25 | 0.24 | 0.36 | 0.56
Performance data (cont)
Cooling Capacities (cont) 48/50 030 (30 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 6000 |  |  |  |  | 7500 |  |  |  |  | 9000 |  |  |  |  | 10500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 384 | 367 | 338 | 312 | 289 | 405 | 386 | 356 | 329 | 307 | 418 | 400 | 369 | 341 | 323 | 429 | 410 | 378 | 351 | 338
| SHC | 158 | 177 | 211 | 245 | 277 | 164 | 192 | 233 | 274 | 300 | 175 | 205 | 253 | 300 | 323 | 183 | 217 | 271 | 325 | 338
| kW | 22.8 | 22.3 | 21.5 | 20.8 | 20.3 | 23.3 | 22.8 | 21.9 | 21.2 | 20.6 | 23.7 | 23.1 | 22.3 | 21.5 | 21.1 | 23.9 | 23.4 | 22.5 | 21.8 | 21.5
| BF | 0 | 0 | 0.1 | 0.07 | 0.07 | 0 | 0.16 | 0.09 | 0.08 | 0.17 | 0.13 | 0.14 | 0.11 | 0.09 | 0.23 | 0.2 | 0.14 | 0.12 | 0.11 | 0.31
85 | TC | 373 | 356 | 330 | 305 | 282 | 392 | 373 | 346 | 322 | 299 | 404 | 386 | 358 | 333 | 317 | 414 | 395 | 367 | 342 | 331
| SHC | 153 | 172 | 208 | 241 | 272 | 161 | 187 | 229 | 270 | 299 | 170 | 200 | 248 | 296 | 317 | 179 | 212 | 267 | 321 | 331
| kW | 25 | 24.5 | 23.7 | 23.2 | 22.9 | 25.5 | 25 | 24.2 | 23.6 | 23.1 | 25.9 | 25.3 | 24.5 | 23.9 | 23.5 | 26.1 | 25.6 | 24.8 | 24.1 | 23.9
| BF | 0 | 0 | 0.09 | 0.07 | 0.07 | 0 | 0.14 | 0.09 | 0.08 | 0.15 | 0.22 | 0.13 | 0.1 | 0.09 | 0.24 | 0.18 | 0.13 | 0.11 | 0.11 | 0.32
95 | TC | 360 | 346 | 322 | 297 | 272 | 377 | 362 | 337 | 312 | 291 | 389 | 374 | 348 | 323 | 309 | 399 | 383 | 356 | 331 | 323
| SHC | 148 | 169 | 204 | 237 | 266 | 156 | 183 | 225 | 266 | 291 | 165 | 196 | 244 | 292 | 309 | 174 | 208 | 263 | 315 | 323
| kW | 27.5 | 27.1 | 26.5 | 26.1 | 26 | 28 | 27.6 | 26.9 | 26.5 | 26.2 | 28.4 | 27.9 | 27.2 | 26.7 | 26.5 | 28.7 | 28.2 | 27.5 | 27 | 26.8
| BF | 0 | 0.1 | 0.09 | 0.07 | 0.07 | 0 | 0.13 | 0.09 | 0.08 | 0.17 | 0.19 | 0.12 | 0.1 | 0.09 | 0.26 | 0.16 | 0.13 | 0.11 | 0.12 | 0.34
105 | TC | 350 | 336 | 311 | 285 | 260 | 365 | 351 | 326 | 300 | 281 | 377 | 362 | 336 | 310 | 298 | 386 | 370 | 343 | 317 | 312
| SHC | 144 | 165 | 199 | 231 | 257 | 152 | 179 | 220 | 260 | 281 | 161 | 191 | 239 | 285 | 298 | 170 | 203 | 257 | 307 | 312
| kW | 30.5 | 30.2 | 29.8 | 29.6 | 29.9 | 31 | 30.7 | 30.2 | 29.9 | 29.8 | 31.4 | 31 | 30.5 | 30.3 | 30 | 31.7 | 31.3 | 30.7 | 30.5 | 30.3
| BF | 0 | 0.17 | 0.08 | 0.06 | 0.09 | 0.13 | 0.12 | 0.09 | 0.07 | 0.2 | 0.17 | 0.12 | 0.1 | 0.09 | 0.29 | 0.15 | 0.12 | 0.11 | 0.12 | 0.36
115 | TC | 338 | 323 | 297 | 272 | 247 | 351 | 337 | 310 | 285 | 269 | 362 | 346 | 320 | 294 | 285 | 370 | 353 | 326 | 302 | 299
| SHC | 138 | 160 | 193 | 225 | 246 | 148 | 173 | 214 | 253 | 269 | 156 | 186 | 233 | 278 | 285 | 164 | 197 | 251 | 295 | 299
| kW | 34.1 | 33.9 | 33.7 | 33.9 | 34.8 | 34.5 | 34.4 | 34.1 | 34.1 | 34.5 | 35 | 34.7 | 34.3 | 34.5 | 34.4 | 35.3 | 35 | 34.5 | 34.5 | 34.5
| BF | 0 | 0.14 | 0.07 | 0.06 | 0.12 | 0.2 | 0.11 | 0.08 | 0.07 | 0.23 | 0.15 | 0.11 | 0.1 | 0.1 | 0.32 | 0.14 | 0.12 | 0.11 | 0.15 | 0.39
48/50 030 (30 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 13500 |  |  |  |  | 15000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 437 | 417 | 385 | 356 | 350 | 444 | 423 | 391 | 361 | 360 | 449 | 428 | 396 | 370 | 369
| SHC | 191 | 229 | 289 | 343 | 350 | 199 | 240 | 306 | 358 | 360 | 206 | 250 | 323 | 370 | 369
| kW | 24.2 | 23.6 | 22.7 | 21.9 | 21.8 | 24.3 | 23.8 | 22.9 | 22.1 | 22.1 | 24.5 | 23.9 | 23 | 22.3 | 22.3
| BF | 0.18 | 0.14 | 0.13 | 0.14 | 0.37 | 0.18 | 0.15 | 0.14 | 0.19 | 0.43 | 0.18 | 0.15 | 0.15 | 0.24 | 0.47
85 | TC | 421 | 402 | 373 | 348 | 343 | 427 | 407 | 378 | 353 | 353 | 432 | 412 | 382 | 362 | 361
| SHC | 186 | 223 | 284 | 338 | 343 | 193 | 234 | 301 | 351 | 353 | 200 | 245 | 318 | 362 | 361
| kW | 26.4 | 25.8 | 25 | 24.3 | 24.2 | 26.5 | 26 | 25.1 | 24.4 | 24.4 | 26.6 | 26.1 | 25.2 | 24.7 | 24.7
| BF | 0.17 | 0.14 | 0.12 | 0.15 | 0.39 | 0.17 | 0.14 | 0.14 | 0.2 | 0.44 | 0.17 | 0.15 | 0.15 | 0.26 | 0.48
95 | TC | 406 | 389 | 362 | 337 | 334 | 411 | 395 | 367 | 344 | 344 | 416 | 399 | 370 | 352 | 352
| SHC | 181 | 219 | 280 | 331 | 334 | 188 | 230 | 297 | 344 | 344 | 195 | 240 | 313 | 352 | 352
| kW | 28.9 | 28.4 | 27.7 | 27.1 | 27 | 29 | 28.6 | 27.8 | 27.3 | 27.3 | 29.2 | 28.7 | 27.9 | 27.5 | 27.5
| BF | 0.16 | 0.13 | 0.12 | 0.16 | 0.4 | 0.16 | 0.14 | 0.13 | 0.22 | 0.45 | 0.17 | 0.16 | 0.14 | 0.28 | 0.5
105 | TC | 392 | 376 | 348 | 324 | 323 | 397 | 380 | 353 | 333 | 332 | 402 | 384 | 356 | 340 | 340
| SHC | 177 | 214 | 275 | 321 | 323 | 184 | 225 | 292 | 329 | 332 | 191 | 235 | 308 | 340 | 340
| kW | 31.9 | 31.5 | 30.9 | 30.4 | 30.5 | 32.1 | 31.7 | 31 | 30.6 | 30.7 | 32.3 | 31.8 | 31.2 | 30.9 | 30.9
| BF | 0.15 | 0.13 | 0.12 | 0.18 | 0.42 | 0.16 | 0.14 | 0.13 | 0.26 | 0.47 | 0.16 | 0.16 | 0.15 | 0.3 | 0.51
115 | TC | 375 | 359 | 331 | 311 | 309 | 380 | 363 | 335 | 318 | 318 | 384 | 366 | 338 | 325 | 325
| SHC | 172 | 209 | 268 | 304 | 309 | 179 | 219 | 285 | 318 | 318 | 185 | 229 | 301 | 325 | 325
| kW | 35.5 | 35.2 | 34.6 | 34.3 | 34.5 | 35.7 | 35.3 | 34.8 | 34.7 | 34.6 | 35.9 | 35.5 | 34.9 | 34.8 | 34.7
| BF | 0.15 | 0.13 | 0.12 | 0.23 | 0.45 | 0.15 | 0.14 | 0.13 | 0.27 | 0.49 | 0.16 | 0.15 | 0.15 | 0.33 | 0.53
Performance data (cont)
Cooling Capacities (cont) 48/50 035 (35 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 7000 |  |  |  |  | 8750 |  |  |  |  | 9625 |  |  |  |  | 10500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 437 | 419 | 387 | 358 | 332 | 459 | 439 | 407 | 377 | 352 | 466 | 446 | 414 | 384 | 361 | 472 | 453 | 420 | 389 | 370
| SHC | 177 | 200 | 242 | 281 | 318 | 183 | 216 | 266 | 313 | 343 | 190 | 224 | 277 | 328 | 361 | 195 | 231 | 288 | 343 | 370
| kW | 27 | 26.3 | 25.3 | 24.4 | 23.8 | 27.7 | 27 | 25.9 | 24.9 | 24.2 | 27.9 | 27.2 | 26.1 | 25.1 | 24.5 | 28.1 | 27.4 | 26.3 | 25.3 | 24.7
| BF | 0 | 0 | 0.11 | 0.08 | 0.08 | 0 | 0.18 | 0.11 | 0.1 | 0.18 | 0 | 0.16 | 0.12 | 0.1 | 0.2 | 0.14 | 0.16 | 0.12 | 0.11 | 0.24
85 | TC | 424 | 406 | 377 | 350 | 323 | 444 | 424 | 395 | 368 | 344 | 450 | 432 | 402 | 375 | 353 | 456 | 438 | 408 | 380 | 363
| SHC | 172 | 196 | 237 | 277 | 313 | 180 | 211 | 261 | 309 | 339 | 185 | 218 | 272 | 325 | 353 | 190 | 225 | 283 | 339 | 363
| kW | 29.5 | 28.8 | 27.8 | 27 | 26.6 | 30.1 | 29.4 | 28.4 | 27.5 | 26.9 | 30.4 | 29.7 | 28.6 | 27.7 | 27.2 | 30.6 | 29.9 | 28.8 | 27.9 | 27.4
| BF | 0 | 0 | 0.1 | 0.08 | 0.08 | 0 | 0.16 | 0.11 | 0.09 | 0.18 | 0 | 0.15 | 0.12 | 0.1 | 0.21 | 0.25 | 0.15 | 0.12 | 0.11 | 0.26
95 | TC | 409 | 394 | 368 | 340 | 311 | 427 | 411 | 384 | 357 | 333 | 433 | 418 | 391 | 363 | 344 | 438 | 423 | 397 | 369 | 353
| SHC | 166 | 191 | 233 | 272 | 304 | 175 | 206 | 256 | 304 | 333 | 179 | 214 | 267 | 319 | 344 | 184 | 220 | 278 | 334 | 353
| kW | 32.3 | 31.7 | 30.9 | 30.3 | 30 | 32.9 | 32.3 | 31.4 | 30.7 | 30.4 | 33.2 | 32.5 | 31.6 | 30.9 | 30.6 | 33.4 | 32.7 | 31.8 | 31.1 | 30.8
| BF | 0 | 0.1 | 0.1 | 0.08 | 0.09 | 0 | 0.15 | 0.1 | 0.09 | 0.18 | 0.27 | 0.14 | 0.11 | 0.1 | 0.23 | 0.21 | 0.14 | 0.12 | 0.11 | 0.28
105 | TC | 398 | 382 | 355 | 327 | 298 | 413 | 399 | 371 | 343 | 321 | 419 | 405 | 377 | 349 | 332 | 425 | 410 | 382 | 354 | 341
| SHC | 161 | 187 | 228 | 265 | 295 | 170 | 202 | 251 | 297 | 321 | 175 | 209 | 262 | 313 | 332 | 180 | 216 | 272 | 326 | 341
| kW | 35.7 | 35.2 | 34.6 | 34.2 | 34.4 | 36.3 | 35.8 | 35.1 | 34.6 | 34.4 | 36.5 | 36 | 35.3 | 34.8 | 34.6 | 36.7 | 36.2 | 35.4 | 35.1 | 34.8
| BF | 0 | 0.18 | 0.09 | 0.08 | 0.11 | 0.14 | 0.14 | 0.1 | 0.09 | 0.21 | 0.21 | 0.13 | 0.11 | 0.1 | 0.26 | 0.19 | 0.13 | 0.12 | 0.11 | 0.3
115 | TC | 383 | 367 | 339 | 311 | 284 | 397 | 382 | 354 | 326 | 308 | 403 | 388 | 359 | 332 | 318 | 408 | 393 | 364 | 336 | 327
| SHC | 154 | 181 | 221 | 258 | 283 | 165 | 196 | 243 | 290 | 308 | 170 | 203 | 254 | 304 | 318 | 175 | 210 | 265 | 318 | 327
| kW | 39.6 | 39.3 | 38.9 | 39.1 | 39.9 | 40.2 | 39.9 | 39.4 | 39.3 | 39.7 | 40.5 | 40.1 | 39.6 | 39.5 | 39.6 | 40.7 | 40.3 | 39.7 | 39.8 | 39.7
| BF | 0 | 0.15 | 0.09 | 0.07 | 0.14 | 0.22 | 0.13 | 0.1 | 0.09 | 0.24 | 0.18 | 0.13 | 0.11 | 0.1 | 0.29 | 0.17 | 0.13 | 0.11 | 0.11 | 0.33
48/50 035 (35 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12225 |  |  |  |  | 14000 |  |  |  |  | 15000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 482 | 463 | 430 | 400 | 386 | 491 | 471 | 438 | 406 | 400 | 496 | 475 | 442 | 411 | 406
| SHC | 204 | 244 | 309 | 371 | 386 | 213 | 257 | 329 | 391 | 400 | 218 | 264 | 340 | 400 | 406
| kW | 28.5 | 27.8 | 26.6 | 25.6 | 25.2 | 28.8 | 28 | 26.9 | 25.8 | 25.6 | 28.9 | 28.2 | 27 | 26 | 25.8
| BF | 0.22 | 0.16 | 0.13 | 0.13 | 0.32 | 0.2 | 0.16 | 0.14 | 0.16 | 0.39 | 0.2 | 0.16 | 0.15 | 0.19 | 0.42
85 | TC | 466 | 447 | 417 | 390 | 379 | 475 | 455 | 424 | 397 | 392 | 478 | 458 | 427 | 400 | 398
| SHC | 199 | 239 | 303 | 366 | 379 | 208 | 252 | 323 | 386 | 392 | 212 | 259 | 334 | 395 | 398
| kW | 30.9 | 30.2 | 29.1 | 28.2 | 27.9 | 31.2 | 30.5 | 29.3 | 28.4 | 28.3 | 31.4 | 30.6 | 29.4 | 28.5 | 28.5
| BF | 0.2 | 0.15 | 0.13 | 0.13 | 0.34 | 0.19 | 0.16 | 0.14 | 0.17 | 0.4 | 0.19 | 0.16 | 0.15 | 0.2 | 0.43
95 | TC | 449 | 433 | 405 | 378 | 369 | 456 | 439 | 412 | 385 | 382 | 460 | 442 | 415 | 389 | 388
| SHC | 193 | 234 | 299 | 360 | 369 | 202 | 246 | 319 | 377 | 382 | 206 | 253 | 330 | 381 | 388
| kW | 33.7 | 33.1 | 32.1 | 31.4 | 31.1 | 34 | 33.3 | 32.3 | 31.6 | 31.5 | 34.1 | 33.4 | 32.4 | 31.6 | 31.6
| BF | 0.18 | 0.14 | 0.13 | 0.13 | 0.35 | 0.18 | 0.15 | 0.14 | 0.17 | 0.42 | 0.18 | 0.16 | 0.15 | 0.23 | 0.45
105 | TC | 435 | 418 | 390 | 362 | 356 | 441 | 425 | 396 | 370 | 369 | 444 | 428 | 399 | 376 | 375
| SHC | 189 | 229 | 293 | 348 | 356 | 197 | 241 | 313 | 363 | 369 | 202 | 249 | 324 | 368 | 375
| kW | 37.1 | 36.5 | 35.7 | 35.2 | 35.1 | 37.4 | 36.8 | 35.9 | 35.3 | 35.3 | 37.5 | 36.9 | 36 | 35.4 | 35.5
| BF | 0.17 | 0.14 | 0.13 | 0.15 | 0.38 | 0.17 | 0.15 | 0.14 | 0.21 | 0.44 | 0.17 | 0.15 | 0.15 | 0.26 | 0.46
115 | TC | 417 | 400 | 371 | 345 | 341 | 423 | 406 | 377 | 355 | 353 | 425 | 409 | 380 | 359 | 359
| SHC | 183 | 223 | 286 | 337 | 341 | 192 | 235 | 305 | 347 | 353 | 196 | 242 | 317 | 359 | 359
| kW | 41.1 | 40.6 | 39.9 | 39.8 | 39.8 | 41.4 | 40.9 | 40.1 | 39.6 | 39.9 | 41.5 | 41 | 40.2 | 40 | 40
| BF | 0.16 | 0.14 | 0.13 | 0.17 | 0.4 | 0.16 | 0.14 | 0.14 | 0.25 | 0.46 | 0.17 | 0.15 | 0.15 | 0.26 | 0.49
Performance data (cont)
Cooling Capacities (cont) 48/50 040 (40 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 8000 |  |  |  |  | 10000 |  |  |  |  | 12000 |  |  |  |  | 14000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 477 | 458 | 420 | 383 | 348 | 501 | 483 | 443 | 405 | 367 | 519 | 497 | 458 | 420 | 383 | 533 | 508 | 469 | 431 | 397
| SHC | 195 | 210 | 246 | 282 | 317 | 206 | 220 | 271 | 313 | 348 | 207 | 237 | 290 | 339 | 371 | 210 | 249 | 307 | 364 | 397
| kW | 24.8 | 24.5 | 24 | 23.6 | 23.3 | 25.3 | 24.9 | 24.3 | 23.9 | 23.5 | 25.7 | 25.2 | 24.6 | 24.1 | 23.5 | 26 | 25.5 | 24.8 | 24.2 | 23.9
| BF | 0 | 0 | 0 | 0.33 | 0.26 | 0 | 0 | 0.39 | 0.31 | 0.31 | 0 | 0 | 0.36 | 0.32 | 0.37 | 0 | 0.22 | 0.36 | 0.33 | 0.39
85 | TC | 467 | 447 | 409 | 371 | 338 | 490 | 471 | 431 | 393 | 356 | 507 | 485 | 446 | 407 | 370 | 520 | 497 | 457 | 419 | 388
| SHC | 191 | 206 | 241 | 277 | 311 | 202 | 218 | 266 | 308 | 340 | 203 | 233 | 286 | 334 | 367 | 205 | 246 | 302 | 358 | 387
| kW | 27.5 | 27.3 | 26.9 | 26.6 | 26.3 | 28 | 27.7 | 27.1 | 26.8 | 26.5 | 28.3 | 27.9 | 27.4 | 27 | 26.6 | 28.6 | 28.2 | 27.6 | 27.1 | 26.8
| BF | 0 | 0 | 0 | 0.31 | 0.26 | 0 | 0 | 0.36 | 0.3 | 0.31 | 0 | 0 | 0.35 | 0.31 | 0.35 | 0 | 0.44 | 0.36 | 0.33 | 0.41
95 | TC | 455 | 435 | 397 | 359 | 326 | 479 | 457 | 418 | 379 | 341 | 494 | 470 | 431 | 393 | 360 | 504 | 482 | 441 | 404 | 377
| SHC | 186 | 199 | 237 | 271 | 304 | 190 | 214 | 261 | 302 | 334 | 194 | 229 | 280 | 328 | 356 | 203 | 241 | 296 | 352 | 377
| kW | 30.7 | 30.6 | 30.2 | 30 | 29.8 | 31.2 | 30.9 | 30.5 | 30.2 | 29.9 | 31.5 | 31.1 | 30.7 | 30.4 | 30 | 31.7 | 31.3 | 30.9 | 30.5 | 30.3
| BF | 0 | 0 | 0 | 0.3 | 0.26 | 0 | 0 | 0.34 | 0.29 | 0.3 | 0 | 0 | 0.34 | 0.31 | 0.37 | 0 | 0.42 | 0.35 | 0.32 | 0.42
105 | TC | 440 | 420 | 382 | 346 | 312 | 463 | 440 | 401 | 364 | 330 | 477 | 453 | 413 | 377 | 347 | 486 | 464 | 424 | 387 | 364
| SHC | 180 | 192 | 231 | 265 | 295 | 184 | 209 | 254 | 295 | 321 | 189 | 223 | 269 | 321 | 347 | 199 | 235 | 289 | 345 | 364
| kW | 34.4 | 34.4 | 34.1 | 34.2 | 34.5 | 34.9 | 34.7 | 34.4 | 34.2 | 34.3 | 35.1 | 34.9 | 34.6 | 34.3 | 34.4 | 35.3 | 35.1 | 34.8 | 34.3 | 34.4
| BF | 0 | 0 | 0.42 | 0.29 | 0.27 | 0 | 0 | 0.32 | 0.29 | 0.33 | 0 | 0.44 | 0.33 | 0.3 | 0.38 | 0 | 0.39 | 0.35 | 0.32 | 0.44
115 | TC | 422 | 406 | 365 | 330 | 297 | 443 | 420 | 383 | 347 | 315 | 456 | 434 | 395 | 359 | 334 | 466 | 443 | 404 | 368 | 350
| SHC | 174 | 187 | 224 | 257 | 283 | 178 | 203 | 247 | 288 | 312 | 183 | 217 | 265 | 314 | 334 | 193 | 229 | 282 | 336 | 350
| kW | 38.7 | 38.4 | 38.9 | 39.4 | 40.3 | 39.1 | 39 | 38.9 | 39.2 | 39.8 | 39.3 | 39.2 | 39.1 | 39.1 | 39.6 | 39.5 | 39.4 | 39.1 | 39.2 | 39.4
| BF | 0 | 0 | 0.34 | 0.28 | 0.29 | 0 | 0 | 0.31 | 0.28 | 0.34 | 0 | 0.39 | 0.32 | 0.29 | 0.4 | 0 | 0.37 | 0.34 | 0.32 | 0.46
48/50 040 (40 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 16000 |  |  |  |  | 18000 |  |  |  |  | 20000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 542 | 518 | 478 | 440 | 413 | 549 | 525 | 486 | 447 | 426 | 557 | 531 | 491 | 453 | 438
| SHC | 220 | 261 | 324 | 386 | 413 | 228 | 272 | 339 | 406 | 426 | 237 | 282 | 354 | 424 | 438
| kW | 26.2 | 25.7 | 24.9 | 24.4 | 24 | 26.4 | 25.8 | 25.1 | 24.5 | 24.2 | 26.5 | 25.9 | 25.2 | 24.6 | 24.4
| BF | 0 | 0.43 | 0.37 | 0.35 | 0.45 | 0 | 0.41 | 0.38 | 0.37 | 0.49 | 0.49 | 0.41 | 0.39 | 0.39 | 0.53
85 | TC | 527 | 505 | 465 | 427 | 402 | 535 | 512 | 472 | 434 | 416 | 541 | 518 | 478 | 440 | 427
| SHC | 216 | 257 | 319 | 380 | 402 | 223 | 268 | 334 | 401 | 416 | 232 | 277 | 350 | 415 | 427
| kW | 28.8 | 28.3 | 27.7 | 27.3 | 27 | 29 | 28.5 | 27.8 | 27.3 | 27.1 | 29.1 | 28.6 | 27.9 | 27.5 | 27.3
| BF | 0 | 0.41 | 0.37 | 0.35 | 0.46 | 0.26 | 0.41 | 0.38 | 0.36 | 0.5 | 0.48 | 0.41 | 0.39 | 0.39 | 0.54
95 | TC | 512 | 490 | 450 | 412 | 391 | 520 | 496 | 456 | 419 | 404 | 527 | 502 | 462 | 423 | 415
| SHC | 212 | 252 | 313 | 373 | 391 | 219 | 263 | 329 | 391 | 404 | 227 | 272 | 344 | 402 | 415
| kW | 31.8 | 31.5 | 31 | 30.6 | 30.4 | 32.1 | 31.6 | 31.1 | 30.7 | 30.5 | 32.2 | 31.8 | 31.2 | 30.8 | 30.7
| BF | 0 | 0.4 | 0.36 | 0.35 | 0.47 | 0.53 | 0.4 | 0.37 | 0.37 | 0.52 | 0.46 | 0.4 | 0.38 | 0.39 | 0.55
105 | TC | 494 | 471 | 432 | 394 | 378 | 502 | 477 | 438 | 401 | 391 | 507 | 483 | 443 | 405 | 400
| SHC | 208 | 246 | 306 | 365 | 378 | 215 | 258 | 322 | 378 | 391 | 222 | 267 | 337 | 395 | 400
| kW | 35.4 | 35.2 | 34.8 | 34.5 | 34.4 | 35.7 | 35.2 | 34.9 | 34.5 | 34.4 | 35.8 | 35.5 | 35 | 34.6 | 34.6
| BF | 0.5 | 0.38 | 0.35 | 0.35 | 0.49 | 0.46 | 0.37 | 0.37 | 0.38 | 0.53 | 0.44 | 0.39 | 0.38 | 0.4 | 0.57
115 | TC | 473 | 450 | 411 | 375 | 365 | 480 | 456 | 417 | 382 | 375 | 484 | 461 | 421 | 389 | 384
| SHC | 201 | 240 | 299 | 354 | 365 | 209 | 250 | 314 | 363 | 375 | 215 | 260 | 330 | 373 | 384
| kW | 39.7 | 39.6 | 39.1 | 39.3 | 39 | 39.9 | 39.7 | 39.2 | 39.3 | 39.3 | 40 | 39.7 | 39.2 | 39 | 39.3
| BF | 0.47 | 0.37 | 0.35 | 0.35 | 0.51 | 0.42 | 0.37 | 0.36 | 0.4 | 0.55 | 0.42 | 0.38 | 0.37 | 0.45 | 0.59
Temp (F) Air Entering Condenser (Edb)
|  | 8000 |  |  |  |  | 10000 |  |  |  |  | 12000 |  |  |  |  | 14000
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 502 | 480 | 439 | 404 | 369 | 531 | 504 | 464 | 427 | 395 | 550 | 523 | 480 | 443 | 417 | 565 | 537 | 493 | 456 | 436
| SHC | 207 | 227 | 273 | 315 | 352 | 217 | 249 | 301 | 353 | 389 | 228 | 266 | 326 | 387 | 417 | 239 | 282 | 349 | 417 | 436
| kW | 25.5 | 25 | 24.2 | 23.5 | 23.1 | 26.1 | 25.5 | 24.6 | 24 | 23.5 | 26.4 | 25.9 | 25 | 24.2 | 23.8 | 26.7 | 26.1 | 25.2 | 24.5 | 24.2
| BF | 0 | 0 | 0.15 | 0.11 | 0.12 | 0 | 0.22 | 0.14 | 0.12 | 0.18 | 0.15 | 0.19 | 0.15 | 0.13 | 0.25 | 0.12 | 0.18 | 0.16 | 0.16 | 0.33
85 | TC | 490 | 469 | 432 | 397 | 360 | 518 | 493 | 456 | 419 | 386 | 536 | 511 | 472 | 435 | 410 | 551 | 523 | 484 | 447 | 429
| SHC | 202 | 224 | 270 | 312 | 346 | 211 | 245 | 297 | 349 | 382 | 223 | 262 | 322 | 383 | 410 | 235 | 277 | 346 | 412 | 429
| kW | 28 | 27.6 | 26.9 | 26.4 | 26.1 | 28.6 | 28.1 | 27.3 | 26.8 | 26.3 | 29 | 28.4 | 27.6 | 27 | 26.7 | 29.3 | 28.6 | 27.9 | 27.3 | 27
| BF | 0 | 0 | 0.15 | 0.11 | 0.12 | 0 | 0.21 | 0.14 | 0.12 | 0.19 | 0.13 | 0.18 | 0.15 | 0.13 | 0.27 | 0.26 | 0.17 | 0.16 | 0.16 | 0.34
95 | TC | 480 | 461 | 423 | 387 | 350 | 507 | 484 | 445 | 408 | 375 | 526 | 501 | 461 | 423 | 400 | 539 | 514 | 472 | 434 | 419
| SHC | 197 | 221 | 265 | 307 | 339 | 208 | 242 | 293 | 344 | 375 | 220 | 258 | 318 | 377 | 400 | 231 | 273 | 341 | 404 | 419
| kW | 31.1 | 30.7 | 30.3 | 30 | 29.9 | 31.7 | 31.2 | 30.6 | 30.3 | 30.1 | 32.1 | 31.6 | 31 | 30.6 | 30.3 | 32.4 | 31.9 | 31.2 | 30.8 | 30.6
| BF | 0 | 0 | 0.15 | 0.11 | 0.13 | 0 | 0.2 | 0.14 | 0.12 | 0.19 | 0.12 | 0.17 | 0.15 | 0.13 | 0.28 | 0.24 | 0.18 | 0.16 | 0.16 | 0.36
105 | TC | 470 | 448 | 409 | 372 | 336 | 495 | 471 | 431 | 393 | 363 | 512 | 485 | 445 | 406 | 387 | 524 | 498 | 455 | 416 | 406
| SHC | 193 | 217 | 259 | 300 | 329 | 203 | 237 | 287 | 337 | 363 | 216 | 253 | 312 | 369 | 387 | 226 | 267 | 336 | 393 | 406
| kW | 34.8 | 34.6 | 34.5 | 34.5 | 35.7 | 35.5 | 35.2 | 34.8 | 34.7 | 35 | 36 | 35.5 | 35.1 | 35 | 35 | 36.4 | 36 | 35.2 | 35.2 | 35.1
| BF | 0 | 0.12 | 0.14 | 0.1 | 0.14 | 0 | 0.18 | 0.13 | 0.11 | 0.22 | 0.11 | 0.16 | 0.14 | 0.13 | 0.31 | 0.22 | 0.18 | 0.15 | 0.17 | 0.38
115 | TC | 454 | 431 | 392 | 355 | 319 | 478 | 452 | 412 | 373 | 349 | 491 | 466 | 425 | 386 | 372 | 502 | 476 | 433 | 397 | 390
| SHC | 186 | 211 | 252 | 291 | 318 | 198 | 230 | 279 | 328 | 349 | 209 | 245 | 304 | 358 | 372 | 219 | 260 | 328 | 378 | 390
| kW | 39.5 | 39.6 | 40.1 | 41.4 | 44 | 40.4 | 40.1 | 40.3 | 41.3 | 42.6 | 40.8 | 40.6 | 40.5 | 41.8 | 41.8 | 41.3 | 41 | 40.5 | 41.7 | 40.9
| BF | 0 | 0.09 | 0.13 | 0.1 | 0.15 | 0.14 | 0.16 | 0.13 | 0.11 | 0.25 | 0.23 | 0.16 | 0.14 | 0.14 | 0.34 | 0.21 | 0.17 | 0.14 | 0.2 | 0.4
48/50 040 (40 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb)
|  | 16000 |  |  |  |  | 18000 |  |  |  |  | 20000
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 577 | 548 | 503 | 463 | 453 | 585 | 556 | 511 | 474 | 466 | 593 | 563 | 517 | 481 | 479
| SHC | 250 | 296 | 372 | 438 | 453 | 259 | 309 | 393 | 458 | 466 | 268 | 322 | 413 | 475 | 479
| kW | 27 | 26.4 | 25.4 | 24.7 | 24.5 | 27.2 | 26.5 | 25.6 | 24.9 | 24.7 | 27.3 | 26.7 | 25.7 | 25 | 25
| BF | 0.24 | 0.19 | 0.17 | 0.19 | 0.39 | 0.23 | 0.21 | 0.19 | 0.23 | 0.44 | 0.23 | 0.22 | 0.2 | 0.27 | 0.49
85 | TC | 563 | 536 | 493 | 455 | 446 | 571 | 544 | 501 | 465 | 459 | 579 | 551 | 507 | 472 | 471
| SHC | 245 | 291 | 368 | 433 | 446 | 255 | 304 | 389 | 452 | 459 | 264 | 317 | 410 | 472 | 471
| kW | 29.5 | 29 | 28.1 | 27.4 | 27.3 | 29.7 | 29.1 | 28.3 | 27.7 | 27.5 | 29.9 | 29.3 | 28.4 | 27.7 | 27.7
| BF | 0.23 | 0.2 | 0.17 | 0.2 | 0.4 | 0.22 | 0.21 | 0.19 | 0.24 | 0.45 | 0.22 | 0.22 | 0.2 | 0.27 | 0.49
95 | TC | 550 | 524 | 481 | 444 | 436 | 559 | 532 | 487 | 453 | 449 | 566 | 538 | 494 | 461 | 461
| SHC | 241 | 287 | 363 | 421 | 436 | 251 | 300 | 388 | 441 | 449 | 260 | 313 | 404 | 461 | 461
| kW | 32.7 | 32.2 | 31.4 | 31 | 30.8 | 32.9 | 32.4 | 31.4 | 31.1 | 31 | 33.1 | 32.5 | 31.7 | 31.2 | 31.2
| BF | 0.22 | 0.19 | 0.17 | 0.22 | 0.42 | 0.22 | 0.2 | 0.16 | 0.26 | 0.46 | 0.22 | 0.21 | 0.2 | 0.29 | 0.51
105 | TC | 533 | 507 | 462 | 427 | 422 | 541 | 514 | 470 | 437 | 435 | 547 | 520 | 476 | 447 | 446
| SHC | 236 | 281 | 360 | 414 | 422 | 245 | 294 | 380 | 431 | 435 | 254 | 307 | 396 | 446 | 446
| kW | 36.7 | 36.3 | 35.3 | 35.4 | 35 | 37 | 36.5 | 35.6 | 35.2 | 35.3 | 37.2 | 36.6 | 35.9 | 35.5 | 35.5
| BF | 0.21 | 0.19 | 0.15 | 0.22 | 0.43 | 0.21 | 0.2 | 0.17 | 0.27 | 0.48 | 0.21 | 0.21 | 0.2 | 0.31 | 0.52
115 | TC | 511 | 484 | 441 | 407 | 405 | 517 | 491 | 447 | 418 | 417 | 523 | 496 | 452 | 428 | 428
| SHC | 229 | 273 | 350 | 401 | 405 | 238 | 286 | 371 | 416 | 417 | 245 | 299 | 392 | 428 | 428
| kW | 41.8 | 41.4 | 40.7 | 41.6 | 41.4 | 42.1 | 41.6 | 41 | 41.2 | 41.3 | 42.7 | 41.8 | 41 | 41.3 | 41.3
| BF | 0.2 | 0.19 | 0.16 | 0.23 | 0.46 | 0.2 | 0.2 | 0.17 | 0.29 | 0.5 | 0.22 | 0.21 | 0.18 | 0.34 | 0.54
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 10000 |  |  |  |  | 12500 |  |  |  |  | 15000 |  |  |  |  | 17500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 633 | 606 | 558 | 512 | 466 | 665 | 635 | 587 | 541 | 494 | 690 | 656 | 607 | 561 | 520 | 707 | 672 | 622 | 576 | 541
| SHC | 260 | 281 | 338 | 389 | 436 | 273 | 303 | 369 | 431 | 480 | 277 | 323 | 398 | 470 | 518 | 288 | 341 | 423 | 506 | 541
| kW | 33.8 | 33.3 | 32.5 | 32.1 | 31.9 | 34.3 | 33.8 | 33 | 32.5 | 32.2 | 34.7 | 34.2 | 33.3 | 32.8 | 32.4 | 35 | 34.4 | 33.6 | 33 | 32.6
| BF | 0 | 0 | 0.09 | 0.18 | 0.15 | 0 | 0 | 0.23 | 0.19 | 0.21 | 0 | 0.13 | 0.23 | 0.2 | 0.28 | 0 | 0.3 | 0.24 | 0.21 | 0.33
85 | TC | 614 | 592 | 543 | 495 | 450 | 646 | 618 | 571 | 523 | 477 | 667 | 637 | 590 | 542 | 501 | 681 | 650 | 605 | 557 | 526
| SHC | 251 | 273 | 331 | 381 | 427 | 257 | 297 | 363 | 423 | 461 | 268 | 316 | 391 | 461 | 500 | 282 | 333 | 417 | 497 | 526
| kW | 37.4 | 37 | 36.4 | 36.2 | 36 | 38 | 37.5 | 36.8 | 36.5 | 36 | 38.4 | 37.8 | 37.1 | 36.7 | 36.5 | 38.7 | 38.1 | 37.4 | 36.9 | 36.7
| BF | 0 | 0 | 0.26 | 0.17 | 0.15 | 0 | 0 | 0.22 | 0.18 | 0.24 | 0 | 0.32 | 0.22 | 0.2 | 0.29 | 0.2 | 0.28 | 0.23 | 0.21 | 0.35
95 | TC | 598 | 573 | 525 | 476 | 428 | 628 | 600 | 551 | 502 | 458 | 646 | 618 | 570 | 520 | 484 | 658 | 632 | 583 | 534 | 508
| SHC | 245 | 268 | 323 | 371 | 413 | 251 | 291 | 355 | 413 | 458 | 262 | 310 | 383 | 452 | 484 | 275 | 327 | 408 | 487 | 508
| kW | 41.8 | 41.4 | 41.2 | 41.1 | 41.2 | 42.4 | 42 | 41.5 | 41.4 | 41.3 | 42.7 | 42.3 | 41.8 | 41.6 | 41.4 | 43 | 42.6 | 42.1 | 41.8 | 41.7
| BF | 0 | 0 | 0.23 | 0.16 | 0.16 | 0 | 0.14 | 0.21 | 0.18 | 0.24 | 0 | 0.29 | 0.21 | 0.19 | 0.31 | 0.17 | 0.27 | 0.23 | 0.21 | 0.38
105 | TC | 578 | 552 | 502 | 454 | 408 | 606 | 577 | 527 | 478 | 436 | 623 | 594 | 544 | 495 | 465 | 635 | 608 | 557 | 508 | 488
| SHC | 237 | 261 | 314 | 360 | 398 | 243 | 283 | 345 | 402 | 436 | 256 | 302 | 372 | 441 | 465 | 268 | 319 | 398 | 474 | 488
| kW | 47.1 | 46.9 | 46.8 | 47.2 | 48.7 | 47.6 | 47.4 | 47.2 | 47.3 | 48.2 | 47.9 | 47.6 | 47.5 | 47.3 | 47.8 | 48.1 | 47.9 | 47.7 | 47.5 | 47.6
| BF | 0 | 0 | 0.2 | 0.16 | 0.17 | 0 | 0.12 | 0.2 | 0.17 | 0.25 | 0 | 0.27 | 0.21 | 0.19 | 0.33 | 0.14 | 0.26 | 0.22 | 0.22 | 0.4
115 | TC | 553 | 526 | 477 | 429 | 382 | 580 | 549 | 500 | 451 | 416 | 595 | 566 | 516 | 467 | 443 | 607 | 578 | 528 | 479 | 466
| SHC | 227 | 253 | 303 | 349 | 379 | 234 | 273 | 334 | 390 | 416 | 248 | 292 | 361 | 428 | 443 | 259 | 309 | 387 | 455 | 466
| kW | 53.2 | 53.3 | 53.8 | 55.5 | 58 | 53.7 | 53.6 | 53.9 | 55.3 | 56.9 | 53.9 | 53.9 | 54.1 | 55.3 | 56 | 54.1 | 54.1 | 54.1 | 55 | 55.5
| BF | 0 | 0 | 0.18 | 0.15 | 0.2 | 0 | 0.27 | 0.19 | 0.17 | 0.28 | 0.16 | 0.25 | 0.2 | 0.19 | 0.36 | 0.33 | 0.24 | 0.22 | 0.23 | 0.43
48/50 050 (50 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
20000
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 719 | 685 | 633 | 587 | 562
| SHC | 301 | 357 | 448 | 539 | 562
| kW | 35.2 | 34.7 | 33.8 | 33.2 | 32.9
| BF | 0.17 | 0.29 | 0.25 | 0.23 | 0.4
85 | TC | 693 | 662 | 616 | 568 | 547
| SHC | 293 | 350 | 441 | 529 | 547
| kW | 38.9 | 38.3 | 37.6 | 37.1 | 36.9
| BF | 0.15 | 0.28 | 0.24 | 0.24 | 0.41
95 | TC | 668 | 643 | 594 | 543 | 528
| SHC | 286 | 343 | 433 | 515 | 528
| kW | 43.2 | 42.8 | 42.2 | 41.9 | 41.8
| BF | 0.35 | 0.27 | 0.24 | 0.24 | 0.43
105 | TC | 645 | 618 | 568 | 519 | 507
| SHC | 279 | 335 | 423 | 498 | 507
| kW | 48.3 | 48.1 | 47.8 | 47.5 | 47.5
| BF | 0.32 | 0.26 | 0.24 | 0.26 | 0.45
115 | TC | 615 | 587 | 537 | 491 | 484
| SHC | 270 | 325 | 412 | 480 | 484
| kW | 54.2 | 54.3 | 54.1 | 55 | 55.1
| BF | 0.3 | 0.25 | 0.23 | 0.28 | 0.48
Performance data (cont)
Cooling Capacities (cont) 48/50 050 (50 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 10000 |  |  |  |  | 12500 |  |  |  |  | 15000 |  |  |  |  | 17500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 638 | 609 | 560 | 517 | 476 | 673 | 643 | 590 | 546 | 503 | 698 | 665 | 611 | 566 | 527 | 715 | 677 | 627 | 581 | 552
| SHC | 264 | 289 | 343 | 397 | 446 | 274 | 312 | 376 | 441 | 490 | 284 | 332 | 406 | 481 | 526 | 298 | 351 | 434 | 518 | 552
| kW | 33.7 | 33.3 | 32.4 | 31.7 | 31.3 | 34.3 | 33.8 | 32.9 | 32.2 | 31.6 | 34.8 | 34.2 | 33.3 | 32.5 | 31.9 | 35.1 | 34.5 | 33.5 | 32.8 | 32.3
| BF | 0 | 0 | 0.2 | 0.14 | 0.13 | 0 | 0.13 | 0.19 | 0.15 | 0.18 | 0 | 0.25 | 0.19 | 0.17 | 0.25 | 0.16 | 0.22 | 0.2 | 0.18 | 0.32
85 | TC | 622 | 595 | 549 | 505 | 461 | 654 | 624 | 578 | 533 | 489 | 678 | 646 | 598 | 552 | 515 | 695 | 661 | 613 | 567 | 540
| SHC | 256 | 280 | 338 | 391 | 437 | 266 | 305 | 371 | 435 | 481 | 277 | 326 | 400 | 475 | 515 | 292 | 345 | 428 | 511 | 540
| kW | 37.4 | 36.9 | 36.1 | 35.5 | 35.4 | 38 | 37.4 | 36.6 | 36 | 35.6 | 38.4 | 37.8 | 37 | 36.3 | 35.9 | 38.8 | 38.1 | 37.2 | 36.6 | 36.2
| BF | 0 | 0 | 0.19 | 0.14 | 0.13 | 0 | 0.12 | 0.18 | 0.15 | 0.19 | 0 | 0.23 | 0.19 | 0.16 | 0.26 | 0.14 | 0.22 | 0.2 | 0.19 | 0.34
95 | TC | 606 | 582 | 535 | 488 | 440 | 638 | 610 | 562 | 515 | 472 | 658 | 630 | 582 | 534 | 500 | 677 | 646 | 596 | 548 | 525
| SHC | 248 | 277 | 332 | 383 | 424 | 257 | 300 | 364 | 426 | 465 | 273 | 320 | 394 | 466 | 500 | 287 | 339 | 421 | 502 | 525
| kW | 41.6 | 41.3 | 40.7 | 40.5 | 40.4 | 42.3 | 41.9 | 41.3 | 40.9 | 40.5 | 42.7 | 42.3 | 41.6 | 41.3 | 41 | 43.2 | 42.7 | 41.9 | 41.6 | 41.2
| BF | 0 | 0 | 0.18 | 0.13 | 0.13 | 0 | 0.11 | 0.17 | 0.15 | 0.22 | 0 | 0.23 | 0.18 | 0.16 | 0.28 | 0.31 | 0.21 | 0.19 | 0.19 | 0.36
105 | TC | 591 | 564 | 515 | 467 | 423 | 621 | 591 | 541 | 492 | 452 | 641 | 611 | 560 | 510 | 481 | 656 | 625 | 573 | 523 | 505
| SHC | 242 | 271 | 323 | 372 | 407 | 253 | 294 | 355 | 416 | 451 | 267 | 313 | 384 | 455 | 481 | 280 | 331 | 412 | 488 | 505
| kW | 46.9 | 46.8 | 46.6 | 46.6 | 47.6 | 47.7 | 47.5 | 47.1 | 46.9 | 47.4 | 48.3 | 48 | 47.5 | 47.2 | 47.3 | 48.7 | 48.3 | 47.7 | 47.5 | 47.3
| BF | 0 | 0 | 0.16 | 0.13 | 0.17 | 0 | 0.23 | 0.17 | 0.14 | 0.23 | 0.16 | 0.21 | 0.18 | 0.16 | 0.31 | 0.28 | 0.21 | 0.19 | 0.19 | 0.38
115 | TC | 569 | 540 | 490 | 443 | 400 | 596 | 565 | 514 | 466 | 431 | 614 | 583 | 531 | 479 | 459 | 627 | 595 | 542 | 493 | 483
| SHC | 234 | 262 | 312 | 360 | 394 | 244 | 284 | 344 | 403 | 431 | 259 | 304 | 374 | 442 | 459 | 271 | 321 | 402 | 470 | 483
| kW | 53.4 | 53.5 | 54.2 | 55.9 | 59.3 | 54.2 | 54.1 | 54.4 | 55.9 | 57.2 | 54.9 | 54.6 | 54.7 | 55.7 | 56.4 | 55.4 | 55.1 | 54.6 | 55.8 | 56
| BF | 0 | 0.12 | 0.15 | 0.12 | 0.17 | 0 | 0.21 | 0.16 | 0.14 | 0.26 | 0.13 | 0.2 | 0.17 | 0.16 | 0.34 | 0.25 | 0.21 | 0.18 | 0.2 | 0.41
48/50 050 (50 TON) HIGH- CAPACITY COIL — STANDARD MODE (cont)
20000
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm 20,000 Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 730 | 695 | 639 | 593 | 572
| SHC | 311 | 368 | 460 | 549 | 572
| kW | 35.3 | 34.7 | 33.8 | 33 | 32.6
| BF | 0.31 | 0.24 | 0.21 | 0.21 | 0.39
85 | TC | 707 | 675 | 624 | 578 | 561
| SHC | 305 | 361 | 454 | 541 | 561
| kW | 39 | 38.4 | 37.5 | 36.8 | 36.5
| BF | 0.28 | 0.23 | 0.21 | 0.22 | 0.4
95 | TC | 690 | 658 | 606 | 558 | 545
| SHC | 299 | 356 | 450 | 524 | 545
| kW | 43.5 | 42.9 | 42.1 | 41.5 | 41.4
| BF | 0.27 | 0.23 | 0.2 | 0.23 | 0.42
105 | TC | 668 | 635 | 582 | 534 | 525
| SHC | 292 | 348 | 440 | 514 | 525
| kW | 49.1 | 48.6 | 47.8 | 47.7 | 47.4
| BF | 0.25 | 0.22 | 0.2 | 0.23 | 0.44
115 | TC | 638 | 606 | 553 | 507 | 502
| SHC | 283 | 337 | 428 | 496 | 502
| kW | 55.8 | 55.4 | 55.2 | 56 | 55.7
| BF | 0.24 | 0.22 | 0.2 | 0.25 | 0.46
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 055 (55 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 11000 |  |  |  |  | 13750 |  |  |  |  | 16500 |  |  |  |  | 19250
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 685 | 654 | 604 | 558 | 510 | 722 | 686 | 636 | 588 | 538 | 744 | 709 | 656 | 609 | 572 | 761 | 726 | 672 | 625 | 598
| SHC | 281 | 311 | 375 | 434 | 486 | 292 | 338 | 412 | 485 | 525 | 307 | 361 | 446 | 531 | 572 | 322 | 381 | 477 | 572 | 598
| kW | 37.2 | 36.5 | 35.5 | 34.8 | 34.6 | 37.9 | 37.2 | 36.1 | 35.3 | 34.6 | 38.4 | 37.6 | 36.5 | 35.7 | 35.2 | 38.8 | 38 | 36.9 | 36.1 | 35.6
| BF | 0 | 0 | 0.15 | 0.11 | 0.11 | 0 | 0.24 | 0.14 | 0.12 | 0.18 | 0 | 0.19 | 0.15 | 0.13 | 0.25 | 0.29 | 0.19 | 0.16 | 0.15 | 0.33
85 | TC | 663 | 636 | 588 | 540 | 491 | 697 | 665 | 618 | 570 | 519 | 717 | 687 | 638 | 589 | 556 | 732 | 702 | 653 | 604 | 582
| SHC | 271 | 304 | 368 | 425 | 474 | 281 | 330 | 405 | 476 | 506 | 299 | 352 | 438 | 522 | 556 | 313 | 373 | 470 | 562 | 582
| kW | 41 | 40.5 | 39.7 | 39.3 | 39.2 | 41.8 | 41.1 | 40.3 | 39.8 | 39.1 | 42.3 | 41.6 | 40.7 | 40.1 | 39.7 | 42.6 | 41.9 | 41 | 40.5 | 40
| BF | 0 | 0 | 0.15 | 0.11 | 0.11 | 0 | 0.21 | 0.14 | 0.12 | 0.19 | 0.13 | 0.19 | 0.15 | 0.13 | 0.28 | 0.26 | 0.18 | 0.16 | 0.16 | 0.35
95 | TC | 646 | 619 | 570 | 520 | 466 | 676 | 647 | 598 | 547 | 504 | 694 | 667 | 617 | 566 | 537 | 708 | 681 | 631 | 580 | 563
| SHC | 264 | 298 | 359 | 415 | 451 | 276 | 323 | 396 | 466 | 504 | 292 | 346 | 430 | 505 | 537 | 306 | 366 | 461 | 549 | 563
| kW | 45.7 | 45.3 | 44.9 | 44.7 | 45.6 | 46.4 | 45.9 | 45.4 | 45.2 | 45.2 | 46.8 | 46.4 | 45.8 | 45.5 | 45.2 | 47.1 | 46.7 | 46.1 | 45.9 | 45.4
| BF | 0 | 0 | 0.14 | 0.11 | 0.12 | 0 | 0.19 | 0.13 | 0.11 | 0.21 | 0.11 | 0.18 | 0.14 | 0.13 | 0.3 | 0.23 | 0.18 | 0.16 | 0.16 | 0.37
105 | TC | 626 | 597 | 546 | 495 | 443 | 654 | 624 | 572 | 522 | 485 | 671 | 642 | 590 | 539 | 516 | 686 | 655 | 604 | 552 | 542
| SHC | 256 | 290 | 349 | 404 | 443 | 269 | 315 | 386 | 454 | 485 | 284 | 337 | 419 | 497 | 516 | 299 | 357 | 451 | 533 | 542
| kW | 51.3 | 51.2 | 51.1 | 52.1 | 54.4 | 51.9 | 51.7 | 51.6 | 52 | 53 | 52.4 | 52.2 | 51.9 | 52.5 | 52.5 | 52.8 | 52.5 | 52.2 | 52.5 | 51.9
| BF | 0 | 0.1 | 0.13 | 0.1 | 0.13 | 0 | 0.18 | 0.13 | 0.11 | 0.24 | 0.26 | 0.17 | 0.14 | 0.14 | 0.33 | 0.22 | 0.17 | 0.15 | 0.17 | 0.39
115 | TC | 602 | 570 | 519 | 468 | — | 626 | 595 | 544 | 492 | — | 643 | 612 | 561 | 508 | 494 | 657 | 625 | 573 | 521 | 517
| SHC | 243 | 280 | 337 | 390 | — | 261 | 305 | 374 | 440 | — | 275 | 326 | 407 | 481 | 494 | 289 | 347 | 439 | 513 | 517
| kW | 58.1 | 58.2 | 59.6 | 62.5 | — | 58.5 | 58.6 | 59.7 | 62.3 | — | 58.9 | 59 | 59.8 | 62.2 | 61 | 59.5 | 59.3 | 59.9 | 61.3 | 61.1
| BF | 0 | 0.22 | 0.12 | 0.1 | — | 0.12 | 0.16 | 0.12 | 0.11 | — | 0.23 | 0.16 | 0.14 | 0.14 | 0.36 | 0.2 | 0.16 | 0.15 | 0.19 | 0.42
48/50 055 (55 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 22000 |  |  |  |  | 24750
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 773 | 738 | 684 | 636 | 620 | 785 | 748 | 693 | 642 | 638
| SHC | 335 | 401 | 508 | 607 | 620 | 348 | 419 | 536 | 627 | 638
| kW | 39.1 | 38.3 | 37.1 | 36.3 | 35.9 | 39.3 | 38.5 | 37.3 | 36.3 | 36.3
| BF | 0.25 | 0.19 | 0.17 | 0.18 | 0.39 | 0.24 | 0.2 | 0.18 | 0.23 | 0.45
85 | TC | 745 | 712 | 664 | 615 | 604 | 755 | 721 | 673 | 623 | 621
| SHC | 326 | 392 | 500 | 594 | 604 | 339 | 411 | 529 | 614 | 621
| kW | 42.9 | 42.2 | 41.3 | 40.6 | 40.2 | 43.2 | 42.3 | 41.5 | 40.6 | 40.6
| BF | 0.23 | 0.19 | 0.17 | 0.19 | 0.41 | 0.23 | 0.19 | 0.18 | 0.23 | 0.46
95 | TC | 722 | 691 | 642 | 592 | 585 | 732 | 701 | 650 | 602 | 602
| SHC | 319 | 385 | 491 | 579 | 585 | 331 | 402 | 520 | 595 | 602
| kW | 47.5 | 46.9 | 46.3 | 45.9 | 45.6 | 47.8 | 47.2 | 46.5 | 45.8 | 45.9
| BF | 0.22 | 0.18 | 0.17 | 0.2 | 0.43 | 0.22 | 0.2 | 0.18 | 0.25 | 0.48
105 | TC | 697 | 664 | 614 | 565 | 562 | 706 | 674 | 622 | 578 | 578
| SHC | 311 | 377 | 481 | 555 | 562 | 324 | 393 | 509 | 572 | 578
| kW | 53.1 | 52.6 | 52.4 | 51.9 | 52 | 53.4 | 53 | 52.6 | 52.1 | 52.1
| BF | 0.21 | 0.17 | 0.17 | 0.23 | 0.45 | 0.21 | 0.19 | 0.18 | 0.28 | 0.5
115 | TC | 666 | 633 | 582 | 539 | 536 | 674 | 640 | 590 | 554 | 553
| SHC | 302 | 365 | 469 | 532 | 536 | 314 | 383 | 497 | 550 | 553
| kW | 59.8 | 59.1 | 59.9 | 60.4 | 60.8 | 60 | 59.2 | 60 | 60.4 | 60.5
| BF | 0.2 | 0.17 | 0.16 | 0.26 | 0.48 | 0.2 | 0.18 | 0.18 | 0.32 | 0.52
Cooling Capacities (cont) 48/50 055 (55 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 11000 |  |  |  |  | 13750 |  |  |  |  | 16500 |  |  |  |  | 19250
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 693 | 657 | 606 | 556 | 513 | 731 | 694 | 639 | 586 | 542 | 757 | 719 | 661 | 609 | 575 | 776 | 737 | 678 | 625 | 602
| SHC | 285 | 318 | 379 | 438 | 494 | 299 | 346 | 419 | 490 | 542 | 318 | 369 | 454 | 539 | 575 | 334 | 390 | 488 | 581 | 602
| kW | 37.2 | 36.5 | 35.4 | 34.4 | 33.6 | 38 | 37.2 | 36.1 | 35 | 34.2 | 38.5 | 37.7 | 36.5 | 35.5 | 34.9 | 38.8 | 38.1 | 36.9 | 35.8 | 35.4
| BF | 0 | 0.08 | 0.12 | 0.09 | 0.09 | 0 | 0.15 | 0.11 | 0.09 | 0.15 | 0.08 | 0.15 | 0.12 | 0.11 | 0.25 | 0.18 | 0.16 | 0.13 | 0.13 | 0.33
85 | TC | 675 | 641 | 591 | 544 | 501 | 709 | 674 | 623 | 573 | 532 | 735 | 699 | 645 | 596 | 565 | 757 | 717 | 661 | 609 | 591
| SHC | 277 | 312 | 372 | 432 | 486 | 292 | 339 | 412 | 484 | 532 | 311 | 361 | 447 | 532 | 565 | 327 | 383 | 481 | 575 | 591
| kW | 41.1 | 40.4 | 39.3 | 38.5 | 37.9 | 41.9 | 41.1 | 40 | 39 | 38.3 | 42.4 | 41.6 | 40.5 | 39.6 | 38.9 | 42.9 | 42 | 40.9 | 39.8 | 39.5
| BF | 0 | 0.08 | 0.11 | 0.08 | 0.09 | 0 | 0.14 | 0.11 | 0.09 | 0.17 | 0.21 | 0.15 | 0.12 | 0.11 | 0.27 | 0.17 | 0.15 | 0.13 | 0.13 | 0.34
95 | TC | 659 | 627 | 578 | 530 | 487 | 692 | 659 | 608 | 558 | 519 | 719 | 682 | 628 | 576 | 551 | 737 | 699 | 644 | 592 | 577
| SHC | 271 | 306 | 367 | 425 | 480 | 287 | 333 | 405 | 476 | 519 | 305 | 355 | 440 | 525 | 551 | 321 | 376 | 474 | 561 | 577
| kW | 45.7 | 45.1 | 44.3 | 43.5 | 43.4 | 46.5 | 45.9 | 44.9 | 44.1 | 43.5 | 47.4 | 46.5 | 45.5 | 44.5 | 44.1 | 48 | 47 | 45.9 | 44.9 | 44.6
| BF | 0 | 0.06 | 0.11 | 0.08 | 0.11 | 0.11 | 0.13 | 0.11 | 0.1 | 0.19 | 0.19 | 0.14 | 0.12 | 0.1 | 0.28 | 0.17 | 0.15 | 0.13 | 0.15 | 0.36
105 | TC | 641 | 610 | 558 | 507 | 463 | 674 | 639 | 586 | 534 | 503 | 696 | 659 | 605 | 555 | 533 | 711 | 674 | 619 | 568 | 558
| SHC | 264 | 299 | 358 | 415 | 458 | 281 | 325 | 396 | 467 | 503 | 298 | 347 | 431 | 509 | 533 | 312 | 367 | 464 | 548 | 558
| kW | 51.6 | 51.1 | 50.6 | 49.7 | 50.7 | 52.9 | 51.9 | 51.3 | 50.2 | 49.3 | 54 | 52.9 | 51.9 | 51.2 | 50.7 | 54.8 | 53.5 | 52.3 | 51.4 | 51.1
| BF | 0 | 0.18 | 0.1 | 0.07 | 0.12 | 0.09 | 0.12 | 0.1 | 0.08 | 0.21 | 0.17 | 0.14 | 0.11 | 0.12 | 0.31 | 0.15 | 0.15 | 0.13 | 0.15 | 0.38
115 | TC | 615 | 581 | 528 | 476 | 436 | 644 | 609 | 554 | 502 | 475 | 663 | 627 | 572 | 519 | 505 | — | 641 | 585 | 537 | 529
| SHC | 252 | 289 | 345 | 400 | 433 | 271 | 314 | 383 | 450 | 475 | 287 | 335 | 418 | 494 | 505 | — | 356 | 451 | 523 | 529
| kW | 60.1 | 59.8 | 59.8 | 58.7 | 60.6 | 62.3 | 61 | 60.6 | 61 | 60.4 | 64.3 | 62.2 | 61.4 | 61.3 | 60.6 | — | 63.6 | 61.9 | 60.8 | 61.1
| BF | 0 | 0.14 | 0.09 | 0.07 | 0.16 | 0.2 | 0.12 | 0.1 | 0.09 | 0.26 | 0.15 | 0.13 | 0.11 | 0.12 | 0.34 | — | 0.14 | 0.13 | 0.18 | 0.41
48/50 055 (55 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 22000 |  |  |  |  | 24750
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 791 | 751 | 691 | 637 | 625 | 805 | 762 | 702 | 650 | 644
| SHC | 348 | 410 | 520 | 614 | 625 | 359 | 429 | 550 | 639 | 644
| kW | 39.1 | 38.3 | 37.2 | 36.1 | 35.8 | 39.4 | 38.6 | 37.4 | 36.4 | 36.2
| BF | 0.17 | 0.16 | 0.14 | 0.17 | 0.39 | 0.2 | 0.17 | 0.15 | 0.22 | 0.44
85 | TC | 771 | 730 | 673 | 621 | 612 | 787 | 743 | 684 | 634 | 632
| SHC | 341 | 403 | 512 | 606 | 612 | 354 | 422 | 543 | 620 | 632
| kW | 43.2 | 42.4 | 41.2 | 40.1 | 39.9 | 43.7 | 42.7 | 41.4 | 40.4 | 40.3
| BF | 0.17 | 0.16 | 0.14 | 0.17 | 0.4 | 0.19 | 0.18 | 0.15 | 0.24 | 0.45
95 | TC | 753 | 713 | 655 | 606 | 598 | 764 | 723 | 665 | 617 | 616
| SHC | 333 | 396 | 505 | 589 | 598 | 346 | 416 | 536 | 610 | 616
| kW | 48.8 | 47.6 | 46.2 | 45.2 | 45 | 49.3 | 47.8 | 46.5 | 45.3 | 45.4
| BF | 0.18 | 0.17 | 0.14 | 0.2 | 0.42 | 0.19 | 0.17 | 0.15 | 0.25 | 0.47
105 | TC | 724 | 686 | 630 | 584 | 578 | 733 | 696 | 638 | 596 | 596
| SHC | 324 | 387 | 495 | 570 | 578 | 336 | 406 | 525 | 596 | 596
| kW | 56.4 | 54.1 | 52.7 | 51.4 | 51.6 | 57.1 | 54.8 | 52.9 | 52 | 51.9
| BF | 0.18 | 0.16 | 0.14 | 0.22 | 0.44 | 0.18 | 0.17 | 0.15 | 0.26 | 0.48
115 | TC | — | 652 | 595 | 551 | 550 | — | — | 603 | 570 | 567
| SHC | — | 375 | 482 | 548 | 550 | — | — | 511 | 561 | 567
| kW | — | 65 | 62.3 | 61.3 | 61.4 | — | — | 63.1 | 61.2 | 61.7
| BF | — | 0.16 | 0.14 | 0.24 | 0.46 | — | — | 0.16 | 0.31 | 0.51
Performance data (cont)
Cooling Capacities (cont) 48/50 060 (60 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 15000 |  |  |  |  | 18000 |  |  |  |  | 21000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 751 | 718 | 664 | 611 | 558 | 791 | 752 | 698 | 644 | 589 | 816 | 777 | 721 | 667 | 624 | 834 | 796 | 739 | 684 | 653
| SHC | 308 | 339 | 410 | 474 | 530 | 318 | 368 | 449 | 528 | 575 | 335 | 393 | 485 | 577 | 624 | 351 | 415 | 520 | 621 | 653
| kW | 43.7 | 42.9 | 41.6 | 40.7 | 40.4 | 44.7 | 43.7 | 42.4 | 41.4 | 40.5 | 45.4 | 44.4 | 43 | 41.9 | 41.2 | 45.9 | 44.8 | 43.4 | 42.4 | 41.7
| BF | 0 | 0 | 0.17 | 0.12 | 0.11 | 0 | 0.1 | 0.16 | 0.13 | 0.18 | 0 | 0.22 | 0.16 | 0.14 | 0.26 | 0.12 | 0.21 | 0.17 | 0.17 | 0.33
85 | TC | 730 | 701 | 647 | 593 | 539 | 765 | 733 | 679 | 625 | 573 | 787 | 756 | 701 | 647 | 607 | 803 | 773 | 718 | 663 | 636
| SHC | 298 | 334 | 403 | 465 | 518 | 306 | 361 | 442 | 519 | 558 | 326 | 385 | 478 | 568 | 607 | 341 | 407 | 511 | 611 | 636
| kW | 48.1 | 47.4 | 46.4 | 46 | 46 | 49.1 | 48.2 | 47.3 | 46.6 | 45.7 | 49.7 | 48.9 | 47.8 | 47 | 46.6 | 50.1 | 49.3 | 48.2 | 47.5 | 47
| BF | 0 | 0 | 0.16 | 0.12 | 0.12 | 0 | 0.25 | 0.15 | 0.13 | 0.21 | 0 | 0.2 | 0.16 | 0.14 | 0.27 | 0.29 | 0.2 | 0.17 | 0.17 | 0.35
95 | TC | 711 | 681 | 626 | 572 | 515 | 744 | 711 | 656 | 601 | 554 | 764 | 733 | 677 | 622 | 587 | 779 | 748 | 692 | 636 | 616
| SHC | 291 | 327 | 393 | 454 | 498 | 300 | 353 | 432 | 507 | 553 | 319 | 377 | 468 | 556 | 587 | 334 | 399 | 501 | 598 | 616
| kW | 53.5 | 53 | 52.5 | 52.3 | 53.8 | 54.4 | 53.8 | 53.3 | 52.7 | 53.2 | 54.9 | 54.4 | 53.7 | 53.3 | 53.2 | 55.4 | 54.8 | 54.1 | 53.6 | 53.1
| BF | 0 | 0 | 0.14 | 0.11 | 0.14 | 0 | 0.22 | 0.15 | 0.12 | 0.21 | 0.13 | 0.19 | 0.16 | 0.14 | 0.3 | 0.26 | 0.19 | 0.17 | 0.17 | 0.37
105 | TC | 686 | 655 | 600 | 546 | 489 | 716 | 683 | 627 | 573 | 531 | 735 | 703 | 647 | 591 | 564 | 748 | 717 | 661 | 605 | 591
| SHC | 281 | 317 | 382 | 442 | 484 | 293 | 343 | 420 | 495 | 531 | 310 | 367 | 456 | 541 | 564 | 324 | 388 | 489 | 576 | 591
| kW | 60 | 59.8 | 59.8 | 61.6 | 64.9 | 60.8 | 60.5 | 60.5 | 61.6 | 63 | 61.3 | 61.1 | 60.8 | 62.3 | 62.4 | 61.6 | 61.4 | 61.1 | 62.2 | 61.8
| BF | 0 | 0.12 | 0.13 | 0.11 | 0.14 | 0 | 0.2 | 0.14 | 0.12 | 0.24 | 0.3 | 0.18 | 0.15 | 0.15 | 0.33 | 0.23 | 0.19 | 0.17 | 0.17 | 0.39
115 | TC | 657 | 624 | 569 | — | — | 682 | 650 | 594 | — | — | 700 | 668 | 612 | 554 | — | 714 | 681 | 625 | 570 | 562
| SHC | 265 | 306 | 369 | — | — | 283 | 332 | 407 | — | — | 299 | 354 | 442 | 522 | — | 313 | 376 | 476 | 556 | 562
| kW | 67.5 | 68 | 69.8 | — | — | 68.1 | 68.7 | 70.2 | — | — | 68.8 | 69.1 | 70.3 | 73.7 | — | 69.4 | 69.5 | 70.4 | 72.7 | 72.3
| BF | 0 | 0.25 | 0.12 | — | — | 0 | 0.18 | 0.14 | — | — | 0.24 | 0.17 | 0.15 | 0.15 | — | 0.22 | 0.18 | 0.16 | 0.2 | 0.42
48/50 060 (60 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 24000 |  |  |  |  | 27000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 848 | 809 | 752 | 697 | 677 | 861 | 820 | 762 | 707 | 698
| SHC | 365 | 436 | 552 | 660 | 677 | 379 | 456 | 583 | 690 | 698
| kW | 46.2 | 45.2 | 43.7 | 42.7 | 42.2 | 46.6 | 45.5 | 44 | 42.8 | 42.5
| BF | 0.28 | 0.21 | 0.19 | 0.19 | 0.39 | 0.26 | 0.21 | 0.2 | 0.23 | 0.44
85 | TC | 816 | 785 | 730 | 675 | 660 | 829 | 794 | 740 | 686 | 680
| SHC | 356 | 428 | 544 | 648 | 660 | 369 | 447 | 575 | 669 | 680
| kW | 50.4 | 49.7 | 48.5 | 47.8 | 47.2 | 50.8 | 49.9 | 48.8 | 47.7 | 47.7
| BF | 0.25 | 0.2 | 0.18 | 0.2 | 0.41 | 0.25 | 0.21 | 0.19 | 0.25 | 0.46
95 | TC | 793 | 759 | 704 | 648 | 638 | 803 | 768 | 713 | 660 | 658
| SHC | 348 | 419 | 534 | 630 | 638 | 361 | 439 | 565 | 652 | 658
| kW | 55.8 | 55.1 | 54.4 | 53.8 | 53.5 | 56.1 | 55.3 | 54.6 | 53.7 | 53.8
| BF | 0.24 | 0.2 | 0.18 | 0.21 | 0.43 | 0.24 | 0.21 | 0.19 | 0.26 | 0.48
105 | TC | 762 | 728 | 671 | 620 | 614 | 771 | 736 | 680 | 632 | 632
| SHC | 338 | 408 | 521 | 605 | 614 | 352 | 427 | 552 | 625 | 632
| kW | 62.2 | 61.7 | 61.3 | 61.2 | 61.4 | 62.6 | 62.1 | 61.5 | 61.2 | 61.5
| BF | 0.23 | 0.2 | 0.18 | 0.24 | 0.45 | 0.23 | 0.21 | 0.19 | 0.28 | 0.5
115 | TC | 724 | 691 | 635 | 586 | 584 | 732 | 697 | 643 | 602 | 602
| SHC | 327 | 396 | 508 | 581 | 584 | 340 | 415 | 538 | 602 | 602
| kW | 69.8 | 69.5 | 70.3 | 71.2 | 71.7 | 70.1 | 69.2 | 70.4 | 71.3 | 71.3
| BF | 0.22 | 0.19 | 0.18 | 0.26 | 0.48 | 0.22 | 0.2 | 0.19 | 0.31 | 0.52
Cooling Capacities (cont) 48/50 060 (60 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 15000 |  |  |  |  | 18000 |  |  |  |  | 21000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 761 | 725 | 664 | 610 | 561 | 802 | 762 | 700 | 643 | 594 | 830 | 789 | 725 | 666 | 628 | 851 | 809 | 744 | 685 | 659
| SHC | 313 | 349 | 415 | 479 | 539 | 328 | 378 | 457 | 534 | 594 | 347 | 404 | 495 | 588 | 628 | 364 | 426 | 531 | 629 | 659
| kW | 43.9 | 43 | 41.4 | 40.1 | 39 | 44.9 | 43.9 | 42.3 | 40.9 | 39.8 | 45.5 | 44.5 | 42.9 | 41.4 | 40.7 | 46 | 45 | 43.4 | 42 | 41.3
| BF | 0 | 0 | 0.12 | 0.09 | 0.08 | 0 | 0.17 | 0.12 | 0.1 | 0.15 | 0.1 | 0.16 | 0.13 | 0.11 | 0.25 | 0.21 | 0.17 | 0.14 | 0.15 | 0.33
85 | TC | 741 | 705 | 651 | 599 | 549 | 779 | 741 | 685 | 631 | 584 | 808 | 768 | 709 | 656 | 619 | 831 | 788 | 727 | 672 | 647
| SHC | 304 | 342 | 408 | 473 | 525 | 319 | 370 | 450 | 528 | 584 | 340 | 396 | 488 | 580 | 619 | 358 | 418 | 524 | 625 | 647
| kW | 48.2 | 47.3 | 45.9 | 44.8 | 44.1 | 49.2 | 48.2 | 46.8 | 45.5 | 44.6 | 49.9 | 48.9 | 47.5 | 46.3 | 45.3 | 50.5 | 49.4 | 48 | 46.7 | 46
| BF | 0 | 0.09 | 0.12 | 0.09 | 0.09 | 0 | 0.16 | 0.12 | 0.1 | 0.16 | 0.25 | 0.15 | 0.13 | 0.12 | 0.26 | 0.19 | 0.17 | 0.14 | 0.14 | 0.34
95 | TC | 725 | 690 | 636 | 584 | 534 | 761 | 724 | 668 | 615 | 571 | 787 | 749 | 691 | 637 | 605 | 808 | 766 | 707 | 652 | 633
| SHC | 298 | 336 | 401 | 465 | 520 | 313 | 364 | 443 | 521 | 570 | 333 | 388 | 481 | 571 | 605 | 350 | 410 | 516 | 613 | 633
| kW | 53.5 | 52.6 | 51.5 | 50.6 | 50.3 | 54.6 | 53.7 | 52.5 | 51.6 | 50.7 | 55.5 | 54.5 | 53.2 | 52.3 | 51.3 | 56.4 | 55.1 | 53.7 | 52.7 | 52
| BF | 0 | 0.07 | 0.12 | 0.09 | 0.11 | 0 | 0.15 | 0.12 | 0.1 | 0.19 | 0.21 | 0.16 | 0.13 | 0.12 | 0.28 | 0.18 | 0.16 | 0.14 | 0.15 | 0.35
105 | TC | 703 | 669 | 614 | 560 | 508 | 736 | 700 | 643 | 588 | 554 | 760 | 721 | 664 | 610 | 584 | 775 | 736 | 679 | 624 | 611
| SHC | 290 | 328 | 392 | 455 | 498 | 306 | 355 | 432 | 510 | 554 | 324 | 378 | 470 | 556 | 584 | 339 | 400 | 505 | 598 | 611
| kW | 60.2 | 59.4 | 58.7 | 57.7 | 59.7 | 61.6 | 60.6 | 59.7 | 58.5 | 57 | 63.1 | 61.7 | 60.4 | 60.2 | 59 | 64.1 | 62.4 | 61 | 60.2 | 59.6
| BF | 0 | 0.06 | 0.11 | 0.07 | 0.11 | 0.1 | 0.14 | 0.11 | 0.09 | 0.21 | 0.19 | 0.15 | 0.12 | 0.13 | 0.3 | 0.17 | 0.16 | 0.14 | 0.16 | 0.38
115 | TC | 675 | 639 | 582 | 527 | 482 | 706 | 668 | 610 | 554 | 523 | — | 688 | 630 | 574 | 555 | — | — | 644 | 590 | 582
| SHC | 276 | 316 | 378 | 440 | 476 | 296 | 343 | 419 | 493 | 523 | — | 366 | 456 | 540 | 555 | — | — | 491 | 573 | 582
| kW | 70.1 | 69.7 | 69.6 | 68 | 71.2 | 72.8 | 70.9 | 70.6 | 71.2 | 70.6 | — | 72.6 | 71.6 | 71.7 | 70.8 | — | — | 72.2 | 71.6 | 71.3
| BF | 0 | 0.15 | 0.1 | 0.07 | 0.16 | 0.07 | 0.13 | 0.11 | 0.1 | 0.25 | — | 0.15 | 0.12 | 0.13 | 0.34 | — | — | 0.14 | 0.18 | 0.41
48/50 060 (60 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 24000 |  |  |  |  | 27000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 868 | 824 | 759 | 700 | 684 | 882 | 836 | 770 | 714 | 705
| SHC | 380 | 448 | 565 | 669 | 684 | 393 | 468 | 598 | 689 | 705
| kW | 46.4 | 45.4 | 43.8 | 42.3 | 42 | 46.7 | 45.7 | 44.1 | 42.7 | 42.5
| BF | 0.19 | 0.18 | 0.15 | 0.18 | 0.39 | 0.2 | 0.19 | 0.17 | 0.22 | 0.44
85 | TC | 847 | 803 | 741 | 685 | 671 | 861 | 814 | 752 | 698 | 692
| SHC | 373 | 440 | 558 | 653 | 671 | 387 | 460 | 591 | 688 | 692
| kW | 51 | 49.9 | 48.3 | 47 | 46.6 | 51.5 | 50.2 | 48.7 | 47.3 | 47.2
| BF | 0.18 | 0.17 | 0.15 | 0.2 | 0.4 | 0.19 | 0.18 | 0.17 | 0.23 | 0.45
95 | TC | 822 | 780 | 720 | 666 | 656 | 835 | 792 | 730 | 679 | 675
| SHC | 364 | 432 | 550 | 641 | 656 | 377 | 453 | 582 | 664 | 675
| kW | 57.1 | 55.6 | 54.1 | 52.9 | 52.5 | 57.9 | 56.2 | 54.5 | 52.9 | 53.1
| BF | 0.19 | 0.17 | 0.15 | 0.2 | 0.41 | 0.2 | 0.18 | 0.17 | 0.26 | 0.46
105 | TC | 789 | 749 | 690 | 639 | 633 | 798 | 757 | 699 | 653 | 652
| SHC | 353 | 421 | 538 | 628 | 633 | 365 | 442 | 570 | 648 | 652
| kW | 65.4 | 63.2 | 61.4 | 60.4 | 60.1 | 66.8 | 63.5 | 61.7 | 60.5 | 60.5
| BF | 0.18 | 0.17 | 0.15 | 0.21 | 0.43 | 0.19 | 0.17 | 0.16 | 0.27 | 0.48
115 | TC | — | — | 655 | 606 | 603 | — | — | 663 | 622 | 622
| SHC | — | — | 524 | 599 | 603 | — | — | 556 | 622 | 622
| kW | — | — | 72.8 | 71 | 71.9 | — | — | 72.8 | 72.1 | 72
| BF | — | — | 0.15 | 0.24 | 0.46 | — | — | 0.16 | 0.29 | 0.51
LEGEND
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm
tlwb
hlwb = hewb –
Performance data (cont)
Cooling Capacities (cont) 48/50 070 (70 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 |  |  |  |  | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 843 | 802 | 744 | 685 | 629 | 880 | 839 | 779 | 720 | 675 | 905 | 863 | 803 | 744 | 710 | 924 | 882 | 820 | 761 | 741
| SHC | 345 | 392 | 472 | 549 | 604 | 363 | 423 | 520 | 614 | 663 | 384 | 453 | 564 | 672 | 710 | 402 | 479 | 606 | 722 | 741
| kW | 46.7 | 45.7 | 44.2 | 42.9 | 41.9 | 47.7 | 46.6 | 45 | 43.7 | 42.7 | 48.4 | 47.3 | 45.6 | 44.3 | 43.5 | 48.9 | 47.7 | 46.1 | 44.7 | 44.2
| BF | 0 | 0.19 | 0.09 | 0.07 | 0.11 | 0 | 0.14 | 0.1 | 0.08 | 0.2 | 0.21 | 0.12 | 0.11 | 0.1 | 0.27 | 0.17 | 0.13 | 0.12 | 0.13 | 0.35
85 | TC | 822 | 783 | 726 | 667 | 612 | 857 | 819 | 759 | 700 | 655 | 880 | 839 | 782 | 722 | 694 | 900 | 860 | 798 | 739 | 724
| SHC | 334 | 384 | 464 | 540 | 599 | 356 | 416 | 511 | 604 | 655 | 376 | 444 | 555 | 660 | 694 | 394 | 471 | 597 | 709 | 724
| kW | 51.3 | 50.2 | 48.9 | 47.7 | 46.8 | 52.2 | 51.2 | 49.7 | 48.5 | 47.6 | 52.9 | 51.8 | 50.3 | 49.1 | 48.3 | 53.4 | 52.3 | 50.8 | 49.5 | 49
| BF | 0 | 0.17 | 0.09 | 0.07 | 0.11 | 0 | 0.13 | 0.1 | 0.08 | 0.2 | 0.19 | 0.12 | 0.11 | 0.11 | 0.29 | 0.16 | 0.13 | 0.12 | 0.14 | 0.36
95 | TC | 799 | 763 | 703 | 645 | 588 | 830 | 791 | 734 | 674 | 635 | 854 | 816 | 755 | 695 | 673 | 871 | 832 | 771 | 711 | 702
| SHC | 326 | 376 | 454 | 531 | 584 | 347 | 406 | 501 | 591 | 635 | 367 | 435 | 545 | 647 | 673 | 385 | 461 | 586 | 688 | 702
| kW | 56.7 | 55.8 | 54.6 | 53.2 | 52.7 | 57.6 | 56.5 | 55.4 | 54.3 | 53.4 | 58.3 | 57.4 | 55.9 | 54.8 | 54.1 | 58.9 | 57.9 | 56.4 | 55.1 | 54.8
| BF | 0 | 0.15 | 0.09 | 0.06 | 0.11 | 0.27 | 0.11 | 0.09 | 0.08 | 0.22 | 0.17 | 0.12 | 0.1 | 0.11 | 0.31 | 0.16 | 0.13 | 0.12 | 0.15 | 0.38
105 | TC | 771 | 734 | 674 | 618 | 569 | 799 | 764 | 703 | 644 | 612 | 821 | 784 | 722 | 664 | 648 | 836 | 798 | 737 | 679 | 676
| SHC | 313 | 365 | 442 | 517 | 561 | 337 | 395 | 488 | 577 | 612 | 356 | 424 | 531 | 631 | 648 | 374 | 449 | 573 | 672 | 676
| kW | 63.1 | 62.3 | 61.1 | 60.4 | 60.1 | 64 | 63.2 | 62 | 61.8 | 61.1 | 64.8 | 63.8 | 62.5 | 62 | 61.4 | 65.3 | 64.4 | 62.9 | 62 | 61.8
| BF | 0 | 0.13 | 0.07 | 0.06 | 0.15 | 0.2 | 0.11 | 0.09 | 0.08 | 0.25 | 0.15 | 0.11 | 0.1 | 0.11 | 0.34 | 0.15 | 0.13 | 0.11 | 0.16 | 0.41
115 | TC | 736 | 699 | 642 | 587 | 541 | 763 | 728 | 669 | 610 | 587 | 782 | 747 | 687 | 629 | 620 | 796 | 760 | 700 | 650 | 646
| SHC | 304 | 353 | 427 | 503 | 541 | 325 | 383 | 474 | 560 | 587 | 344 | 411 | 517 | 602 | 620 | 361 | 435 | 559 | 641 | 646
| kW | 70.7 | 69.4 | 70.3 | 69.2 | 71 | 71.7 | 71.3 | 70.8 | 71.4 | 70.3 | 72.5 | 72.1 | 71.4 | 71.1 | 71 | 73 | 72.4 | 71.7 | 70.8 | 71.1
| BF | 0 | 0.1 | 0.08 | 0.05 | 0.17 | 0.16 | 0.1 | 0.09 | 0.09 | 0.28 | 0.14 | 0.11 | 0.1 | 0.14 | 0.37 | 0.14 | 0.13 | 0.11 | 0.2 | 0.43
48/50 070 (70 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 938 | 897 | 834 | 774 | 767 | 945 | 903 | 840 | 782 | 779
| SHC | 419 | 504 | 646 | 758 | 767 | 428 | 518 | 668 | 776 | 779
| kW | 49.3 | 48.1 | 46.4 | 45 | 44.8 | 49.5 | 48.3 | 46.6 | 45.1 | 45.1
| BF | 0.17 | 0.15 | 0.13 | 0.18 | 0.41 | 0.17 | 0.15 | 0.14 | 0.21 | 0.44
85 | TC | 913 | 874 | 811 | 751 | 749 | 919 | 880 | 816 | 763 | 761
| SHC | 411 | 496 | 637 | 745 | 749 | 420 | 510 | 659 | 756 | 761
| kW | 53.8 | 52.8 | 51.1 | 49.7 | 49.6 | 54 | 52.9 | 51.3 | 50 | 49.9
| BF | 0.16 | 0.14 | 0.13 | 0.18 | 0.43 | 0.16 | 0.15 | 0.14 | 0.23 | 0.45
95 | TC | 883 | 845 | 782 | 728 | 726 | 889 | 850 | 788 | 741 | 738
| SHC | 401 | 486 | 626 | 723 | 726 | 411 | 500 | 648 | 727 | 738
| kW | 59.3 | 58.3 | 56.7 | 55.4 | 55.4 | 59.5 | 58.4 | 56.9 | 55.7 | 55.7
| BF | 0.16 | 0.14 | 0.13 | 0.21 | 0.44 | 0.16 | 0.15 | 0.14 | 0.27 | 0.47
105 | TC | 847 | 809 | 747 | 701 | 698 | 853 | 815 | 753 | 710 | 710
| SHC | 390 | 474 | 615 | 692 | 698 | 400 | 488 | 635 | 710 | 710
| kW | 65.7 | 64.7 | 63.1 | 62.1 | 62.2 | 65.9 | 64.9 | 63.4 | 62.4 | 62.4
| BF | 0.15 | 0.14 | 0.12 | 0.24 | 0.46 | 0.15 | 0.14 | 0.14 | 0.27 | 0.49
115 | TC | 806 | 770 | 710 | 673 | 668 | 811 | 774 | 714 | 680 | 679
| SHC | 378 | 460 | 598 | 655 | 668 | 387 | 474 | 619 | 680 | 679
| kW | 73.5 | 72.8 | 71.9 | 71.1 | 71.2 | 73.7 | 72.9 | 72.2 | 71.3 | 71.4
| BF | 0.14 | 0.14 | 0.13 | 0.29 | 0.49 | 0.15 | 0.14 | 0.14 | 0.3 | 0.51
LEGEND
BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. Direct interpolation is permissible. Do not extrapolate. 2. The following formulas may be used: t = t – sensible capacity (Btuh) 1.10 x cfm Wet-bulb temperature corresponding to enthalpy of air leaving evaporator coil (hlwb). h = h – total capacity (Btuh) 4.5 x cfm
Performance data (cont)
Cooling Capacities (cont) 48/50 070 (70 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 |  |  |  |  | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 863 | 814 | 754 | 690 | 636 | 905 | 862 | 793 | 728 | 686 | 934 | 889 | 820 | 753 | 729 | 956 | 911 | 839 | 771 | 764
| SHC | 353 | 404 | 485 | 563 | 630 | 380 | 441 | 539 | 635 | 686 | 403 | 473 | 589 | 700 | 729 | 423 | 504 | 639 | 757 | 764
| kW | 47.8 | 46.6 | 44.8 | 43.2 | 42 | 48.8 | 47.6 | 45.7 | 44.1 | 43.1 | 49.6 | 48.3 | 46.4 | 44.7 | 44.2 | 50.2 | 48.9 | 46.9 | 45.3 | 45.1
| BF | 0 | 0.05 | 0.03 | 0.01 | 0.05 | 0.12 | 0.05 | 0.03 | 0.02 | 0.16 | 0.08 | 0.05 | 0.04 | 0.04 | 0.25 | 0.07 | 0.05 | 0.04 | 0.06 | 0.33
85 | TC | 838 | 797 | 729 | 678 | 623 | 876 | 834 | 772 | 715 | 673 | 903 | 861 | 798 | 734 | 714 | 926 | 882 | 817 | 753 | 746
| SHC | 345 | 396 | 475 | 556 | 621 | 370 | 430 | 530 | 628 | 673 | 392 | 463 | 581 | 692 | 714 | 413 | 494 | 630 | 742 | 746
| kW | 52.1 | 50.9 | 49.1 | 47.7 | 46.4 | 53.2 | 51.9 | 50.1 | 48.7 | 47.7 | 53.9 | 52.7 | 50.9 | 49.2 | 48.7 | 54.5 | 53.3 | 51.4 | 49.7 | 49.6
| BF | 0 | 0.06 | 0.02 | 0.02 | 0.05 | 0.1 | 0.05 | 0.03 | 0.03 | 0.17 | 0.07 | 0.05 | 0.03 | 0.04 | 0.27 | 0.07 | 0.05 | 0.04 | 0.08 | 0.35
95 | TC | 814 | 777 | 711 | 662 | 611 | 853 | 813 | 753 | 693 | 660 | 879 | 841 | 777 | 718 | 699 | 902 | 860 | 795 | 734 | 730
| SHC | 337 | 388 | 467 | 548 | 608 | 362 | 422 | 522 | 618 | 660 | 384 | 455 | 572 | 683 | 699 | 405 | 486 | 621 | 730 | 730
| kW | 57.3 | 56.2 | 54.4 | 53.2 | 51.9 | 58.4 | 57.3 | 55.6 | 54.1 | 53.1 | 59.3 | 58.1 | 56.3 | 54.8 | 54.2 | 60 | 58.7 | 56.9 | 55.2 | 55.1
| BF | 0 | 0.05 | 0.02 | 0.02 | 0.07 | 0.08 | 0.05 | 0.03 | 0.02 | 0.19 | 0.06 | 0.05 | 0.03 | 0.04 | 0.29 | 0.07 | 0.05 | 0.04 | 0.09 | 0.36
105 | TC | 791 | 755 | 691 | 640 | 593 | 828 | 788 | 728 | 667 | 642 | 852 | 813 | 750 | 691 | 680 | 871 | 831 | 766 | 711 | 709
| SHC | 330 | 379 | 458 | 537 | 593 | 354 | 413 | 512 | 607 | 642 | 375 | 445 | 561 | 668 | 680 | 395 | 476 | 610 | 702 | 709
| kW | 63.6 | 62.6 | 60.7 | 59.9 | 58.6 | 64.9 | 63.7 | 62.1 | 60.4 | 59.8 | 65.8 | 64.7 | 63 | 61.3 | 60.8 | 66.6 | 65.4 | 63.5 | 61.6 | 61.6
| BF | 0 | 0.05 | 0.02 | 0.02 | 0.09 | 0.07 | 0.04 | 0.03 | 0.02 | 0.21 | 0.06 | 0.04 | 0.03 | 0.05 | 0.31 | 0.06 | 0.05 | 0.04 | 0.13 | 0.38
115 | TC | 761 | 725 | 664 | 611 | 571 | 794 | 758 | 697 | 639 | 618 | 817 | 779 | 717 | 659 | 654 | 834 | 795 | 731 | 682 | 682
| SHC | 319 | 367 | 446 | 523 | 571 | 341 | 401 | 498 | 591 | 618 | 363 | 433 | 548 | 646 | 654 | 382 | 463 | 595 | 682 | 682
| kW | 71.2 | 70.3 | 68.2 | 69.1 | 67.5 | 72.7 | 71.9 | 70.5 | 69.9 | 68.5 | 73.9 | 73 | 71.5 | 69.6 | 69.2 | 75 | 73.8 | 72 | 69.2 | 70
| BF | 0.12 | 0.04 | 0.02 | 0.02 | 0.13 | 0.06 | 0.04 | 0.03 | 0.03 | 0.24 | 0.06 | 0.04 | 0.03 | 0.07 | 0.33 | 0.06 | 0.05 | 0.04 | 0.14 | 0.4
48/50 070 (70 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 973 | 926 | 853 | 795 | 792 | 980 | 934 | 860 | 809 | 806
| SHC | 442 | 534 | 685 | 787 | 792 | 453 | 551 | 711 | 802 | 806
| kW | 50.6 | 49.3 | 47.4 | 45.9 | 45.9 | 50.8 | 49.5 | 47.5 | 46.3 | 46.2
| BF | 0.07 | 0.06 | 0.05 | 0.14 | 0.39 | 0.07 | 0.06 | 0.05 | 0.18 | 0.42
85 | TC | 942 | 898 | 830 | 773 | 772 | 950 | 905 | 839 | 783 | 785
| SHC | 432 | 524 | 676 | 769 | 772 | 443 | 541 | 701 | 783 | 785
| kW | 55 | 53.7 | 51.8 | 50.4 | 50.3 | 55.2 | 54 | 52 | 50.7 | 50.7
| BF | 0.07 | 0.05 | 0.05 | 0.16 | 0.41 | 0.07 | 0.06 | 0.05 | 0.2 | 0.44
95 | TC | 918 | 874 | 808 | 753 | 756 | 924 | 881 | 815 | 766 | 768
| SHC | 424 | 516 | 667 | 753 | 756 | 435 | 532 | 692 | 766 | 768
| kW | 60.5 | 59.2 | 57.3 | 55.7 | 55.8 | 60.7 | 59.5 | 57.6 | 56.1 | 56.2
| BF | 0.07 | 0.05 | 0.05 | 0.17 | 0.42 | 0.07 | 0.06 | 0.05 | 0.21 | 0.45
105 | TC | 885 | 843 | 779 | 732 | 734 | 891 | 850 | 784 | 746 | 746
| SHC | 414 | 505 | 654 | 732 | 734 | 424 | 522 | 679 | 746 | 746
| kW | 67.1 | 65.9 | 64 | 62.2 | 62.4 | 67.4 | 66.1 | 64.2 | 62.8 | 62.8
| BF | 0.07 | 0.05 | 0.05 | 0.2 | 0.44 | 0.07 | 0.06 | 0.06 | 0.23 | 0.47
115 | TC | 847 | 806 | 742 | 706 | 706 | 853 | 812 | 747 | 718 | 717
| SHC | 401 | 492 | 640 | 706 | 706 | 412 | 509 | 664 | 718 | 717
| kW | 75.8 | 74.5 | 72.8 | 70.6 | 70.7 | 76.1 | 74.9 | 72.9 | 71 | 71
| BF | 0.06 | 0.05 | 0.05 | 0.22 | 0.46 | 0.07 | 0.05 | 0.06 | 0.26 | 0.49
Performance data (cont)
Cooling Capacities (cont) 48/50 075 (75 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 |  |  |  |  | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 889 | 852 | 787 | 724 | 663 | 933 | 893 | 826 | 763 | 705 | 960 | 917 | 854 | 789 | 745 | 981 | 937 | 874 | 809 | 780
| SHC | 365 | 410 | 491 | 568 | 635 | 377 | 443 | 540 | 634 | 695 | 402 | 472 | 585 | 693 | 745 | 420 | 499 | 627 | 747 | 780
| kW | 50.7 | 49.6 | 48.1 | 46.7 | 45.8 | 51.8 | 50.7 | 49 | 47.7 | 46.5 | 52.6 | 51.4 | 49.7 | 48.3 | 47.3 | 53.3 | 52 | 50.3 | 48.8 | 48
| BF | 0 | 0 | 0.1 | 0.07 | 0.08 | 0 | 0.16 | 0.1 | 0.09 | 0.16 | 0.3 | 0.14 | 0.11 | 0.1 | 0.24 | 0.2 | 0.14 | 0.12 | 0.12 | 0.32
85 | TC | 869 | 831 | 766 | 703 | 641 | 909 | 870 | 803 | 740 | 686 | 935 | 892 | 829 | 765 | 726 | 957 | 910 | 848 | 783 | 760
| SHC | 357 | 402 | 482 | 558 | 619 | 372 | 435 | 530 | 623 | 679 | 394 | 463 | 575 | 682 | 726 | 413 | 490 | 617 | 734 | 760
| kW | 55.8 | 54.9 | 53.4 | 52.1 | 51.2 | 57 | 55.9 | 54.4 | 53.1 | 52 | 57.7 | 56.5 | 55.1 | 53.8 | 52.9 | 58.4 | 57.1 | 55.6 | 54.2 | 53.5
| BF | 0 | 0 | 0.1 | 0.07 | 0.09 | 0 | 0.15 | 0.1 | 0.08 | 0.18 | 0.24 | 0.13 | 0.11 | 0.1 | 0.26 | 0.18 | 0.13 | 0.12 | 0.13 | 0.33
95 | TC | 844 | 803 | 740 | 679 | 615 | 880 | 841 | 775 | 711 | 662 | 906 | 864 | 799 | 735 | 704 | 925 | 884 | 817 | 752 | 735
| SHC | 346 | 392 | 470 | 547 | 602 | 364 | 424 | 518 | 609 | 662 | 384 | 453 | 563 | 667 | 704 | 403 | 480 | 605 | 716 | 735
| kW | 62 | 60.8 | 59.8 | 58.3 | 58.6 | 63 | 62.1 | 60.7 | 59.5 | 58.9 | 63.9 | 62.7 | 61.4 | 60.2 | 59.1 | 64.6 | 63.5 | 61.9 | 60.5 | 60.1
| BF | 0 | 0.19 | 0.09 | 0.06 | 0.1 | 0 | 0.14 | 0.1 | 0.08 | 0.19 | 0.2 | 0.12 | 0.11 | 0.1 | 0.28 | 0.17 | 0.13 | 0.12 | 0.13 | 0.36
105 | TC | 813 | 773 | 709 | 649 | 592 | 846 | 806 | 742 | 679 | 637 | 869 | 828 | 765 | 701 | 678 | 886 | 846 | 781 | 717 | 708
| SHC | 331 | 380 | 457 | 532 | 582 | 353 | 412 | 504 | 593 | 637 | 372 | 440 | 549 | 650 | 678 | 390 | 467 | 591 | 693 | 708
| kW | 69.2 | 68.3 | 67.4 | 67.1 | 67.2 | 70.3 | 69.1 | 68.6 | 68.7 | 68.2 | 71.1 | 69.7 | 69.1 | 69.2 | 68 | 71.8 | 70.7 | 69.6 | 69.1 | 68.7
| BF | 0 | 0.16 | 0.08 | 0.06 | 0.13 | 0 | 0.12 | 0.09 | 0.08 | 0.22 | 0.17 | 0.11 | 0.1 | 0.11 | 0.31 | 0.16 | 0.13 | 0.12 | 0.15 | 0.38
115 | TC | 779 | 739 | 676 | 616 | 562 | 808 | 770 | 706 | 643 | 610 | 830 | 791 | 726 | 664 | 647 | 845 | 806 | 742 | 683 | 677
| SHC | 316 | 367 | 443 | 516 | 560 | 340 | 398 | 489 | 576 | 610 | 360 | 427 | 533 | 631 | 647 | 377 | 452 | 574 | 669 | 677
| kW | 78.2 | 78.6 | 77.5 | 78 | 79.9 | 79.3 | 78.4 | 78.9 | 79.8 | 79.5 | 80.3 | 79.9 | 79.3 | 79.9 | 79.4 | 81 | 80.3 | 79.6 | 78.5 | 79.4
| BF | 0 | 0.14 | 0.08 | 0.06 | 0.14 | 0.2 | 0.11 | 0.09 | 0.08 | 0.25 | 0.15 | 0.11 | 0.1 | 0.11 | 0.34 | 0.15 | 0.13 | 0.12 | 0.17 | 0.41
48/50 075 (75 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1000 | 955 | 889 | 823 | 808 | 1007 | 964 | 896 | 830 | 822
| SHC | 439 | 525 | 668 | 791 | 808 | 448 | 539 | 690 | 811 | 822
| kW | 53.7 | 52.5 | 50.7 | 49.1 | 48.7 | 53.9 | 52.7 | 50.9 | 49.3 | 49.1
| BF | 0.18 | 0.15 | 0.13 | 0.16 | 0.38 | 0.18 | 0.15 | 0.14 | 0.18 | 0.41
85 | TC | 972 | 930 | 862 | 798 | 787 | 979 | 937 | 869 | 804 | 801
| SHC | 430 | 516 | 658 | 773 | 787 | 439 | 530 | 680 | 797 | 801
| kW | 58.9 | 57.7 | 56 | 54.5 | 54.2 | 59.1 | 57.9 | 56.2 | 54.6 | 54.5
| BF | 0.17 | 0.14 | 0.13 | 0.17 | 0.4 | 0.17 | 0.15 | 0.14 | 0.19 | 0.43
95 | TC | 939 | 898 | 831 | 766 | 762 | 946 | 904 | 837 | 777 | 775
| SHC | 420 | 505 | 645 | 757 | 762 | 429 | 519 | 667 | 771 | 775
| kW | 65 | 64 | 62.3 | 60.8 | 60.6 | 65.2 | 64.2 | 62.4 | 61 | 61
| BF | 0.16 | 0.14 | 0.13 | 0.17 | 0.42 | 0.16 | 0.15 | 0.14 | 0.21 | 0.44
105 | TC | 899 | 859 | 793 | 736 | 733 | 905 | 864 | 800 | 748 | 746
| SHC | 407 | 491 | 631 | 725 | 733 | 416 | 505 | 653 | 739 | 746
| kW | 72.2 | 71.2 | 69.9 | 68.9 | 69 | 72.4 | 71.4 | 70.2 | 69 | 69.2
| BF | 0.16 | 0.14 | 0.13 | 0.21 | 0.44 | 0.16 | 0.15 | 0.13 | 0.25 | 0.47
115 | TC | 857 | 818 | 753 | 705 | 701 | 863 | 823 | 759 | 717 | 713
| SHC | 393 | 477 | 615 | 692 | 701 | 403 | 491 | 637 | 702 | 713
| kW | 81.3 | 80.8 | 80.2 | 79.2 | 79.5 | 81.6 | 81 | 80.2 | 79.3 | 79.5
| BF | 0.15 | 0.14 | 0.13 | 0.25 | 0.46 | 0.15 | 0.14 | 0.13 | 0.29 | 0.49
hlwb = hewb – |  | 4.5 x cfm
Performance data (cont)
Cooling Capacities (cont) 48/50 075 (75 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 |  |  |  |  | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 912 | 868 | 796 | 732 | 674 | 960 | 913 | 841 | 773 | 721 | 992 | 944 | 871 | 803 | 767 | 1016 | 967 | 892 | 823 | 805
| SHC | 376 | 425 | 505 | 584 | 657 | 400 | 461 | 560 | 658 | 721 | 423 | 493 | 611 | 724 | 767 | 444 | 525 | 659 | 785 | 805
| kW | 51.6 | 50.4 | 48.4 | 46.7 | 45.3 | 52.9 | 51.5 | 49.5 | 47.8 | 46.5 | 53.8 | 52.4 | 50.3 | 48.5 | 47.7 | 54.4 | 53 | 50.9 | 49.1 | 48.7
| BF | 0 | 0.09 | 0.02 | 0.02 | 0.02 | 0 | 0.06 | 0.03 | 0.02 | 0.12 | 0.1 | 0.05 | 0.04 | 0.04 | 0.22 | 0.07 | 0.05 | 0.04 | 0.05 | 0.3
85 | TC | 885 | 837 | 776 | 714 | 660 | 928 | 884 | 819 | 752 | 708 | 958 | 913 | 847 | 786 | 752 | 980 | 938 | 869 | 802 | 787
| SHC | 363 | 413 | 495 | 575 | 649 | 389 | 449 | 550 | 649 | 708 | 411 | 482 | 601 | 716 | 752 | 431 | 514 | 650 | 774 | 787
| kW | 56.5 | 55.2 | 53.3 | 51.7 | 50.4 | 57.7 | 56.4 | 54.4 | 52.6 | 51.6 | 58.6 | 57.2 | 55.3 | 53.6 | 52.7 | 59.3 | 57.9 | 55.9 | 54.1 | 53.7
| BF | 0 | 0.05 | 0.03 | 0.01 | 0.03 | 0.14 | 0.05 | 0.03 | 0.02 | 0.13 | 0.08 | 0.05 | 0.03 | 0.04 | 0.23 | 0.07 | 0.05 | 0.04 | 0.06 | 0.31
95 | TC | 858 | 809 | 759 | 698 | 643 | 901 | 861 | 793 | 735 | 693 | 931 | 889 | 825 | 763 | 735 | 954 | 913 | 845 | 777 | 769
| SHC | 352 | 402 | 487 | 567 | 636 | 379 | 441 | 540 | 643 | 693 | 402 | 474 | 592 | 705 | 735 | 423 | 505 | 641 | 760 | 769
| kW | 62.2 | 60.8 | 59.3 | 57.7 | 56.5 | 63.5 | 62.3 | 60.3 | 58.8 | 57.7 | 64.5 | 63.2 | 61.3 | 59.7 | 58.8 | 65.3 | 64 | 62 | 60 | 59.8
| BF | 0 | 0.04 | 0.03 | 0.02 | 0.04 | 0.11 | 0.05 | 0.03 | 0.01 | 0.15 | 0.07 | 0.05 | 0.03 | 0.04 | 0.25 | 0.07 | 0.05 | 0.04 | 0.06 | 0.33
105 | TC | 835 | 795 | 730 | 676 | 623 | 875 | 834 | 767 | 709 | 673 | 903 | 862 | 796 | 733 | 714 | 922 | 881 | 813 | 751 | 746
| SHC | 344 | 396 | 476 | 555 | 614 | 370 | 430 | 529 | 626 | 673 | 392 | 463 | 580 | 690 | 714 | 412 | 493 | 628 | 744 | 746
| kW | 69.2 | 68 | 66.1 | 65.2 | 63.6 | 70.7 | 69.5 | 67.4 | 66.2 | 65 | 71.8 | 70.6 | 68.7 | 67 | 66.1 | 72.6 | 71.3 | 69.3 | 67.3 | 67.1
| BF | 0 | 0.05 | 0.02 | 0.02 | 0.08 | 0.09 | 0.05 | 0.02 | 0.02 | 0.17 | 0.07 | 0.05 | 0.03 | 0.04 | 0.27 | 0.06 | 0.05 | 0.04 | 0.07 | 0.35
115 | TC | 804 | 766 | 701 | 645 | 596 | 840 | 799 | 735 | 677 | 648 | 865 | 826 | 760 | 699 | 687 | 884 | 843 | 777 | 719 | 718
| SHC | 334 | 384 | 463 | 540 | 596 | 358 | 418 | 515 | 611 | 648 | 379 | 450 | 565 | 673 | 687 | 399 | 480 | 614 | 709 | 718
| kW | 77.7 | 76.8 | 74.5 | 75.6 | 74.1 | 79.5 | 78.3 | 76.4 | 75.8 | 74.9 | 80.7 | 79.8 | 78.3 | 76.7 | 75.8 | 82.1 | 80.8 | 79 | 75.3 | 76.5
| BF | 0 | 0.05 | 0.02 | 0.02 | 0.09 | 0.07 | 0.04 | 0.02 | 0.02 | 0.21 | 0.06 | 0.04 | 0.03 | 0.04 | 0.3 | 0.06 | 0.05 | 0.04 | 0.12 | 0.37
48/50 075 (75 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1034 | 985 | 909 | 839 | 836 | 1042 | 993 | 916 | 853 | 851
| SHC | 463 | 555 | 707 | 833 | 836 | 473 | 571 | 733 | 849 | 851
| kW | 54.9 | 53.5 | 51.4 | 49.6 | 49.5 | 55.2 | 53.8 | 51.6 | 50 | 49.9
| BF | 0.08 | 0.06 | 0.05 | 0.09 | 0.36 | 0.08 | 0.06 | 0.05 | 0.13 | 0.39
85 | TC | 1001 | 955 | 885 | 817 | 816 | 1009 | 963 | 892 | 831 | 829
| SHC | 452 | 544 | 698 | 817 | 816 | 463 | 561 | 724 | 820 | 829
| kW | 59.8 | 58.5 | 56.4 | 54.5 | 54.5 | 60.1 | 58.7 | 56.6 | 55 | 54.9
| BF | 0.07 | 0.06 | 0.05 | 0.1 | 0.38 | 0.08 | 0.06 | 0.05 | 0.17 | 0.41
95 | TC | 973 | 929 | 859 | 799 | 797 | 981 | 936 | 867 | 812 | 810
| SHC | 443 | 535 | 687 | 796 | 797 | 453 | 552 | 713 | 806 | 810
| kW | 65.9 | 64.6 | 62.5 | 60.6 | 60.6 | 66.2 | 64.8 | 62.8 | 61 | 61
| BF | 0.07 | 0.06 | 0.05 | 0.13 | 0.39 | 0.07 | 0.06 | 0.05 | 0.18 | 0.42
105 | TC | 938 | 895 | 827 | 772 | 772 | 945 | 901 | 833 | 784 | 785
| SHC | 431 | 523 | 674 | 767 | 772 | 442 | 539 | 699 | 784 | 785
| kW | 73.3 | 71.9 | 69.9 | 67.6 | 67.9 | 73.6 | 72.2 | 70.2 | 68.1 | 68.3
| BF | 0.07 | 0.05 | 0.05 | 0.16 | 0.41 | 0.07 | 0.06 | 0.05 | 0.2 | 0.44
115 | TC | 898 | 856 | 789 | 742 | 743 | 905 | 862 | 794 | 756 | 755
| SHC | 418 | 510 | 659 | 742 | 743 | 429 | 526 | 684 | 756 | 755
| kW | 83 | 81.6 | 80 | 76.5 | 77.3 | 83.4 | 82 | 80 | 77.6 | 77.7
| BF | 0.07 | 0.05 | 0.05 | 0.18 | 0.43 | 0.07 | 0.06 | 0.05 | 0.22 | 0.46
Performance data (cont)
Cooling Capacities (cont) 48/50 090 (90 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 18000 |  |  |  |  | 22500 |  |  |  |  | 27000 |  |  |  |  | 31500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1118 | 1070 | 985 | 903 | 822 | 1173 | 1118 | 1032 | 950 | 884 | 1204 | 1152 | 1066 | 981 | 922 | 1231 | 1175 | 1090 | 1005 | 970
| SHC | 460 | 513 | 614 | 709 | 790 | 474 | 553 | 674 | 790 | 858 | 501 | 590 | 729 | 863 | 922 | 525 | 624 | 781 | 928 | 970
| kW | 61.5 | 60.5 | 59 | 57.8 | 56.7 | 62.6 | 61.5 | 59.9 | 58.6 | 57.4 | 63.3 | 62.2 | 60.6 | 59.2 | 58.2 | 63.9 | 62.8 | 61.1 | 59.6 | 58.9
| BF | 0 | 0 | 0.13 | 0.1 | 0.11 | 0 | 0.21 | 0.13 | 0.11 | 0.21 | 0 | 0.18 | 0.14 | 0.13 | 0.25 | 0.25 | 0.17 | 0.15 | 0.15 | 0.34
85 | TC | 1086 | 1037 | 954 | 873 | 791 | 1135 | 1083 | 998 | 917 | 847 | 1165 | 1112 | 1030 | 947 | 899 | 1187 | 1137 | 1052 | 970 | 942
| SHC | 444 | 501 | 600 | 694 | 759 | 461 | 540 | 659 | 775 | 847 | 489 | 576 | 714 | 846 | 899 | 512 | 609 | 766 | 911 | 942
| kW | 68.1 | 67.1 | 65.8 | 64.6 | 63.3 | 69.1 | 68.1 | 66.6 | 65.4 | 64.2 | 69.8 | 68.7 | 67.2 | 66 | 65.1 | 70.3 | 69.3 | 67.7 | 66.4 | 65.8
| BF | 0 | 0 | 0.13 | 0.1 | 0.1 | 0 | 0.19 | 0.13 | 0.11 | 0.19 | 0.3 | 0.16 | 0.14 | 0.13 | 0.28 | 0.22 | 0.17 | 0.15 | 0.16 | 0.36
95 | TC | 1050 | 1001 | 920 | 841 | 763 | 1093 | 1044 | 961 | 882 | 827 | 1122 | 1073 | 990 | 909 | 873 | 1144 | 1093 | 1011 | 930 | 910
| SHC | 430 | 488 | 585 | 678 | 748 | 450 | 526 | 644 | 758 | 810 | 475 | 561 | 699 | 828 | 873 | 498 | 594 | 750 | 888 | 910
| kW | 75.7 | 74.7 | 73.6 | 72.3 | 71.3 | 76.7 | 75.8 | 74.4 | 73.1 | 72.1 | 77.4 | 76.5 | 75 | 73.7 | 72.9 | 77.9 | 76.9 | 75.4 | 74.1 | 73.7
| BF | 0 | 0.26 | 0.12 | 0.09 | 0.12 | 0 | 0.17 | 0.12 | 0.11 | 0.25 | 0.24 | 0.16 | 0.13 | 0.13 | 0.3 | 0.21 | 0.16 | 0.15 | 0.16 | 0.38
105 | TC | 1010 | 961 | 881 | 806 | 734 | 1048 | 1000 | 919 | 842 | 791 | 1075 | 1026 | 946 | 867 | 839 | 1095 | 1046 | 965 | 886 | 874
| SHC | 411 | 472 | 568 | 663 | 729 | 436 | 510 | 626 | 739 | 791 | 460 | 546 | 681 | 807 | 839 | 482 | 578 | 732 | 859 | 874
| kW | 84.5 | 83.7 | 82.4 | 81.3 | 81.1 | 85.4 | 84.6 | 83.2 | 82.2 | 81.8 | 86.1 | 85.1 | 83.8 | 82.8 | 82 | 86.6 | 85.7 | 84.2 | 82.9 | 82.6
| BF | 0 | 0.2 | 0.11 | 0.08 | 0.14 | 0 | 0.15 | 0.12 | 0.11 | 0.24 | 0.21 | 0.15 | 0.13 | 0.13 | 0.33 | 0.19 | 0.16 | 0.14 | 0.18 | 0.4
115 | TC | 963 | 914 | 838 | 768 | 713 | 997 | 950 | 872 | 797 | 758 | 1021 | 974 | 896 | 821 | 802 | 1039 | 992 | 914 | 839 | 837
| SHC | 391 | 454 | 550 | 647 | 693 | 420 | 492 | 607 | 718 | 758 | 443 | 527 | 661 | 784 | 802 | 465 | 560 | 712 | 833 | 837
| kW | 94.5 | 93.7 | 93.5 | 92.2 | 92.2 | 95.3 | 94.5 | 93.9 | 94 | 93.5 | 96 | 95.2 | 94.2 | 94.2 | 93.8 | 96.5 | 95.6 | 94.5 | 94.1 | 94
| BF | 0 | 0.16 | 0.1 | 0.08 | 0.2 | 0.24 | 0.14 | 0.11 | 0.11 | 0.28 | 0.18 | 0.14 | 0.13 | 0.14 | 0.36 | 0.18 | 0.15 | 0.14 | 0.19 | 0.43
36000
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm 36,000 Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 1251 | 1195 | 1109 | 1023 | 1004
| SHC | 547 | 656 | 831 | 983 | 1004
| kW | 64.3 | 63.2 | 61.4 | 59.9 | 59.6
| BF | 0.22 | 0.17 | 0.16 | 0.18 | 0.4
85 | TC | 1208 | 1153 | 1070 | 986 | 974
| SHC | 534 | 641 | 816 | 962 | 974
| kW | 70.7 | 69.6 | 68.1 | 66.7 | 66.4
| BF | 0.21 | 0.17 | 0.16 | 0.19 | 0.42
95 | TC | 1161 | 1110 | 1027 | 948 | 942
| SHC | 519 | 626 | 800 | 929 | 942
| kW | 78.3 | 77.3 | 75.8 | 74.4 | 74.3
| BF | 0.2 | 0.17 | 0.16 | 0.22 | 0.44
105 | TC | 1110 | 1061 | 980 | 908 | 905
| SHC | 503 | 609 | 781 | 899 | 905
| kW | 87 | 86.1 | 84.6 | 83.2 | 83.2
| BF | 0.19 | 0.17 | 0.16 | 0.24 | 0.46
115 | TC | 1052 | 1005 | 927 | 867 | 864
| SHC | 485 | 589 | 762 | 860 | 864
| kW | 96.8 | 96 | 94.8 | 94.2 | 94.3
| BF | 0.18 | 0.17 | 0.16 | 0.27 | 0.48
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50 090 (90 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 18000 |  |  |  |  | 22500 |  |  |  |  | 27000 |  |  |  |  | 31500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1177 | 1117 | 1025 | 946 | 870 | 1238 | 1176 | 1081 | 999 | 929 | 1279 | 1214 | 1119 | 1036 | 984 | 1309 | 1246 | 1147 | 1061 | 1031
| SHC | 486 | 546 | 648 | 750 | 843 | 512 | 591 | 717 | 843 | 921 | 542 | 633 | 781 | 927 | 984 | 569 | 672 | 842 | 1004 | 1031
| kW | 63.2 | 62 | 60 | 58.4 | 57 | 64.6 | 63.2 | 61.2 | 59.5 | 58.1 | 65.4 | 64.1 | 62 | 60.2 | 59.2 | 66.1 | 64.7 | 62.6 | 60.8 | 60.2
| BF | 0 | 0.13 | 0.04 | 0.03 | 0.04 | 0 | 0.08 | 0.04 | 0.04 | 0.13 | 0.13 | 0.06 | 0.05 | 0.05 | 0.22 | 0.1 | 0.07 | 0.06 | 0.07 | 0.3
85 | TC | 1138 | 1081 | 1000 | 922 | 846 | 1191 | 1133 | 1051 | 971 | 908 | 1228 | 1167 | 1087 | 1005 | 962 | 1255 | 1198 | 1113 | 1028 | 1006
| SHC | 465 | 531 | 636 | 738 | 828 | 496 | 575 | 704 | 830 | 908 | 525 | 616 | 768 | 912 | 962 | 551 | 655 | 829 | 986 | 1006
| kW | 69.7 | 68.4 | 66.6 | 65.1 | 63.8 | 70.9 | 69.6 | 67.8 | 66.2 | 64.9 | 71.7 | 70.4 | 68.6 | 66.9 | 65.9 | 72.3 | 71 | 69.2 | 67.4 | 66.9
| BF | 0 | 0.1 | 0.04 | 0.03 | 0.04 | 0 | 0.07 | 0.04 | 0.03 | 0.13 | 0.11 | 0.06 | 0.05 | 0.05 | 0.24 | 0.09 | 0.07 | 0.06 | 0.07 | 0.31
95 | TC | 1100 | 1050 | 971 | 894 | 819 | 1151 | 1092 | 1018 | 940 | 883 | 1185 | 1134 | 1051 | 971 | 936 | 1208 | 1153 | 1075 | 994 | 979
| SHC | 450 | 518 | 623 | 723 | 810 | 483 | 560 | 690 | 814 | 883 | 510 | 602 | 754 | 895 | 936 | 535 | 640 | 813 | 968 | 979
| kW | 77.1 | 76 | 74.4 | 73.1 | 71.5 | 78.3 | 77 | 75.5 | 74.1 | 72.7 | 79.2 | 78 | 76.3 | 74.8 | 73.8 | 79.8 | 78.5 | 76.9 | 75.2 | 74.8
| BF | 0 | 0.08 | 0.04 | 0.03 | 0.05 | 0.17 | 0.06 | 0.04 | 0.03 | 0.16 | 0.1 | 0.06 | 0.05 | 0.05 | 0.26 | 0.09 | 0.06 | 0.05 | 0.08 | 0.33
105 | TC | 1064 | 1014 | 936 | 858 | 792 | 1110 | 1060 | 980 | 900 | 854 | 1140 | 1091 | 1009 | 930 | 905 | 1161 | 1104 | 1031 | 952 | 946
| SHC | 434 | 504 | 607 | 706 | 780 | 469 | 547 | 674 | 794 | 854 | 495 | 586 | 736 | 875 | 905 | 520 | 623 | 797 | 941 | 946
| kW | 85.9 | 84.9 | 83.5 | 82.3 | 80.5 | 87.2 | 86.1 | 84.6 | 83.3 | 82 | 88 | 86.9 | 85.4 | 83.9 | 83.1 | 88.5 | 87.1 | 86 | 84.2 | 83.9
| BF | 0 | 0.07 | 0.04 | 0.02 | 0.09 | 0.13 | 0.06 | 0.04 | 0.04 | 0.19 | 0.09 | 0.06 | 0.05 | 0.05 | 0.28 | 0.08 | 0.06 | 0.05 | 0.09 | 0.36
115 | TC | 1019 | 967 | 893 | 816 | 756 | 1061 | 1012 | 932 | 855 | 820 | 1087 | 1039 | 960 | 882 | 868 | 1108 | 1059 | 979 | 910 | 906
| SHC | 422 | 486 | 588 | 685 | 756 | 452 | 528 | 654 | 773 | 820 | 477 | 568 | 716 | 852 | 868 | 502 | 605 | 776 | 899 | 906
| kW | 96.1 | 94.7 | 94.2 | 94.4 | 92.7 | 97.4 | 96.4 | 95.3 | 95.2 | 93.4 | 98.2 | 97.2 | 96.1 | 94.4 | 94.2 | 98.8 | 97.8 | 96.7 | 95 | 94.8
| BF | 0 | 0.05 | 0.03 | 0.03 | 0.1 | 0.1 | 0.06 | 0.04 | 0.04 | 0.22 | 0.08 | 0.06 | 0.05 | 0.06 | 0.31 | 0.08 | 0.06 | 0.05 | 0.13 | 0.38
LEGEND
48/50 090 (90 TON) HIGH- CAPACITY COIL — STANDARD MODE (cont)
36000
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm 36,000 Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 1331 | 1267 | 1169 | 1081 | 1069
| SHC | 593 | 711 | 903 | 1066 | 1069
| kW | 66.6 | 65.2 | 63 | 61.2 | 61.1
| BF | 0.1 | 0.07 | 0.06 | 0.1 | 0.36
85 | TC | 1276 | 1218 | 1133 | 1048 | 1043
| SHC | 575 | 692 | 889 | 1042 | 1043
| kW | 72.8 | 71.5 | 69.6 | 67.8 | 67.7
| BF | 0.09 | 0.07 | 0.06 | 0.11 | 0.38
95 | TC | 1231 | 1177 | 1093 | 1017 | 1014
| SHC | 560 | 678 | 873 | 1007 | 1014
| kW | 80.3 | 79.1 | 77.4 | 75.6 | 75.6
| BF | 0.09 | 0.07 | 0.06 | 0.15 | 0.4
105 | TC | 1182 | 1129 | 1047 | 983 | 979
| SHC | 544 | 661 | 855 | 968 | 979
| kW | 89.1 | 88 | 86.4 | 84.8 | 84.7
| BF | 0.09 | 0.07 | 0.06 | 0.18 | 0.42
115 | TC | 1126 | 1073 | 993 | 938 | 937
| SHC | 526 | 642 | 832 | 938 | 937
| kW | 99.5 | 98.3 | 97.4 | 95.3 | 95.3
| BF | 0.08 | 0.07 | 0.06 | 0.2 | 0.44
Interpolation is permissible. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat.
Performance data (cont)
Cooling Capacities (cont) 48/50P2,P3,P4,P5100 (100 TON) STANDARD CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 20000 |  |  |  |  | 25000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1198 | 1147 | 1057 | 970 | 883 | 1251 | 1194 | 1104 | 1017 | 944 | 1285 | 1228 | 1138 | 1050 | 991
| SHC | 489 | 549 | 663 | 768 | 854 | 509 | 593 | 727 | 856 | 928 | 535 | 632 | 786 | 935 | 991
| kW | 68.6 | 67.4 | 65.6 | 64.1 | 62.7 | 69.9 | 68.5 | 66.6 | 65 | 63.7 | 70.8 | 69.3 | 67.4 | 65.7 | 64.7
| BF | 0 | 0 | 0.14 | 0.11 | 0.13 | 0 | 0.23 | 0.14 | 0.12 | 0.22 | 0.12 | 0.19 | 0.15 | 0.14 | 0.28
85 | TC | 1161 | 1111 | 1023 | 938 | 855 | 1209 | 1155 | 1068 | 982 | 923 | 1238 | 1186 | 1099 | 1012 | 975
| SHC | 475 | 536 | 648 | 752 | 833 | 490 | 579 | 711 | 840 | 892 | 521 | 617 | 771 | 917 | 947
| kW | 75.7 | 74.6 | 72.9 | 71.5 | 70.2 | 77 | 75.7 | 73.9 | 72.4 | 71.2 | 77.8 | 76.5 | 74.6 | 73 | 72.2
| BF | 0 | 0.1 | 0.14 | 0.1 | 0.14 | 0 | 0.2 | 0.14 | 0.12 | 0.27 | 0.1 | 0.18 | 0.15 | 0.14 | 0.35
95 | TC | 1121 | 1071 | 985 | 902 | 825 | 1164 | 1113 | 1027 | 942 | 893 | 1191 | 1141 | 1056 | 970 | 933
| SHC | 457 | 522 | 632 | 735 | 811 | 480 | 564 | 695 | 821 | 870 | 506 | 602 | 754 | 896 | 933
| kW | 84.1 | 83 | 81.4 | 80 | 79.3 | 85.2 | 84.1 | 82.4 | 80.8 | 79.7 | 86 | 84.8 | 83.1 | 81.5 | 80.8
| BF | 0 | 0.08 | 0.13 | 0.1 | 0.15 | 0.14 | 0.18 | 0.13 | 0.12 | 0.28 | 0.28 | 0.17 | 0.14 | 0.14 | 0.33
105 | TC | 1077 | 1026 | 942 | 861 | 796 | 1113 | 1064 | 981 | 899 | 849 | 1139 | 1090 | 1007 | 924 | 897
| SHC | 436 | 506 | 613 | 716 | 775 | 464 | 547 | 676 | 800 | 848 | 490 | 585 | 735 | 872 | 897
| kW | 93.7 | 92.7 | 91.4 | 90.5 | 89.8 | 94.7 | 93.7 | 92.1 | 91.3 | 90.9 | 95.4 | 94.3 | 92.7 | 91.9 | 91.4
| BF | 0 | 0.07 | 0.12 | 0.1 | 0.2 | 0.1 | 0.17 | 0.13 | 0.12 | 0.27 | 0.23 | 0.16 | 0.14 | 0.15 | 0.36
115 | TC | 1025 | 976 | 895 | 817 | 759 | 1057 | 1010 | 930 | 851 | 812 | 1080 | 1034 | 954 | 875 | 858
| SHC | 417 | 487 | 593 | 695 | 747 | 447 | 528 | 656 | 778 | 812 | 471 | 565 | 715 | 841 | 858
| kW | 104.6 | 103.9 | 103.4 | 103.4 | 103.1 | 105.4 | 104.6 | 103.9 | 103.9 | 103.8 | 106.1 | 105.3 | 104.3 | 104.1 | 104
| BF | 0 | 0.18 | 0.11 | 0.09 | 0.21 | 0.08 | 0.15 | 0.12 | 0.12 | 0.3 | 0.2 | 0.16 | 0.14 | 0.17 | 0.39
48/50P2,P3,P4,P5100 (100 TON) STANDARD CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 35000 |  |  |  |  | 40000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1310 | 1252 | 1162 | 1073 | 1038 | 1329 | 1273 | 1181 | 1092 | 1074
| SHC | 561 | 669 | 843 | 1005 | 1038 | 584 | 705 | 898 | 1059 | 1074
| kW | 71.4 | 70 | 68 | 66.2 | 65.5 | 71.9 | 70.5 | 68.4 | 66.6 | 66.2
| BF | 0.27 | 0.19 | 0.16 | 0.17 | 0.36 | 0.24 | 0.19 | 0.17 | 0.21 | 0.42
85 | TC | 1260 | 1206 | 1121 | 1034 | 1007 | 1278 | 1224 | 1139 | 1054 | 1044
| SHC | 545 | 654 | 828 | 980 | 1007 | 568 | 688 | 882 | 1032 | 1044
| kW | 78.4 | 77.1 | 75.2 | 73.5 | 72.9 | 78.9 | 77.5 | 75.6 | 73.9 | 73.6
| BF | 0.25 | 0.18 | 0.16 | 0.18 | 0.38 | 0.23 | 0.18 | 0.17 | 0.22 | 0.44
95 | TC | 1212 | 1160 | 1077 | 992 | 973 | 1228 | 1177 | 1093 | 1014 | 1006
| SHC | 530 | 638 | 810 | 951 | 973 | 553 | 671 | 865 | 992 | 1006
| kW | 86.6 | 85.3 | 83.6 | 81.9 | 81.5 | 87 | 85.8 | 84 | 82.3 | 82.2
| BF | 0.23 | 0.17 | 0.16 | 0.19 | 0.4 | 0.22 | 0.18 | 0.17 | 0.25 | 0.46
105 | TC | 1158 | 1108 | 1026 | 947 | 937 | 1173 | 1123 | 1041 | 970 | 967
| SHC | 513 | 620 | 791 | 926 | 937 | 536 | 653 | 845 | 960 | 967
| kW | 95.9 | 94.8 | 93.2 | 92.2 | 91.7 | 96.4 | 95.3 | 93.6 | 92.5 | 92.4
| BF | 0.21 | 0.17 | 0.15 | 0.2 | 0.43 | 0.21 | 0.18 | 0.17 | 0.27 | 0.48
115 | TC | 1098 | 1050 | 972 | 901 | 894 | 1110 | 1063 | 985 | 923 | 922
| SHC | 495 | 600 | 770 | 882 | 894 | 517 | 633 | 824 | 923 | 922
| kW | 106.6 | 105.7 | 104.7 | 104 | 104.2 | 107 | 106.1 | 104.9 | 104.4 | 104.5
| BF | 0.19 | 0.16 | 0.15 | 0.24 | 0.45 | 0.2 | 0.17 | 0.17 | 0.29 | 0.51
Performance data (cont)
Cooling Capacities (cont) 48/50P2,P3,P4,P5100 (100 TON) HIGH-CAPACITY COIL — STANDARD MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 20000 |  |  |  |  | 25000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1269 | 1208 | 1114 | 1026 | 941 | 1332 | 1267 | 1171 | 1081 | 1010 | 1373 | 1308 | 1210 | 1118 | 1069
| SHC | 524 | 591 | 707 | 820 | 910 | 552 | 640 | 782 | 920 | 1002 | 585 | 685 | 852 | 1010 | 1069
| kW | 71.2 | 69.7 | 67.3 | 65.4 | 63.7 | 72.9 | 71.1 | 68.7 | 66.6 | 65 | 73.9 | 72.2 | 69.7 | 67.5 | 66.4
| BF | 0 | 0.05 | 0.05 | 0.03 | 0.06 | 0.1 | 0.08 | 0.05 | 0.04 | 0.15 | 0.14 | 0.08 | 0.06 | 0.06 | 0.24
85 | TC | 1231 | 1172 | 1084 | 998 | 916 | 1285 | 1227 | 1136 | 1048 | 987 | 1324 | 1265 | 1173 | 1083 | 1043
| SHC | 505 | 577 | 694 | 805 | 891 | 537 | 626 | 767 | 904 | 977 | 568 | 670 | 836 | 993 | 1043
| kW | 78.3 | 76.7 | 74.6 | 72.8 | 71.1 | 79.7 | 78.3 | 75.9 | 74.1 | 72.5 | 80.8 | 79.2 | 76.9 | 74.9 | 73.8
| BF | 0 | 0.11 | 0.05 | 0.03 | 0.07 | 0.07 | 0.07 | 0.05 | 0.04 | 0.17 | 0.12 | 0.07 | 0.05 | 0.06 | 0.25
95 | TC | 1189 | 1136 | 1049 | 963 | 887 | 1241 | 1183 | 1097 | 1010 | 955 | 1275 | 1221 | 1131 | 1041 | 1012
| SHC | 488 | 563 | 678 | 788 | 871 | 522 | 609 | 751 | 885 | 955 | 552 | 653 | 819 | 971 | 1012
| kW | 86.5 | 85.1 | 83.2 | 81.5 | 80.1 | 88 | 86.5 | 84.5 | 82.7 | 81.3 | 89 | 87.6 | 85.5 | 83.4 | 82.5
| BF | 0 | 0.1 | 0.04 | 0.03 | 0.08 | 0.06 | 0.07 | 0.05 | 0.04 | 0.18 | 0.1 | 0.07 | 0.05 | 0.06 | 0.28
105 | TC | 1147 | 1090 | 1007 | 923 | 853 | 1193 | 1139 | 1051 | 965 | 921 | 1224 | 1170 | 1082 | 995 | 975
| SHC | 473 | 545 | 659 | 768 | 849 | 506 | 592 | 731 | 863 | 921 | 535 | 635 | 800 | 945 | 975
| kW | 96.1 | 94.7 | 93.3 | 92.4 | 90.6 | 97.6 | 96.3 | 94.6 | 93.4 | 92.2 | 98.6 | 97.3 | 95.5 | 94 | 93
| BF | 0 | 0.07 | 0.04 | 0.03 | 0.09 | 0.13 | 0.07 | 0.04 | 0.04 | 0.21 | 0.09 | 0.07 | 0.05 | 0.07 | 0.3
115 | TC | 1095 | 1043 | 959 | 877 | 817 | 1137 | 1085 | 999 | 915 | 883 | 1166 | 1113 | 1027 | 945 | 933
| SHC | 455 | 526 | 638 | 746 | 816 | 487 | 572 | 710 | 839 | 883 | 516 | 614 | 778 | 912 | 933
| kW | 107.2 | 106.4 | 105.6 | 105.4 | 104 | 108.8 | 107.9 | 106.7 | 106.4 | 104.6 | 109.9 | 108.8 | 107.6 | 106.5 | 105.5
| BF | 0.08 | 0.07 | 0.04 | 0.03 | 0.12 | 0.1 | 0.06 | 0.04 | 0.05 | 0.24 | 0.08 | 0.06 | 0.05 | 0.09 | 0.33
48/50P2,P3,P4,P5100 (100 TON) HIGH-CAPACITY COIL — STANDARD MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 35000 |  |  |  |  | 40000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1402 | 1337 | 1239 | 1144 | 1118 | 1426 | 1360 | 1260 | 1170 | 1159
| SHC | 613 | 729 | 919 | 1086 | 1118 | 640 | 769 | 984 | 1149 | 1159
| kW | 74.7 | 73 | 70.4 | 68.2 | 67.6 | 75.3 | 73.6 | 71 | 68.8 | 68.6
| BF | 0.11 | 0.07 | 0.06 | 0.09 | 0.31 | 0.1 | 0.08 | 0.07 | 0.13 | 0.38
85 | TC | 1351 | 1292 | 1199 | 1107 | 1090 | 1373 | 1313 | 1219 | 1135 | 1128
| SHC | 596 | 712 | 903 | 1064 | 1090 | 623 | 753 | 967 | 1121 | 1128
| kW | 81.6 | 80 | 77.6 | 75.5 | 74.9 | 82.2 | 80.6 | 78.2 | 76.1 | 75.9
| BF | 0.1 | 0.08 | 0.06 | 0.09 | 0.33 | 0.1 | 0.08 | 0.07 | 0.15 | 0.4
95 | TC | 1302 | 1246 | 1155 | 1069 | 1057 | 1322 | 1264 | 1173 | 1097 | 1093
| SHC | 580 | 695 | 886 | 1038 | 1057 | 606 | 736 | 949 | 1083 | 1093
| kW | 89.8 | 88.3 | 86.2 | 84.1 | 83.7 | 90.4 | 88.9 | 86.8 | 84.7 | 84.6
| BF | 0.09 | 0.07 | 0.06 | 0.11 | 0.35 | 0.09 | 0.08 | 0.07 | 0.18 | 0.41
105 | TC | 1249 | 1192 | 1104 | 1026 | 1018 | 1266 | 1209 | 1120 | 1054 | 1052
| SHC | 562 | 677 | 865 | 1004 | 1018 | 588 | 717 | 928 | 1048 | 1052
| kW | 99.4 | 98 | 96.2 | 94.4 | 94 | 100 | 98.6 | 96.8 | 94.6 | 94.7
| BF | 0.09 | 0.07 | 0.06 | 0.13 | 0.38 | 0.09 | 0.08 | 0.07 | 0.2 | 0.44
115 | TC | 1187 | 1133 | 1046 | 976 | 973 | 1204 | 1149 | 1061 | 1009 | 1006
| SHC | 542 | 656 | 842 | 971 | 973 | 568 | 696 | 904 | 999 | 1006
| kW | 110.6 | 109.5 | 108.3 | 105.9 | 106.2 | 111.5 | 110.2 | 108.6 | 106.8 | 106.9
| BF | 0.08 | 0.07 | 0.06 | 0.15 | 0.4 | 0.09 | 0.07 | 0.07 | 0.24 | 0.46
[21 empty] | 77 | 76 | 75 | under 75
[21 empty] | 83 | 84 | 85 | over 85
[21 empty] | 3.14 2.97 2.64 | 4.18 3.96 3.52 | 5.22 4.95 4.40 | Use formula shown below
tlwb =
=
lwb ewb
=
lwb ewb
=
lwb ewb
=
=
=
=
=
=
=
=
tlwb =