## Table 1
SPECIFICATIONS | [16 empty] | UNIT
General Data |  | Nominal Tonnage | [5 empty] | 3 Ton |  |  | 4 Ton |  |  |  | 5 Ton |  | 6 Ton
|  | Efficiency Type | [5 empty] | Ultra-High |  |  | Ultra-High |  |  |  | Ultra-High |  | Ultra-High
|  | Model Number | [5 empty] | LCM036U4E |  |  | LCM048U4E |  |  |  | LCM060U4E |  | LCM074U4E
|  | Blower Type | [5 empty] | DirectPlus™ ECM Direct Drive with SZVAV |  |  | DirectPlus™ ECM Direct Drive with SZVAV |  |  |  | DirectPlus™ ECM Direct Drive with SZVAV |  | DirectPlus™ ECM Direct Drive with SZVAV
|  | Model Number | [5 empty] | LCM036U4P |  |  | LCM048U4P |  |  |  | LCM060U4P |  | LCM074U4P
|  | Blower Type | [5 empty] | DirectPlus™ ECM Direct Drive with VAV |  |  | DirectPlus™ ECM Direct Drive with VAV |  |  |  | DirectPlus™ ECM Direct Drive with VAV |  | DirectPlus™ ECM Direct Drive with VAV
Cooling Performance |  | Gross Cooling Capacity - Btuh | [5 empty] | 34600 |  |  | 47000 |  |  |  | 58500 |  | 71000
|  | 1 Net Cooling Capacity - Btuh | [5 empty] | 34000 |  |  | 46000 |  |  |  | 57000 |  | 69000
|  | AHRI Rated Air Flow - cfm | [5 empty] | 1200 |  |  | 1550 |  |  |  | 1800 |  | 2150
|  | Total Unit Power - kW | [5 empty] | 2.3 |  |  | 3.3 |  |  |  | 4.4 |  | 5.8
|  | SEER (Btuh/Watt) - 208/230V-3ph | [5 empty] | 1 22.5 |  |  | 1 21.0 |  |  |  | 1 20.0 |  | - - -
|  | SEER (Btuh/Watt) - 460V-3ph | [5 empty] | 1 22.0 |  |  | 1 20.2 |  |  |  | 1 19.5 |  | - - -
|  | SEER (Btuh/Watt) - 575V-3ph | [5 empty] | 1 22.0 |  |  | 1 20.2 |  |  |  | 1 19.5 |  | - - -
|  | IEER (Btuh/Watt) - 208/230V-3ph | [5 empty] | - - - |  |  | - - - |  |  |  | - - - |  | 2 23.3
|  | IEER (Btuh/Watt) - 460V-3ph | [5 empty] | - - - |  |  | - - - |  |  |  | - - - |  | 2 23.3
|  | IEER (Btuh/Watt) - 575V-3ph | [5 empty] | - - - |  |  | - - - |  |  |  | - - - |  | 2 23.3
|  | EER (Btuh/Watt) - 208/230V-3ph | [5 empty] | 1 15.0 |  |  | 1 14.0 |  |  |  | 1 13.0 |  | 2 12.0
|  | EER (Btuh/Watt) - 460V-3ph | [5 empty] | 1 14.5 |  |  | 113.7 |  |  |  | 1 12.5 |  | 2 12.0
|  | EER (Btuh/Watt) - 575V-3ph | [5 empty] | 1 14.5 |  |  | 113.7 |  |  |  | 1 12.5 |  | 2 12.0
Refrigerant Charge |  | Refrigerant Type | [5 empty] | R-410A |  |  | R-410A |  |  |  | R-410A |  | R-410A
|  | Without Reheat Option | [5 empty] | 17 lbs. 0 oz. |  |  | 17 lbs. 0 oz. |  |  |  | 16 lbs. 8 oz. |  | 16 lbs. 8 oz.
|  | With Reheat Option | [5 empty] | 17 lbs. 2 oz. |  |  | 17 lbs. 2 oz. |  |  |  | 16 lbs. 13 oz. |  | 16 lbs. 13 oz.
Electric Heat Available | [7 empty] | 7.5 and 15 kW |  |  | 7.5 and 15 kW |  |  |  | 7.5, 15 and 22.5 kW |  | 7.5, 15 and 22.5 kW
Compressor Type (Number) | [7 empty] | Variable Capacity Scroll (1)
Outdoor Coil |  | Net face area (total) - sq. ft. | [5 empty] | 19.3 |  |  | 19.3 |  |  |  | 19.3 |  | 19.3
|  | Tube diameter - in. | [5 empty] | 3/8 |  |  | 3/8 |  |  |  | 3/8 |  | 3/8
|  | Number of rows | [5 empty] | 2 |  |  | 2 |  |  |  | 2 |  | 2
|  | Fins per inch | [5 empty] | 20 |  |  | 20 |  |  |  | 20 |  | 20
Outdoor Coil Fans |  | Motor - (No.) HP | [5 empty] | (1) 1/3 (ECM) |  |  | (1) 1/3 (ECM) |  |  |  | (1) 1/3 (ECM) |  | (1) 1/3 (ECM)
|  | Motor rpm | [5 empty] | 550 - 850 |  |  | 600 - 900 |  |  |  | 700 - 950 |  | 700 - 1050
|  | Total Motor watts | [5 empty] | 50 - 200 |  |  | 80 - 236 |  |  |  | 120 - 272 |  | 120 - 360
|  | Diameter - (No.) in. | [5 empty] | (1) 24 |  |  | (1) 24 |  |  |  | (1) 24 |  | (1) 24
|  | Number of blades | [5 empty] | 3 |  |  | 3 |  |  |  | 3 |  | 3
|  | Total air volume - cfm | [5 empty] | 2500 - 3850 |  |  | 2750 - 4100 |  |  |  | 3200 - 4300 |  | 3200 - 4700
Indoor Coil |  | Net face area (total) - sq. ft. | [5 empty] | 9.72 |  |  | 9.72 |  |  |  | 9.72 |  | 9.72
|  | Tube diameter - in. | [5 empty] | 3/8 |  |  | 3/8 |  |  |  | 3/8 |  | 3/8
|  | Number of rows | [5 empty] | 3 |  |  | 3 |  |  |  | 4 |  | 4
|  | Fins per inch | [5 empty] | 14 |  |  | 14 |  |  |  | 14 |  | 14
|  | Drain connection - Number and size. | [5 empty] | 1 in. NPT coupling
|  | Expansion device type | [5 empty] | Balance port TXV
Indoor Blower |  | Nominal motor output | [5 empty] | 1.5 HP (ECM) |  |  | 1.5 HP (ECM) |  |  |  | 1.5 HP (ECM) |  | 1.5 HP (ECM)
|  | Blower wheel nominal diameter x width - in. | [5 empty] | (1) 14 x 5 |  |  | (1) 14 x 5 |  |  |  | (1) 14 x 5 |  | (1) 14 x 5
Filters |  | Type of filter | [5 empty] | MERV 4, Disposable
|  | Number and size - in. | [5 empty] | (4) 20 x 20 x 2
Electrical characteristics | [7 empty] | 208/230V, 460V, or 575V - 60 hz -3 phase
NOTE - Net capacity includes evaporator blower motor heat deduction. Gross capacity does not include evaporator blower motor heat deduction. 1, 2 AHRI Certified to AHRI Standard 1 210/240 or 2 340/360: 95°F outdoor air temperature and 80°F db/67°F wb entering evaporator air; minimum external duct static
pressure.
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
3 TON - LCM036U4
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F |  |  |  |  | 75°F | [6 empty] | 85°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 550 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | - - - |  | - - - | - - - | - - - | - - -
| 700 | 33.5 | 1.26 | 0.68 | 0.79 | 0.89 | 32.4 |  | 1.52 | 0.69 |  | 0.8 | 0.91 | 31.1 |  | 1.79 | 0.7 | 0.81 | 0.93
| 850 | 35.5 | 1.22 | 0.71 | 0.83 | 0.95 | 34.3 |  | 1.48 | 0.72 |  | 0.85 | 0.97 | 32.8 |  | 1.76 | 0.73 | 0.86 | 0.99
| 1000 | 37.1 | 1.19 | 0.74 | 0.88 | 1 | 35.7 |  | 1.46 | 0.75 |  | 0.89 | 1 | 34.2 |  | 1.74 | 0.77 | 0.91 | 1
| 1200 | 38.7 | 1.16 | 0.78 | 0.94 | 1 | 37.2 |  | 1.44 | 0.8 |  | 0.96 | 1 | 35.7 |  | 1.71 | 0.81 | 0.98 | 1
| 1400 | 40 | 1.14 | 0.82 | 0.99 | 1 | 38.5 |  | 1.41 | 0.84 |  | 1 | 1 | 37.1 |  | 1.69 | 0.86 | 1 | 1
67°F | 550 | 32.7 | 1.27 | 0.54 | 0.63 | 0.71 | 31.7 |  | 1.53 | 0.54 |  | 0.63 | 0.72 | 30.5 |  | 1.8 | 0.54 | 0.64 | 0.73
| 700 | 35.5 | 1.22 | 0.55 | 0.65 | 0.76 | 34.3 |  | 1.49 | 0.56 |  | 0.66 | 0.77 | 33 |  | 1.76 | 0.56 | 0.67 | 0.78
| 850 | 37.7 | 1.19 | 0.57 | 0.68 | 0.8 | 36.3 |  | 1.46 | 0.57 |  | 0.69 | 0.81 | 34.7 |  | 1.73 | 0.58 | 0.71 | 0.83
| 1000 | 39.2 | 1.15 | 0.59 | 0.72 | 0.84 | 37.7 |  | 1.43 | 0.59 |  | 0.73 | 0.86 | 36.2 |  | 1.71 | 0.6 | 0.74 | 0.88
| 1200 | 40.8 | 1.13 | 0.61 | 0.76 | 0.9 | 39.2 |  | 1.4 | 0.62 |  | 0.77 | 0.92 | 37.7 |  | 1.68 | 0.63 | 0.79 | 0.94
| 1400 | 42.2 | 1.09 | 0.64 | 0.8 | 0.96 | 40.5 |  | 1.37 | 0.65 |  | 0.82 | 0.98 | 38.7 |  | 1.66 | 0.66 | 0.84 | 1
71°F | 550 | 34.7 | 1.24 | 0.43 | 0.51 | 0.6 | 33.5 |  | 1.5 | 0.43 |  | 0.52 | 0.6 | 32.3 |  | 1.77 | 0.43 | 0.52 | 0.61
| 700 | 37.6 | 1.19 | 0.43 | 0.53 | 0.63 | 36.2 |  | 1.45 | 0.43 |  | 0.54 | 0.64 | 34.9 |  | 1.73 | 0.43 | 0.54 | 0.64
| 850 | 39.8 | 1.14 | 0.44 | 0.55 | 0.66 | 38.3 |  | 1.42 | 0.44 |  | 0.56 | 0.67 | 36.7 |  | 1.69 | 0.44 | 0.56 | 0.68
| 1000 | 41.4 | 1.11 | 0.44 | 0.57 | 0.69 | 39.9 |  | 1.39 | 0.45 |  | 0.58 | 0.7 | 38.2 |  | 1.67 | 0.45 | 0.59 | 0.72
| 1200 | 43.2 | 1.08 | 0.46 | 0.6 | 0.74 | 41.5 |  | 1.35 | 0.46 |  | 0.61 | 0.75 | 39.8 |  | 1.64 | 0.46 | 0.62 | 0.77
| 1400 | 44.5 | 1.05 | 0.47 | 0.63 | 0.78 | 42.8 |  | 1.33 | 0.47 |  | 0.64 | 0.8 | 40.9 |  | 1.62 | 0.48 | 0.65 | 0.82
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 95°F |  |  |  |  | 105°F | [6 empty] | 115°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 550 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | 25.1 |  | 2.75 | 0.69 | 0.81 | 0.92
| 700 | 29.8 | 2.08 | 0.71 | 0.83 | 0.95 | 28.4 |  | 2.38 | 0.72 |  | 0.85 | 0.97 | 27 |  | 2.71 | 0.73 | 0.87 | 0.99
| 850 | 31.4 | 2.05 | 0.74 | 0.88 | 1 | 29.9 |  | 2.36 | 0.76 |  | 0.9 | 1 | 28.3 |  | 2.7 | 0.78 | 0.93 | 1
| 1000 | 32.6 | 2.03 | 0.78 | 0.94 | 1 | 31.1 |  | 2.35 | 0.8 |  | 0.96 | 1 | 29.4 |  | 2.67 | 0.82 | 0.99 | 1
| 1200 | 34 | 2 | 0.83 | 1 | 1 | 32.6 |  | 2.31 | 0.86 |  | 1 | 1 | 31 |  | 2.65 | 0.88 | 1 | 1
| 1400 | 35.6 | 1.98 | 0.88 | 1 | 1 | 34.1 |  | 2.29 | 0.91 |  | 1 | 1 | 32.4 |  | 2.62 | 0.94 | 1 | 1
67°F | 550 | 29.3 | 2.08 | 0.55 | 0.65 | 0.74 | 28 |  | 2.39 | 0.55 |  | 0.65 | 0.76 | 26.7 |  | 2.71 | 0.56 | 0.66 | 0.77
| 700 | 31.6 | 2.05 | 0.57 | 0.68 | 0.8 | 30.2 |  | 2.36 | 0.57 |  | 0.69 | 0.81 | 28.6 |  | 2.69 | 0.58 | 0.71 | 0.83
| 850 | 33.3 | 2.02 | 0.59 | 0.72 | 0.85 | 31.7 |  | 2.34 | 0.6 |  | 0.73 | 0.87 | 30 |  | 2.67 | 0.61 | 0.75 | 0.89
| 1000 | 34.6 | 2 | 0.61 | 0.76 | 0.9 | 32.8 |  | 2.31 | 0.62 |  | 0.78 | 0.93 | 31.2 |  | 2.65 | 0.63 | 0.8 | 0.95
| 1200 | 35.8 | 1.97 | 0.64 | 0.81 | 0.97 | 34.1 |  | 2.28 | 0.66 |  | 0.83 | 0.99 | 32.3 |  | 2.62 | 0.67 | 0.86 | 1
| 1400 | 36.9 | 1.95 | 0.67 | 0.86 | 1 | 35 |  | 2.27 | 0.69 |  | 0.89 | 1 | 33.1 |  | 2.6 | 0.71 | 0.91 | 1
71°F | 550 | 31 | 2.06 | 0.43 | 0.53 | 0.62 | 29.6 |  | 2.36 | 0.43 |  | 0.53 | 0.63 | 28.2 |  | 2.69 | 0.43 | 0.54 | 0.64
| 700 | 33.4 | 2.02 | 0.44 | 0.55 | 0.66 | 31.9 |  | 2.32 | 0.44 |  | 0.55 | 0.67 | 30.3 |  | 2.66 | 0.44 | 0.56 | 0.68
| 850 | 35.1 | 1.99 | 0.44 | 0.57 | 0.69 | 33.5 |  | 2.3 | 0.45 |  | 0.58 | 0.71 | 31.8 |  | 2.63 | 0.45 | 0.59 | 0.73
| 1000 | 36.5 | 1.97 | 0.45 | 0.6 | 0.73 | 34.8 |  | 2.27 | 0.46 |  | 0.61 | 0.75 | 33 |  | 2.61 | 0.47 | 0.62 | 0.77
| 1200 | 38 | 1.94 | 0.47 | 0.63 | 0.79 | 36.1 |  | 2.26 | 0.47 |  | 0.64 | 0.81 | 34.2 |  | 2.59 | 0.48 | 0.66 | 0.83
| 1400 | 38.9 | 1.91 | 0.47 | 0.66 | 0.84 | 37 |  | 2.23 | 0.49 |  | 0.68 | 0.86 | 35 |  | 2.57 | 0.49 | 0.7 | 0.89
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
4 TON - LCM048U4
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F |  |  |  |  | 75°F | [6 empty] | 85°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 850 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | 40.9 |  | 2.45 | 0.68 | 0.79 | 0.89
| 1000 | 46.5 | 1.84 | 0.69 | 0.8 | 0.9 | 44.5 |  | 2.13 | 0.69 |  | 0.81 | 0.92 | 42.8 |  | 2.45 | 0.7 | 0.82 | 0.94
| 1150 | 48.4 | 1.83 | 0.71 | 0.83 | 0.94 | 46.4 |  | 2.12 | 0.72 |  | 0.84 | 0.96 | 44.5 |  | 2.44 | 0.73 | 0.86 | 0.98
| 1300 | 50 | 1.82 | 0.73 | 0.86 | 0.98 | 47.8 |  | 2.12 | 0.74 |  | 0.88 | 1 | 45.9 |  | 2.43 | 0.75 | 0.89 | 1
| 1600 | 52.5 | 1.81 | 0.77 | 0.92 | 1 | 50.1 |  | 2.1 | 0.79 |  | 0.94 | 1 | 48 |  | 2.43 | 0.81 | 0.97 | 1
| 1900 | 54.4 | 1.81 | 0.82 | 0.98 | 1 | 52 |  | 2.1 | 0.84 |  | 1 | 1 | 49.9 |  | 2.42 | 0.86 | 1 | 1
67°F | 850 | 46.9 | 1.84 | 0.54 | 0.64 | 0.73 | 45 |  | 2.12 | 0.55 |  | 0.65 | 0.74 | 43.3 |  | 2.44 | 0.55 | 0.65 | 0.75
| 1000 | 49.3 | 1.83 | 0.55 | 0.66 | 0.76 | 47.3 |  | 2.11 | 0.56 |  | 0.67 | 0.77 | 45.4 |  | 2.43 | 0.56 | 0.68 | 0.79
| 1150 | 51.3 | 1.82 | 0.57 | 0.68 | 0.79 | 49.1 |  | 2.11 | 0.57 |  | 0.69 | 0.81 | 47.1 |  | 2.43 | 0.58 | 0.7 | 0.83
| 1300 | 53 | 1.81 | 0.58 | 0.7 | 0.82 | 50.7 |  | 2.11 | 0.59 |  | 0.72 | 0.84 | 48.5 |  | 2.43 | 0.59 | 0.73 | 0.86
| 1600 | 55.4 | 1.81 | 0.6 | 0.75 | 0.89 | 52.9 |  | 2.1 | 0.61 |  | 0.77 | 0.91 | 50.7 |  | 2.42 | 0.62 | 0.78 | 0.93
| 1900 | 57.2 | 1.8 | 0.63 | 0.8 | 0.95 | 54.6 |  | 2.09 | 0.64 |  | 0.82 | 0.97 | 52.2 |  | 2.42 | 0.66 | 0.83 | 1
71°F | 850 | 49.5 | 1.82 | 0.43 | 0.52 | 0.61 | 47.5 |  | 2.11 | 0.43 |  | 0.53 | 0.62 | 45.7 |  | 2.44 | 0.43 | 0.53 | 0.63
| 1000 | 52 | 1.82 | 0.43 | 0.53 | 0.63 | 49.9 |  | 2.11 | 0.44 |  | 0.54 | 0.64 | 48 |  | 2.43 | 0.44 | 0.55 | 0.65
| 1150 | 54.1 | 1.81 | 0.44 | 0.55 | 0.65 | 51.8 |  | 2.1 | 0.44 |  | 0.55 | 0.67 | 49.7 |  | 2.43 | 0.44 | 0.56 | 0.68
| 1300 | 55.9 | 1.81 | 0.44 | 0.56 | 0.68 | 53.4 |  | 2.1 | 0.44 |  | 0.57 | 0.69 | 51.2 |  | 2.42 | 0.45 | 0.58 | 0.7
| 1600 | 58.5 | 1.8 | 0.45 | 0.59 | 0.73 | 55.8 |  | 2.09 | 0.46 |  | 0.6 | 0.74 | 53.5 |  | 2.42 | 0.46 | 0.61 | 0.76
| 1900 | 60.6 | 1.8 | 0.46 | 0.62 | 0.77 | 57.7 |  | 2.09 | 0.47 |  | 0.63 | 0.8 | 55.1 |  | 2.41 | 0.48 | 0.65 | 0.81
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 95°F |  |  |  |  | 105°F | [6 empty] | 115°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 850 | 39.2 | 2.8 | 0.69 | 0.8 | 0.91 | 37.5 |  | 3.2 | 0.7 |  | 0.81 | 0.93 | 35.5 |  | 3.62 | 0.71 | 0.83 | 0.95
| 1000 | 41.2 | 2.8 | 0.71 | 0.84 | 0.96 | 39.3 |  | 3.19 | 0.73 |  | 0.86 | 0.98 | 37.1 |  | 3.62 | 0.74 | 0.88 | 1
| 1150 | 42.7 | 2.79 | 0.74 | 0.88 | 1 | 40.7 |  | 3.18 | 0.75 |  | 0.9 | 1 | 38.4 |  | 3.61 | 0.77 | 0.92 | 1
| 1300 | 43.9 | 2.78 | 0.77 | 0.91 | 1 | 41.8 |  | 3.18 | 0.78 |  | 0.94 | 1 | 39.4 |  | 3.61 | 0.81 | 0.97 | 1
| 1600 | 46 | 2.78 | 0.82 | 0.99 | 1 | 43.8 |  | 3.17 | 0.84 |  | 1 | 1 | 41.6 |  | 3.6 | 0.87 | 1 | 1
| 1900 | 48 | 2.78 | 0.88 | 1 | 1 | 45.9 |  | 3.17 | 0.9 |  | 1 | 1 | 43.6 |  | 3.61 | 0.93 | 1 | 1
67°F | 850 | 41.7 | 2.8 | 0.56 | 0.66 | 0.77 | 39.8 |  | 3.17 | 0.56 |  | 0.67 | 0.78 | 37.7 |  | 3.62 | 0.57 | 0.69 | 0.8
| 1000 | 43.6 | 2.79 | 0.57 | 0.69 | 0.8 | 41.7 |  | 3.18 | 0.58 |  | 0.7 | 0.82 | 39.2 |  | 3.6 | 0.59 | 0.72 | 0.84
| 1150 | 45.2 | 2.79 | 0.58 | 0.71 | 0.84 | 43.1 |  | 3.18 | 0.59 |  | 0.73 | 0.86 | 40.6 |  | 3.6 | 0.6 | 0.75 | 0.89
| 1300 | 46.5 | 2.78 | 0.6 | 0.74 | 0.88 | 44.3 |  | 3.17 | 0.61 |  | 0.76 | 0.9 | 41.6 |  | 3.61 | 0.63 | 0.78 | 0.93
| 1600 | 48.4 | 2.78 | 0.64 | 0.8 | 0.96 | 46 |  | 3.17 | 0.65 |  | 0.82 | 0.98 | 43.4 |  | 3.6 | 0.66 | 0.85 | 1
| 1900 | 49.9 | 2.78 | 0.67 | 0.85 | 1 | 47.4 |  | 3.17 | 0.68 |  | 0.88 | 1 | 44.5 |  | 3.6 | 0.7 | 0.91 | 1
71°F | 850 | 44 | 2.8 | 0.43 | 0.54 | 0.64 | 42.1 |  | 3.18 | 0.43 |  | 0.54 | 0.65 | 39.8 |  | 3.61 | 0.44 | 0.55 | 0.66
| 1000 | 46 | 2.78 | 0.44 | 0.55 | 0.66 | 43.9 |  | 3.17 | 0.44 |  | 0.56 | 0.67 | 41.5 |  | 3.61 | 0.44 | 0.57 | 0.69
| 1150 | 47.6 | 2.78 | 0.44 | 0.57 | 0.69 | 45.5 |  | 3.18 | 0.45 |  | 0.58 | 0.7 | 42.9 |  | 3.61 | 0.45 | 0.59 | 0.72
| 1300 | 49.1 | 2.78 | 0.45 | 0.59 | 0.72 | 46.7 |  | 3.17 | 0.45 |  | 0.6 | 0.74 | 44.1 |  | 3.6 | 0.46 | 0.61 | 0.76
| 1600 | 51.1 | 2.77 | 0.47 | 0.62 | 0.78 | 48.7 |  | 3.17 | 0.47 |  | 0.64 | 0.8 | 45.8 |  | 3.6 | 0.48 | 0.65 | 0.82
| 1900 | 52.6 | 2.77 | 0.48 | 0.66 | 0.83 | 50 |  | 3.17 | 0.48 |  | 0.68 | 0.86 | 47 |  | 3.6 | 0.49 | 0.7 | 0.89
RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
5 TON - LCM060U4
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F |  |  |  |  | 75°F | [6 empty] | 85°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 950 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | - - - |  | - - - | - - - | - - - | - - -
| 1150 | 56.1 | 2.48 | 0.67 | 0.77 | 0.87 | 54.7 |  | 2.79 | 0.67 |  | 0.78 | 0.88 | 52.8 |  | 3.18 | 0.68 | 0.79 | 0.9
| 1300 | 58.3 | 2.48 | 0.68 | 0.8 | 0.91 | 56.5 |  | 2.8 | 0.69 |  | 0.8 | 0.92 | 54.7 |  | 3.19 | 0.7 | 0.82 | 0.94
| 1550 | 61 | 2.48 | 0.71 | 0.84 | 0.96 | 59 |  | 2.8 | 0.72 |  | 0.85 | 0.98 | 57 |  | 3.2 | 0.73 | 0.87 | 0.99
| 1800 | 63.1 | 2.47 | 0.75 | 0.89 | 1 | 61.2 |  | 2.8 | 0.76 |  | 0.9 | 1 | 59 |  | 3.21 | 0.77 | 0.92 | 1
| 2300 | 66.3 | 2.47 | 0.81 | 0.97 | 1 | 64.1 |  | 2.8 | 0.82 |  | 0.99 | 1 | 61.9 |  | 3.21 | 0.83 | 1 | 1
67°F | 950 | 56.4 | 2.48 | 0.53 | 0.62 | 0.71 | 54.8 |  | 2.79 | 0.54 |  | 0.63 | 0.72 | 53.1 |  | 3.19 | 0.54 | 0.63 | 0.72
| 1150 | 59.9 | 2.48 | 0.54 | 0.64 | 0.74 | 58.1 |  | 2.8 | 0.55 |  | 0.65 | 0.75 | 56.1 |  | 3.19 | 0.55 | 0.65 | 0.75
| 1300 | 61.9 | 2.48 | 0.55 | 0.66 | 0.76 | 60.1 |  | 2.8 | 0.55 |  | 0.67 | 0.78 | 58 |  | 3.2 | 0.56 | 0.67 | 0.79
| 1550 | 64.6 | 2.47 | 0.57 | 0.69 | 0.81 | 62.5 |  | 2.8 | 0.57 |  | 0.69 | 0.82 | 60.4 |  | 3.21 | 0.58 | 0.7 | 0.84
| 1800 | 66.9 | 2.46 | 0.59 | 0.72 | 0.85 | 64.8 |  | 2.8 | 0.59 |  | 0.73 | 0.87 | 62.3 |  | 3.21 | 0.6 | 0.74 | 0.88
| 2300 | 70.2 | 2.45 | 0.63 | 0.79 | 0.94 | 67.8 |  | 2.8 | 0.63 |  | 0.8 | 0.96 | 65.3 |  | 3.22 | 0.63 | 0.81 | 0.98
71°F | 950 | 59.7 | 2.48 | 0.43 | 0.51 | 0.59 | 58.1 |  | 2.8 | 0.43 |  | 0.51 | 0.6 | 56.3 |  | 3.2 | 0.43 | 0.52 | 0.6
| 1150 | 63.3 | 2.47 | 0.43 | 0.52 | 0.62 | 61.5 |  | 2.8 | 0.43 |  | 0.53 | 0.62 | 59.5 |  | 3.21 | 0.43 | 0.53 | 0.63
| 1300 | 65.6 | 2.47 | 0.43 | 0.53 | 0.63 | 63.6 |  | 2.8 | 0.43 |  | 0.54 | 0.64 | 61.5 |  | 3.21 | 0.43 | 0.54 | 0.65
| 1550 | 68.5 | 2.46 | 0.43 | 0.55 | 0.66 | 66.4 |  | 2.8 | 0.44 |  | 0.55 | 0.67 | 64 |  | 3.22 | 0.44 | 0.55 | 0.68
| 1800 | 70.9 | 2.45 | 0.44 | 0.58 | 0.7 | 68.6 |  | 2.8 | 0.44 |  | 0.58 | 0.71 | 66 |  | 3.22 | 0.45 | 0.59 | 0.72
| 2300 | 74.2 | 2.44 | 0.46 | 0.62 | 0.76 | 71.7 |  | 2.79 | 0.47 |  | 0.62 | 0.78 | 68.9 |  | 3.22 | 0.46 | 0.63 | 0.79
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 95°F |  |  |  |  | 105°F | [6 empty] | 115°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 950 | - - - | - - - | - - - | - - - | - - - | 45.9 |  | 4.1 | 0.67 |  | 0.78 | 0.88 | 43.7 |  | 4.6 | 0.68 | 0.79 | 0.9
| 1150 | 50.7 | 3.63 | 0.69 | 0.8 | 0.92 | 48.5 |  | 4.12 | 0.7 |  | 0.82 | 0.94 | 46.1 |  | 4.62 | 0.71 | 0.84 | 0.96
| 1300 | 52.4 | 3.65 | 0.71 | 0.83 | 0.96 | 50.1 |  | 4.13 | 0.72 |  | 0.85 | 0.98 | 47.5 |  | 4.63 | 0.73 | 0.87 | 1
| 1550 | 54.6 | 3.66 | 0.74 | 0.89 | 1 | 52.1 |  | 4.15 | 0.76 |  | 0.91 | 1 | 49.4 |  | 4.66 | 0.78 | 0.94 | 1
| 1800 | 56.3 | 3.66 | 0.78 | 0.94 | 1 | 53.9 |  | 4.16 | 0.8 |  | 0.96 | 1 | 51 |  | 4.67 | 0.82 | 0.99 | 1
| 2300 | 59.5 | 3.68 | 0.86 | 1 | 1 | 57.1 |  | 4.18 | 0.87 |  | 1 | 1 | 54.4 |  | 4.7 | 0.91 | 1 | 1
67°F | 950 | 51.1 | 3.64 | 0.54 | 0.64 | 0.73 | 49 |  | 4.13 | 0.55 |  | 0.64 | 0.74 | 46.6 |  | 4.63 | 0.55 | 0.65 | 0.75
| 1150 | 54 | 3.65 | 0.55 | 0.66 | 0.76 | 51.6 |  | 4.15 | 0.56 |  | 0.67 | 0.79 | 49 |  | 4.65 | 0.56 | 0.68 | 0.8
| 1300 | 55.7 | 3.66 | 0.57 | 0.69 | 0.8 | 53.2 |  | 4.15 | 0.57 |  | 0.69 | 0.82 | 50.5 |  | 4.67 | 0.58 | 0.71 | 0.84
| 1550 | 57.9 | 3.67 | 0.59 | 0.72 | 0.85 | 55.3 |  | 4.17 | 0.6 |  | 0.74 | 0.87 | 52.4 |  | 4.68 | 0.61 | 0.76 | 0.9
| 1800 | 59.7 | 3.68 | 0.61 | 0.76 | 0.91 | 57 |  | 4.18 | 0.62 |  | 0.78 | 0.93 | 53.9 |  | 4.69 | 0.62 | 0.79 | 0.96
| 2300 | 62.5 | 3.69 | 0.66 | 0.83 | 1 | 59.3 |  | 4.19 | 0.66 |  | 0.86 | 1 | 56.2 |  | 4.71 | 0.68 | 0.88 | 1
71°F | 950 | 54.1 | 3.65 | 0.43 | 0.52 | 0.61 | 51.9 |  | 4.15 | 0.43 |  | 0.53 | 0.62 | 49.5 |  | 4.66 | 0.43 | 0.53 | 0.63
| 1150 | 57.2 | 3.66 | 0.43 | 0.53 | 0.64 | 54.7 |  | 4.16 | 0.43 |  | 0.54 | 0.65 | 52 |  | 4.68 | 0.44 | 0.55 | 0.66
| 1300 | 59.1 | 3.68 | 0.43 | 0.55 | 0.66 | 56.4 |  | 4.18 | 0.44 |  | 0.55 | 0.67 | 53.5 |  | 4.69 | 0.44 | 0.56 | 0.68
| 1550 | 61.4 | 3.69 | 0.45 | 0.57 | 0.69 | 58.6 |  | 4.19 | 0.45 |  | 0.58 | 0.7 | 55.6 |  | 4.7 | 0.45 | 0.6 | 0.73
| 1800 | 63.3 | 3.69 | 0.46 | 0.6 | 0.73 | 60.3 |  | 4.2 | 0.46 |  | 0.61 | 0.75 | 57 |  | 4.72 | 0.46 | 0.62 | 0.77
| 2300 | 66 | 3.7 | 0.47 | 0.64 | 0.81 | 62.8 |  | 4.21 | 0.48 |  | 0.67 | 0.83 | 59.4 |  | 4.74 | 0.48 | 0.67 | 0.86
RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
6 TON - LCM074U4
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F |  |  |  |  | 75°F | [6 empty] | 85°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 950 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | - - - |  | - - - | - - - | - - - | - - -
| 1200 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | - - - |  | - - - | - - - | - - - | - - -
| 1500 | 70.9 | 3.24 | 0.68 | 0.8 | 0.9 | 68.6 |  | 3.66 | 0.69 |  | 0.8 | 0.92 | 66.6 |  | 4.17 | 0.7 | 0.82 | 0.93
| 1750 | 73.7 | 3.25 | 0.7 | 0.83 | 0.95 | 71.5 |  | 3.67 | 0.72 |  | 0.85 | 0.97 | 68.8 |  | 4.19 | 0.73 | 0.86 | 0.99
| 2050 | 76.3 | 3.25 | 0.74 | 0.88 | 1 | 74 |  | 3.68 | 0.74 |  | 0.89 | 1 | 71.3 |  | 4.21 | 0.76 | 0.91 | 1
| 2300 | 78.3 | 3.25 | 0.77 | 0.92 | 1 | 75.8 |  | 3.69 | 0.78 |  | 0.93 | 1 | 72.9 |  | 4.22 | 0.79 | 0.95 | 1
67°F | 950 | 65.1 | 3.22 | 0.53 | 0.61 | 0.69 | 63.4 |  | 3.63 | 0.53 |  | 0.61 | 0.69 | 61.4 |  | 4.13 | 0.53 | 0.62 | 0.7
| 1200 | 70.4 | 3.24 | 0.54 | 0.63 | 0.72 | 68.5 |  | 3.66 | 0.54 |  | 0.63 | 0.73 | 66.3 |  | 4.17 | 0.54 | 0.64 | 0.74
| 1500 | 75.2 | 3.25 | 0.55 | 0.66 | 0.76 | 72.9 |  | 3.68 | 0.56 |  | 0.66 | 0.77 | 70.3 |  | 4.2 | 0.56 | 0.67 | 0.78
| 1750 | 78.1 | 3.25 | 0.56 | 0.68 | 0.8 | 75.7 |  | 3.69 | 0.57 |  | 0.69 | 0.81 | 72.9 |  | 4.22 | 0.58 | 0.7 | 0.83
| 2050 | 80.9 | 3.25 | 0.58 | 0.72 | 0.84 | 78.2 |  | 3.7 | 0.58 |  | 0.73 | 0.86 | 75.3 |  | 4.23 | 0.6 | 0.74 | 0.87
| 2300 | 82.8 | 3.25 | 0.6 | 0.74 | 0.88 | 80.1 |  | 3.7 | 0.61 |  | 0.76 | 0.9 | 77.2 |  | 4.24 | 0.61 | 0.77 | 0.92
71°F | 950 | 69.1 | 3.23 | 0.43 | 0.51 | 0.58 | 67.3 |  | 3.65 | 0.43 |  | 0.51 | 0.58 | 65.1 |  | 4.17 | 0.43 | 0.51 | 0.59
| 1200 | 74.8 | 3.25 | 0.43 | 0.52 | 0.6 | 72.6 |  | 3.68 | 0.43 |  | 0.52 | 0.61 | 70.2 |  | 4.2 | 0.43 | 0.52 | 0.62
| 1500 | 79.6 | 3.25 | 0.43 | 0.53 | 0.63 | 77.2 |  | 3.7 | 0.43 |  | 0.54 | 0.64 | 74.5 |  | 4.23 | 0.43 | 0.54 | 0.65
| 1750 | 82.7 | 3.25 | 0.44 | 0.55 | 0.65 | 80.2 |  | 3.7 | 0.44 |  | 0.55 | 0.66 | 77.3 |  | 4.24 | 0.44 | 0.56 | 0.68
| 2050 | 85.5 | 3.25 | 0.44 | 0.57 | 0.69 | 82.9 |  | 3.71 | 0.44 |  | 0.57 | 0.7 | 79.9 |  | 4.26 | 0.45 | 0.58 | 0.71
| 2300 | 87.7 | 3.25 | 0.45 | 0.59 | 0.72 | 85 |  | 3.71 | 0.45 |  | 0.6 | 0.73 | 81.6 |  | 4.27 | 0.45 | 0.6 | 0.74
Entering Wet Bulb Tempera- ture | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 95°F |  |  |  |  | 105°F | [6 empty] | 115°F
|  | Total Cooling Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cooling Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T)
|  |  |  | Dry Bulb | [5 empty] | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh |  | kW | 75°F |  | 80°F | 85°F | kBtuh |  | kW | 75°F | 80°F | 85°F
63°F | 950 | - - - | - - - | - - - | - - - | - - - | - - - |  | - - - | - - - |  | - - - | - - - | - - - |  | - - - | - - - | - - - | - - -
| 1200 | - - - | - - - | - - - | - - - | - - - | 57.2 |  | 5.34 | 0.68 |  | 0.79 | 0.9 | 54.5 |  | 5.96 | 0.69 | 0.81 | 0.92
| 1500 | 63.7 | 4.76 | 0.71 | 0.83 | 0.95 | 60.8 |  | 5.38 | 0.72 |  | 0.85 | 0.98 | 57.7 |  | 6.01 | 0.73 | 0.87 | 1
| 1750 | 65.9 | 4.77 | 0.73 | 0.88 | 1 | 63 |  | 5.4 | 0.75 |  | 0.9 | 1 | 59.7 |  | 6.03 | 0.76 | 0.92 | 1
| 2050 | 68.3 | 4.8 | 0.77 | 0.93 | 1 | 65 |  | 5.42 | 0.79 |  | 0.96 | 1 | 61.9 |  | 6.06 | 0.81 | 0.98 | 1
| 2300 | 69.8 | 4.81 | 0.81 | 0.97 | 1 | 66.6 |  | 5.44 | 0.83 |  | 0.99 | 1 | 63.3 |  | 6.07 | 0.85 | 1 | 1
67°F | 950 | 59.1 | 4.71 | 0.53 | 0.62 | 0.71 | 56.8 |  | 5.33 | 0.54 |  | 0.63 | 0.72 | 54.3 |  | 5.97 | 0.54 | 0.64 | 0.73
| 1200 | 63.7 | 4.75 | 0.55 | 0.65 | 0.75 | 61 |  | 5.38 | 0.55 |  | 0.66 | 0.76 | 58 |  | 6.01 | 0.56 | 0.67 | 0.77
| 1500 | 67.6 | 4.79 | 0.56 | 0.68 | 0.8 | 64.5 |  | 5.41 | 0.57 |  | 0.69 | 0.82 | 61.3 |  | 6.05 | 0.58 | 0.71 | 0.84
| 1750 | 70 | 4.81 | 0.58 | 0.71 | 0.84 | 66.8 |  | 5.44 | 0.59 |  | 0.73 | 0.86 | 63.3 |  | 6.08 | 0.6 | 0.74 | 0.89
| 2050 | 72.1 | 4.83 | 0.61 | 0.74 | 0.9 | 69 |  | 5.46 | 0.62 |  | 0.77 | 0.92 | 65.4 |  | 6.11 | 0.63 | 0.79 | 0.95
| 2300 | 73.8 | 4.84 | 0.62 | 0.79 | 0.94 | 70.5 |  | 5.47 | 0.64 |  | 0.81 | 0.97 | 66.6 |  | 6.12 | 0.65 | 0.83 | 0.99
71°F | 950 | 62.8 | 4.74 | 0.43 | 0.51 | 0.59 | 60.2 |  | 5.36 | 0.43 |  | 0.51 | 0.6 | 57.7 |  | 6.01 | 0.43 | 0.52 | 0.61
| 1200 | 67.5 | 4.79 | 0.43 | 0.53 | 0.62 | 64.7 |  | 5.42 | 0.43 |  | 0.53 | 0.63 | 61.6 |  | 6.06 | 0.43 | 0.54 | 0.64
| 1500 | 71.6 | 4.82 | 0.43 | 0.55 | 0.65 | 68.4 |  | 5.45 | 0.44 |  | 0.55 | 0.67 | 65.1 |  | 6.1 | 0.44 | 0.56 | 0.68
| 1750 | 74.2 | 4.84 | 0.44 | 0.57 | 0.69 | 70.7 |  | 5.48 | 0.45 |  | 0.57 | 0.7 | 67.2 |  | 6.12 | 0.45 | 0.59 | 0.72
| 2050 | 76.6 | 4.86 | 0.45 | 0.59 | 0.72 | 73 |  | 5.5 | 0.46 |  | 0.6 | 0.74 | 69.3 |  | 6.15 | 0.46 | 0.62 | 0.77
| 2300 | 78.2 | 4.88 | 0.46 | 0.62 | 0.76 | 74.6 |  | 5.51 | 0.47 |  | 0.63 | 0.78 | 70.4 |  | 6.16 | 0.47 | 0.64 | 0.81