## Table 1
SPECIFICATIONS | [22 empty] | UNIT
General Data |  |  | Nominal Tonnage | [7 empty] | 7.5 Ton |  |  |  | 8.5 Ton |  |  |  | 10 Ton |  |  |  | 12.5 Ton
|  |  | Efficiency Type | [7 empty] | Ultra-High |  |  |  | Ultra-High |  |  |  | Ultra-High |  |  |  | Ultra-High
|  |  | Model Number | [7 empty] | LCM092U4E |  |  |  | LCM102U4E |  |  |  | LCM120U4E |  |  |  | LCM150U4E
[8 empty] | Blower Type |  |  | DirectPlus™ ECM Direct Drive with SZVAV |  |  |  | DirectPlus™ ECM Direct Drive with SZVAV |  |  |  | DirectPlus™ ECM Direct Drive with SZVAV |  |  |  | DirectPlus™ ECM Direct Drive with SZVAV
|  |  | Model Number | [7 empty] | LCM092U4P |  |  |  | LCM102U4P |  |  |  | LCM120U4P |  |  |  | LCM150U4P
[8 empty] | Blower Type |  |  | DirectPlus™ ECM Direct Drive with VAV |  |  |  | DirectPlus™ ECM Direct Drive with VAV |  |  |  | DirectPlus™ ECM Direct Drive with VAV |  |  |  | DirectPlus™ ECM Direct Drive with VAV
Cooling Performance |  |  | Gross Cooling Capacity - Btuh | [7 empty] | 90500 |  |  |  | 101600 |  |  |  | 121800 |  |  |  | 144000
|  |  | 1 Net Cooling Ca |  |  |  |  | pacity - Btuh |  |  | 86000 |  |  |  | 97000 |  |  |  | 114000 |  |  |  | 138000
|  |  | 1 AHRI Rated |  |  |  |  | Air Flow - cfm |  |  | 2800 |  |  |  | 3400 |  |  |  | 3600 |  |  |  | 4400
|  |  | Total Unit Power - kW | [7 empty] | 7.2 |  |  |  | 8.1 |  |  |  | 9.5 |  |  |  | 12.5
|  |  | 1 IEER |  |  |  |  | (Btuh/Watt) |  |  | 22 |  |  |  | 21 |  |  |  | 21 |  |  |  | 20
|  |  | 1 EER |  |  |  |  | (Btuh/Watt) |  |  | 12.6 |  |  |  | 12.6 |  |  |  | 12.2 |  |  |  | 11
Refrigerant Charge |  |  | Refrigerant Type | [7 empty] | R-410A |  |  |  | R-410A |  |  |  | R-410A |  |  |  | R-410A
|  |  | Without Reheat Option |  |  |  |  | Circuit 1 |  |  | 13 lbs.11 oz. |  |  |  | 13 lbs. 15 oz. |  |  |  | 15 lbs. 8 oz. |  |  |  | 15 lb. 12 oz.
[8 empty] | Circuit 2 |  |  | 9 lbs. 13 oz. |  |  |  | 9 lbs. 10 oz. |  |  |  | 11 lbs. 2 oz. |  |  |  | 10 lb. 8 oz.
|  |  | With Reheat Option |  |  |  |  | Circuit 1 |  |  | 15 lbs. 0 oz. |  |  |  | 15 lbs. 0 oz. |  |  |  | 18 lbs. 12 oz. |  |  |  | 19 lb. 12 oz.
[8 empty] | Circuit 2 |  |  | 9 lbs. 13 oz. |  |  |  | 9 lbs. 10 oz. |  |  |  | 11 lbs. 2 oz. |  |  |  | 10 lb. 8 oz.
Electric Heat Available - See page 19 | [10 empty] | 7.5, 15, 22.5, 30 & 45 kW | [7 empty] | 15, 22.5, 30, 45 & 60 kW
Compressor Type (number) | [10 empty] | Variable Capacity Scroll (1) Fixed Capacity Scroll (1)
Outdoor Coil |  |  | Net face area (total) - sq. ft. | [7 empty] | 20.5 |  |  |  | 20.5 |  |  |  | 28 |  |  |  | 28
|  |  | Tube diameter - in. | [7 empty] | 3/8 |  |  |  | 3/8 |  |  |  | 3/8 |  |  |  | 3/8
|  |  | Number of rows | [7 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3
[8 empty] | Fins per inch |  |  | 20 |  |  |  | 20 |  |  |  | 20 |  |  |  | 20
Outdoor Coil Fans |  |  | Motor - (No.) hp | [7 empty] | (2) 1/3 ECM |  |  |  | (2) 1/3 ECM |  |  |  | (2) 1/3 ECM |  |  |  | (2) 1/3 ECM
[8 empty] | Motor rpm |  |  | 400-850 |  |  |  | 400-1020 |  |  |  | 500-1020 |  |  |  | 500-1020
|  |  | Total Motor watts | [7 empty] | 65-450 |  |  |  | 65-750 |  |  |  | 65-750 |  |  |  | 65-750
|  |  | Diameter - (No.) in. | [7 empty] | (2) 24 |  |  |  | (2) 24 |  |  |  | (2) 24 |  |  |  | (2) 24
|  |  | Number of blades | [7 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3
|  |  | Total Air volume - cfm | [7 empty] | 7300 |  |  |  | 8800 |  |  |  | 8800 |  |  |  | 8800
Indoor Coil |  |  | Net face area (total) - sq. ft. | [7 empty] | 13.54 |  |  |  | 13.54 |  |  |  | 13.54 |  |  |  | 13.54
|  |  | Tube diameter - in. | [7 empty] | 3/8 |  |  |  | 3/8 |  |  |  | 3/8 |  |  |  | 3/8
|  |  | Number of rows | [7 empty] | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4
[8 empty] | Fins per inch |  |  | 14 |  |  |  | 14 |  |  |  | 14 |  |  |  | 14
| Drain connection - Number and size | [9 empty] | (1) 1 in. NPT coupling
|  |  | Expansion device type | [7 empty] | Balance port TXV, removable head
Indoor Blower |  |  | Nominal motor output | [7 empty] | 3.75 HP (ECM) |  |  |  | 3.75 HP (ECM) |  |  |  | 3.75 HP (ECM) |  |  |  | 3.75 HP (ECM)
| Blower wheel nominal diameter x width - in. | [9 empty] | (1) 22 x 9 |  |  |  | (1) 22 x 9 |  |  |  | (1) 22 x 9 |  |  |  | (1) 22 x 9
Filters | [7 empty] | Type of filter |  |  | MERV 4, Disposable
|  |  | Number and size - in. | [7 empty] | (4) 20 x 25 x 2
Electrical characteristics | [10 empty] | 208/230V, 460V, or 575V - 60 hz -3 phase
NOTE - Net capacity includes evaporator blower motor heat deduction. Gross capacity does not include evaporator blower motor heat deduction. 1 AHRI Certified to AHRI Standard 340/360; 95°F outdoor air temperature and 80°F db/67°F wb entering evaporator air; minimum external duct static pressure.
Model L™ Ultra-High Efficiency Packaged Electric / Electric 7.5 to 12.5 Ton / Page 21
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
7.5 TON - LCM092U4E/P (LOW COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [6 empty] | 75°F | [5 empty] | 85°F | [5 empty] | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 800 | 66.2 |  | 3.77 | 0.55 | 0.62 | 0.71 |  | 64.3 | 4.37 |  | 0.55 | 0.64 | 0.71 | 62 | 4.99 | 0.6 | 0.64 |  | 0.71 | 59.7 | 5.68 |  | 0.59 | 0.67 | 0.74
| 1335 | 80.2 |  | 3.8 | 0.6 | 0.7 | 0.79 |  | 77.6 | 4.41 |  | 0.61 | 0.7 | 0.8 | 74.9 | 5.04 | 0.61 | 0.71 |  | 0.81 | 71.8 | 5.73 |  | 0.62 | 0.73 | 0.83
| 1875 | 89 |  | 3.82 | 0.63 | 0.75 | 0.87 |  | 85.8 | 4.44 |  | 0.64 | 0.77 | 0.89 | 82.4 | 5.07 | 0.65 | 0.78 |  | 0.91 | 78.7 | 5.76 |  | 0.67 | 0.81 | 0.93
67°F | 800 | 69.8 |  | 3.76 | 0.48 | 0.57 | 0.62 |  | 67.5 | 4.37 |  | 0.48 | 0.56 | 0.62 | 65.2 | 5 | 0.5 | 0.56 |  | 0.63 | 62.5 | 5.69 |  | 0.49 | 0.56 | 0.63
| 1335 | 84.4 |  | 3.81 | 0.49 | 0.57 | 0.66 |  | 81.7 | 4.42 |  | 0.5 | 0.58 | 0.67 | 78.8 | 5.06 | 0.5 | 0.58 |  | 0.68 | 75.6 | 5.75 |  | 0.5 | 0.59 | 0.69
| 1875 | 93.8 |  | 3.84 | 0.52 | 0.61 | 0.72 |  | 90.4 | 4.45 |  | 0.51 | 0.62 | 0.73 | 86.9 | 5.09 | 0.52 | 0.63 |  | 0.75 | 83 | 5.78 |  | 0.53 | 0.64 | 0.76
71°F | 800 | 72.8 |  | 3.77 | 0.39 | 0.47 | 0.53 |  | 70.3 | 4.38 |  | 0.42 | 0.47 | 0.53 | 68 | 5.01 | 0.41 | 0.47 |  | 0.53 | 65.6 | 5.71 |  | 0.4 | 0.47 | 0.53
| 1335 | 88.6 |  | 3.82 | 0.4 | 0.48 | 0.55 |  | 85.7 | 4.43 |  | 0.4 | 0.48 | 0.55 | 82.7 | 5.07 | 0.4 | 0.48 |  | 0.56 | 79.4 | 5.77 |  | 0.39 | 0.48 | 0.56
| 1875 | 98.3 |  | 3.85 | 0.4 | 0.5 | 0.59 |  | 94.9 | 4.47 |  | 0.4 | 0.5 | 0.59 | 91.3 | 5.11 | 0.4 | 0.5 |  | 0.6 | 87.2 | 5.81 |  | 0.4 | 0.51 | 0.6
NOTE - Compressors operating at maximum capacity.
7.5 TON - LCM092U4E/P (HIGH COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [6 empty] | 95°F | [5 empty] | 105°F | [5 empty] | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 1875 | 82.4 |  | 5.07 | 0.64 | 0.77 | 0.9 |  | 78.7 | 5.76 |  | 0.66 | 0.79 | 0.92 | 74.7 | 6.54 | 0.67 | 0.81 |  | 0.95 | 69.9 | 7.43 |  | 0.68 | 0.85 | 0.98
| 2625 | 88.8 |  | 5.1 | 0.71 | 0.88 | 1 |  | 84.6 | 5.78 |  | 0.73 | 0.9 | 1 | 80.3 | 6.57 | 0.75 | 0.93 |  | 1 | 75.4 | 7.46 |  | 0.79 | 0.97 | 1
| 3600 | 94.9 |  | 5.12 | 0.81 | 1 | 1 |  | 90.8 | 5.82 |  | 0.83 | 1 | 1 | 86.3 | 6.6 | 0.86 | 1 |  | 1 | 81 | 7.49 |  | 0.91 | 1 | 1
67°F | 1875 | 86.9 |  | 5.09 | 0.52 | 0.62 | 0.73 |  | 83 | 5.78 |  | 0.53 | 0.63 | 0.74 | 78.7 | 6.56 | 0.53 | 0.65 |  | 0.77 | 73.8 | 7.45 |  | 0.54 | 0.66 | 0.81
| 2625 | 93.7 |  | 5.12 | 0.56 | 0.68 | 0.84 |  | 89.3 | 5.81 |  | 0.57 | 0.7 | 0.87 | 84.3 | 6.59 | 0.57 | 0.72 |  | 0.9 | 78.7 | 7.48 |  | 0.59 | 0.75 | 0.94
| 3600 | 99 |  | 5.15 | 0.61 | 0.79 | 0.97 |  | 94.1 | 5.84 |  | 0.61 | 0.82 | 1 | 88.5 | 6.61 | 0.63 | 0.86 |  | 1 | 82.4 | 7.5 |  | 0.65 | 0.9 | 1
71°F | 1875 | 91.3 |  | 5.11 | 0.4 | 0.5 | 0.6 |  | 87.2 | 5.81 |  | 0.4 | 0.51 | 0.6 | 82.8 | 6.59 | 0.4 | 0.52 |  | 0.63 | 77.6 | 7.48 |  | 0.41 | 0.53 | 0.64
| 2625 | 98.5 |  | 5.14 | 0.41 | 0.54 | 0.66 |  | 93.9 | 5.84 |  | 0.42 | 0.55 | 0.67 | 88.6 | 6.62 | 0.41 | 0.56 |  | 0.7 | 82.8 | 7.5 |  | 0.43 | 0.58 | 0.72
| 3600 | 104.2 |  | 5.17 | 0.44 | 0.6 | 0.77 |  | 99 | 5.86 |  | 0.44 | 0.61 | 0.79 | 93.2 | 6.64 | 0.45 | 0.63 |  | 0.84 | 86.7 | 7.52 |  | 0.46 | 0.66 | 0.86
NOTE - Compressors operating at maximum capacity.
8.5 TON - LCM102U4E/P (LOW COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [6 empty] | 75°F | [5 empty] | 85°F | [5 empty] | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 800 | 70.6 |  | 4.03 | 0.54 | 0.61 | 0.7 |  | 68.6 | 4.67 |  | 0.55 | 0.63 | 0.7 | 66.2 | 5.34 | 0.57 | 0.63 |  | 0.7 | 63.9 | 6.07 |  | 0.56 | 0.64 | 0.71
| 1465 | 89 |  | 4.05 | 0.6 | 0.69 | 0.78 |  | 86.1 | 4.71 |  | 0.6 | 0.7 | 0.79 | 83.1 | 5.39 | 0.61 | 0.7 |  | 0.81 | 79.6 | 6.12 |  | 0.62 | 0.72 | 0.82
| 2125 | 99.3 |  | 4.08 | 0.63 | 0.76 | 0.88 |  | 95.8 | 4.74 |  | 0.64 | 0.77 | 0.89 | 92.1 | 5.41 | 0.65 | 0.78 |  | 0.9 | 88 | 6.15 |  | 0.66 | 0.81 | 0.93
67°F | 800 | 74.6 |  | 4.02 | 0.49 | 0.54 | 0.59 |  | 72.2 | 4.68 |  | 0.48 | 0.54 | 0.59 | 69.7 | 5.35 | 0.51 | 0.56 |  | 0.62 | 67.4 | 6.07 |  | 0.5 | 0.56 | 0.62
| 1465 | 93.8 |  | 4.06 | 0.49 | 0.57 | 0.66 |  | 90.8 | 4.72 |  | 0.5 | 0.58 | 0.66 | 87.7 | 5.4 | 0.5 | 0.58 |  | 0.67 | 84.1 | 6.14 |  | 0.5 | 0.59 | 0.68
| 2125 | 104.9 |  | 4.1 | 0.51 | 0.61 | 0.72 |  | 101.3 | 4.75 |  | 0.51 | 0.62 | 0.74 | 97.3 | 5.43 | 0.52 | 0.64 |  | 0.75 | 92.9 | 6.17 |  | 0.52 | 0.64 | 0.76
71°F | 800 | 78.6 |  | 4.02 | 0.4 | 0.49 | 0.53 |  | 75.9 | 4.68 |  | 0.43 | 0.48 | 0.53 | 72.9 | 5.35 | 0.42 | 0.47 |  | 0.52 | 70.4 | 6.09 |  | 0.41 | 0.47 | 0.52
| 1465 | 98.6 |  | 4.08 | 0.4 | 0.47 | 0.54 |  | 95.5 | 4.74 |  | 0.39 | 0.48 | 0.55 | 92.1 | 5.42 | 0.4 | 0.48 |  | 0.55 | 88.3 | 6.16 |  | 0.4 | 0.47 | 0.56
| 2125 | 110.4 |  | 4.11 | 0.4 | 0.49 | 0.59 |  | 106.5 | 4.77 |  | 0.4 | 0.5 | 0.59 | 102.3 | 5.46 | 0.4 | 0.51 |  | 0.61 | 97.8 | 6.2 |  | 0.4 | 0.51 | 0.61
NOTE - Compressors operating at maximum capacity.
8.5 TON - LCM102U4E/P (HIGH COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [6 empty] | 95°F | [5 empty] | 105°F | [5 empty] | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 2125 | 92.1 |  | 5.41 | 0.64 | 0.77 | 0.9 |  | 88 | 6.15 |  | 0.65 | 0.79 | 0.92 | 83.3 | 6.98 | 0.67 | 0.82 |  | 0.95 | 78 | 7.93 |  | 0.69 | 0.84 | 0.98
| 2975 | 99.2 |  | 5.44 | 0.72 | 0.88 | 1 |  | 94.8 | 6.17 |  | 0.74 | 0.91 | 1 | 89.8 | 7.01 | 0.77 | 0.94 |  | 1 | 84.1 | 7.96 |  | 0.78 | 0.97 | 1
| 4080 | 106.1 |  | 5.46 | 0.81 | 1 | 1 |  | 101.4 | 6.21 |  | 0.83 | 1 | 1 | 96.4 | 7.04 | 0.87 | 1 |  | 1 | 90.4 | 7.99 |  | 0.92 | 1 | 1
67°F | 2125 | 97.3 |  | 5.43 | 0.52 | 0.63 | 0.74 |  | 92.9 | 6.17 |  | 0.52 | 0.63 | 0.75 | 88 | 7.01 | 0.53 | 0.65 |  | 0.78 | 82.4 | 7.95 |  | 0.54 | 0.66 | 0.8
| 2975 | 104.6 |  | 5.46 | 0.56 | 0.69 | 0.85 |  | 99.5 | 6.2 |  | 0.57 | 0.7 | 0.87 | 94 | 7.03 | 0.58 | 0.73 |  | 0.9 | 87.7 | 7.99 |  | 0.58 | 0.77 | 0.94
| 4080 | 110.4 |  | 5.49 | 0.61 | 0.78 | 0.98 |  | 104.6 | 6.22 |  | 0.62 | 0.81 | 1 | 98.5 | 7.05 | 0.64 | 0.87 |  | 1 | 91.6 | 8 |  | 0.66 | 0.89 | 1
71°F | 2125 | 102.3 |  | 5.46 | 0.4 | 0.51 | 0.6 |  | 97.8 | 6.2 |  | 0.4 | 0.51 | 0.61 | 92.6 | 7.03 | 0.4 | 0.52 |  | 0.63 | 86.9 | 7.98 |  | 0.4 | 0.53 | 0.64
| 2975 | 110.1 |  | 5.49 | 0.42 | 0.55 | 0.67 |  | 104.9 | 6.22 |  | 0.42 | 0.55 | 0.68 | 99 | 7.06 | 0.42 | 0.57 |  | 0.7 | 92.4 | 8.01 |  | 0.43 | 0.58 | 0.74
| 4080 | 116.1 |  | 5.51 | 0.45 | 0.59 | 0.79 |  | 110.3 | 6.25 |  | 0.44 | 0.61 | 0.79 | 103.9 | 7.08 | 0.46 | 0.62 |  | 0.85 | 96.5 | 8.03 |  | 0.45 | 0.64 | 0.87
NOTE - Compressors operating at maximum capacity.
Model L™ Ultra-High Efficiency Packaged Electric / Electric 7.5 to 12.5 Ton / Page 22
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
10 TON - LCM120U4E/P (LOW COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [6 empty] | 75°F | [5 empty] | 85°F | [5 empty] | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 875 | 80 |  | 5.13 | 0.55 | 0.62 | 0.68 |  | 78.1 | 5.8 |  | 0.56 | 0.62 | 0.69 | 76.1 | 6.59 | 0.55 | 0.64 |  | 0.7 | 73.5 | 7.5 |  | 0.56 | 0.64 | 0.71
| 1650 | 103.7 |  | 5.21 | 0.6 | 0.69 | 0.78 |  | 100.6 | 5.89 |  | 0.6 | 0.69 | 0.78 | 97.3 | 6.69 | 0.6 | 0.7 |  | 0.79 | 93.7 | 7.59 |  | 0.61 | 0.7 | 0.8
| 2500 | 117.8 |  | 5.26 | 0.64 | 0.75 | 0.86 |  | 114.1 | 5.94 |  | 0.65 | 0.77 | 0.88 | 110 | 6.75 | 0.66 | 0.77 |  | 0.89 | 105.4 | 7.66 |  | 0.66 | 0.79 | 0.91
67°F | 875 | 84.7 |  | 5.13 | 0.47 | 0.53 | 0.58 |  | 82.7 | 5.82 |  | 0.47 | 0.52 | 0.6 | 80.5 | 6.61 | 0.46 | 0.55 |  | 0.6 | 77.6 | 7.51 |  | 0.49 | 0.54 | 0.6
| 1650 | 109.3 |  | 5.23 | 0.5 | 0.57 | 0.65 |  | 106.2 | 5.92 |  | 0.5 | 0.57 | 0.66 | 102.7 | 6.7 | 0.5 | 0.58 |  | 0.66 | 98.9 | 7.63 |  | 0.5 | 0.58 | 0.67
| 2500 | 124.5 |  | 5.29 | 0.51 | 0.61 | 0.71 |  | 120.5 | 5.98 |  | 0.51 | 0.62 | 0.72 | 116.2 | 6.78 | 0.52 | 0.63 |  | 0.74 | 111.5 | 7.7 |  | 0.53 | 0.64 | 0.76
71°F | 875 | 89.6 |  | 5.15 | 0.41 | 0.47 | 0.52 |  | 87.6 | 5.83 |  | 0.41 | 0.46 | 0.54 | 84.9 | 6.63 | 0.41 | 0.49 |  | 0.53 | 81.7 | 7.53 |  | 0.43 | 0.48 | 0.53
| 1650 | 115 |  | 5.25 | 0.4 | 0.48 | 0.54 |  | 111.7 | 5.94 |  | 0.4 | 0.47 | 0.55 | 108.1 | 6.74 | 0.4 | 0.48 |  | 0.55 | 104.1 | 7.65 |  | 0.4 | 0.48 | 0.55
| 2500 | 131 |  | 5.3 | 0.4 | 0.5 | 0.58 |  | 126.8 | 6 |  | 0.41 | 0.49 | 0.59 | 122.4 | 6.81 | 0.4 | 0.5 |  | 0.6 | 117.5 | 7.74 |  | 0.4 | 0.51 | 0.61
NOTE - Compressors operating at maximum capacity.
10 TON - LCM120U4E/P (HIGH COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [6 empty] | 95°F | [5 empty] | 105°F | [5 empty] | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 2500 | 109.6 |  | 6.56 | 0.64 | 0.76 | 0.89 |  | 105 | 7.43 |  | 0.65 | 0.78 | 0.91 | 100.2 | 8.4 | 0.66 | 0.8 |  | 0.93 | 94.8 | 9.47 |  | 0.68 | 0.83 | 0.96
| 3500 | 118.1 |  | 6.63 | 0.71 | 0.86 | 1 |  | 112.9 | 7.5 |  | 0.73 | 0.89 | 1 | 107.7 | 8.48 | 0.75 | 0.91 |  | 1 | 102.1 | 9.54 |  | 0.77 | 0.94 | 1
| 4800 | 125.9 |  | 6.68 | 0.8 | 0.99 | 1 |  | 120.5 | 7.57 |  | 0.82 | 1 | 1 | 115.3 | 8.54 | 0.86 | 1 |  | 1 | 109.4 | 9.63 |  | 0.88 | 1 | 1
67°F | 2500 | 115.8 |  | 6.61 | 0.52 | 0.62 | 0.73 |  | 111 | 7.49 |  | 0.53 | 0.63 | 0.75 | 105.7 | 8.46 | 0.53 | 0.64 |  | 0.76 | 100.3 | 9.54 |  | 0.54 | 0.66 | 0.79
| 3500 | 124.8 |  | 6.68 | 0.56 | 0.68 | 0.83 |  | 119.2 | 7.55 |  | 0.57 | 0.69 | 0.85 | 113.4 | 8.53 | 0.58 | 0.71 |  | 0.88 | 107 | 9.61 |  | 0.58 | 0.74 | 0.91
| 4800 | 131.8 |  | 6.73 | 0.59 | 0.77 | 0.96 |  | 125.7 | 7.61 |  | 0.62 | 0.81 | 0.99 | 119.2 | 8.59 | 0.63 | 0.84 |  | 1 | 112.2 | 9.66 |  | 0.65 | 0.87 | 1
71°F | 2500 | 121.8 |  | 6.66 | 0.4 | 0.5 | 0.6 |  | 116.9 | 7.55 |  | 0.41 | 0.51 | 0.61 | 111.5 | 8.52 | 0.4 | 0.52 |  | 0.62 | 105.7 | 9.59 |  | 0.41 | 0.52 | 0.63
| 3500 | 131.4 |  | 6.73 | 0.41 | 0.54 | 0.66 |  | 125.6 | 7.61 |  | 0.42 | 0.55 | 0.68 | 119.5 | 8.6 | 0.43 | 0.56 |  | 0.68 | 112.9 | 9.67 |  | 0.43 | 0.56 | 0.71
| 4800 | 138.7 |  | 6.77 | 0.43 | 0.59 | 0.76 |  | 132.4 | 7.66 |  | 0.45 | 0.6 | 0.77 | 125.8 | 8.65 | 0.44 | 0.61 |  | 0.81 | 118.5 | 9.73 |  | 0.45 | 0.63 | 0.82
NOTE - Compressors operating at maximum capacity.
12.5 TON - LCM150U4E/P (LOW COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [6 empty] | 75°F | [5 empty] | 85°F | [5 empty] | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 1100 | 99.1 |  | 7.01 | 0.56 | 0.62 | 0.69 |  | 96.8 | 7.84 |  | 0.56 | 0.62 | 0.69 | 94.1 | 8.84 | 0.56 | 0.63 |  | 0.71 | 91.1 | 9.97 |  | 0.56 | 0.64 | 0.71
| 1965 | 125.2 |  | 7.13 | 0.6 | 0.69 | 0.77 |  | 121.5 | 7.99 |  | 0.6 | 0.69 | 0.78 | 117.5 | 9 | 0.61 | 0.7 |  | 0.79 | 113.1 | 10.13 |  | 0.61 | 0.71 | 0.8
| 3125 | 144 |  | 7.24 | 0.65 | 0.76 | 0.87 |  | 139.3 | 8.11 |  | 0.66 | 0.77 | 0.89 | 134.3 | 9.13 | 0.67 | 0.79 |  | 0.91 | 128.7 | 10.25 |  | 0.68 | 0.8 | 0.93
67°F | 1100 | 105 |  | 7.03 | 0.47 | 0.53 | 0.59 |  | 102.5 | 7.87 |  | 0.47 | 0.52 | 0.61 | 99.9 | 8.88 | 0.49 | 0.53 |  | 0.61 | 96.3 | 10 |  | 0.49 | 0.57 | 0.6
| 1965 | 131.8 |  | 7.17 | 0.5 | 0.57 | 0.65 |  | 128.2 | 8.03 |  | 0.5 | 0.58 | 0.65 | 124 | 9.05 | 0.5 | 0.58 |  | 0.66 | 119.4 | 10.19 |  | 0.5 | 0.59 | 0.67
| 3125 | 151.9 |  | 7.29 | 0.52 | 0.62 | 0.73 |  | 147.1 | 8.17 |  | 0.52 | 0.62 | 0.74 | 141.8 | 9.21 | 0.53 | 0.63 |  | 0.75 | 135.9 | 10.35 |  | 0.53 | 0.65 | 0.77
71°F | 1100 | 111 |  | 7.06 | 0.41 | 0.47 | 0.52 |  | 108.6 | 7.91 |  | 0.41 | 0.46 | 0.54 | 105.2 | 8.92 | 0.4 | 0.49 |  | 0.54 | 100.8 | 10.03 |  | 0.43 | 0.48 | 0.53
| 1965 | 138.6 |  | 7.21 | 0.4 | 0.47 | 0.55 |  | 134.7 | 8.08 |  | 0.4 | 0.48 | 0.55 | 130.3 | 9.09 | 0.4 | 0.48 |  | 0.56 | 125.5 | 10.25 |  | 0.4 | 0.48 | 0.56
| 3125 | 159.7 |  | 7.33 | 0.41 | 0.5 | 0.6 |  | 154.7 | 8.24 |  | 0.41 | 0.51 | 0.6 | 149.2 | 9.26 | 0.4 | 0.51 |  | 0.61 | 143.1 | 10.43 |  | 0.41 | 0.52 | 0.62
NOTE - Compressors operating at maximum capacity.
12.5 TON - LCM150U4E/P (HIGH COOLING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [6 empty] | 95°F | [5 empty] | 105°F | [5 empty] | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb |  |  |  |  | Dry Bulb | [6 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F | 85°F |  | kBtuh | kW |  | 75°F | 80°F | 85°F | kBtuh | kW | 75°F | 80°F |  | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 3125 | 134.1 |  | 8.99 | 0.66 | 0.77 | 0.9 |  | 128.4 | 10.1 |  | 0.67 | 0.79 | 0.92 | 122.5 | 11.34 | 0.68 | 0.82 |  | 0.95 | 116.2 | 12.67 |  | 0.69 | 0.83 | 0.98
| 4375 | 144.1 |  | 9.08 | 0.72 | 0.89 | 1 |  | 137.8 | 10.2 |  | 0.73 | 0.9 | 1 | 131.2 | 11.44 | 0.75 | 0.93 |  | 1 | 124.3 | 12.78 |  | 0.77 | 0.96 | 1
| 6000 | 152.7 |  | 9.16 | 0.82 | 1 | 1 |  | 146.5 | 10.31 |  | 0.84 | 1 | 1 | 140.3 | 11.56 | 0.86 | 1 |  | 1 | 133.4 | 12.9 |  | 0.88 | 1 | 1
67°F | 3125 | 141.5 |  | 9.06 | 0.53 | 0.63 | 0.74 |  | 135.6 | 10.19 |  | 0.53 | 0.64 | 0.75 | 129.4 | 11.42 | 0.54 | 0.66 |  | 0.77 | 122.8 | 12.77 |  | 0.55 | 0.66 | 0.8
| 4375 | 152.1 |  | 9.17 | 0.56 | 0.7 | 0.85 |  | 145.4 | 10.29 |  | 0.57 | 0.71 | 0.87 | 138.5 | 11.54 | 0.58 | 0.73 |  | 0.89 | 131 | 12.87 |  | 0.6 | 0.75 | 0.93
| 6000 | 160.4 |  | 9.23 | 0.62 | 0.79 | 0.98 |  | 153.3 | 10.38 |  | 0.63 | 0.81 | 1 | 145.4 | 11.63 | 0.64 | 0.83 |  | 1 | 137.3 | 12.93 |  | 0.65 | 0.87 | 1
71°F | 3125 | 148.9 |  | 9.14 | 0.4 | 0.51 | 0.6 |  | 142.7 | 10.27 |  | 0.41 | 0.52 | 0.62 | 136.3 | 11.53 | 0.41 | 0.52 |  | 0.63 | 129.3 | 12.85 |  | 0.42 | 0.53 | 0.64
| 4375 | 160.1 |  | 9.24 | 0.42 | 0.54 | 0.67 |  | 153.2 | 10.38 |  | 0.42 | 0.55 | 0.68 | 145.8 | 11.63 | 0.43 | 0.57 |  | 0.7 | 138 | 12.97 |  | 0.42 | 0.58 | 0.73
| 6000 | 168.7 |  | 9.32 | 0.45 | 0.59 | 0.78 |  | 160.9 | 10.46 |  | 0.45 | 0.62 | 0.79 | 153.1 | 11.71 | 0.46 | 0.64 |  | 0.83 | 144.6 | 13.06 |  | 0.47 | 0.65 | 0.85
NOTE - Compressors operating at maximum capacity.
Model L™ Ultra-High Efficiency Packaged Electric / Electric 7.5 to 12.5 Ton / Page 23